## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-825_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-825_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-825_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-825_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-825_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-825_0_4_node_72 | 0.4 | n |  | TRUE
6 | bus_LV_261-825_0_4_node_60 | 0.4 | n |  | TRUE
7 | bus_LV_261-825_0_4_node_73 | 0.4 | n |  | TRUE
8 | bus_LV_261-825_0_4_node_59 | 0.4 | n |  | TRUE
9 | bus_LV_261-825_0_4_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_261-825_0_4_node_67 | 0.4 | n |  | TRUE
11 | bus_LV_261-825_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_261-825_0_4_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_261-825_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_261-825_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_261-825_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_261-825_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_261-825_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_261-825_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_261-825_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_261-825_0_4_node_64 | 0.4 | n |  | TRUE
21 | bus_LV_261-825_0_4_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_261-825_0_4_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_261-825_0_4_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_261-825_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_261-825_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_261-825_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_261-825_0_4_node_56 | 0.4 | n |  | TRUE
28 | bus_LV_261-825_0_4_node_57 | 0.4 | n |  | TRUE
29 | bus_LV_261-825_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_261-825_0_4_node_43 | 0.4 | n |  | TRUE
31 | bus_LV_261-825_0_4_node_54 | 0.4 | n |  | TRUE
32 | bus_LV_261-825_0_4_node_42 | 0.4 | n |  | TRUE
33 | bus_LV_261-825_0_4_node_53 | 0.4 | n |  | TRUE
34 | bus_LV_261-825_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_261-825_0_4_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_261-825_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_261-825_0_4_node_62 | 0.4 | n |  | TRUE
38 | bus_LV_261-825_0_4_node_47 | 0.4 | n |  | TRUE
39 | bus_LV_261-825_0_4_node_61 | 0.4 | n |  | TRUE
40 | bus_LV_261-825_0_4_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_261-825_0_4_node_45 | 0.4 | n |  | TRUE
42 | bus_LV_261-825_0_4_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_261-825_0_4_node_78 | 0.4 | n |  | TRUE
44 | bus_LV_261-825_0_4_node_74 | 0.4 | n |  | TRUE
45 | bus_LV_261-825_0_4_node_69 | 0.4 | n |  | TRUE
46 | bus_LV_261-825_0_4_node_70 | 0.4 | n |  | TRUE
47 | bus_LV_261-825_0_4_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_261-825_0_4_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_261-825_0_4_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_261-825_0_4_node_51 | 0.4 | n |  | TRUE
51 | bus_LV_261-825_0_4_node_55 | 0.4 | n |  | TRUE
52 | bus_LV_261-825_0_4_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_261-825_0_4_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_261-825_0_4_node_36 | 0.4 | n |  | TRUE
55 | bus_LV_261-825_0_4_node_68 | 0.4 | n |  | TRUE
56 | bus_LV_261-825_0_4_node_77 | 0.4 | n |  | TRUE
57 | bus_LV_261-825_0_4_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_261-825_0_4_node_32 | 0.4 | n |  | TRUE
59 | bus_LV_261-825_0_4_node_33 | 0.4 | n |  | TRUE
60 | bus_LV_261-825_0_4_node_34 | 0.4 | n |  | TRUE
61 | bus_LV_261-825_0_4_node_35 | 0.4 | n |  | TRUE
62 | bus_LV_261-825_0_4_node_37 | 0.4 | n |  | TRUE
63 | bus_LV_261-825_0_4_node_38 | 0.4 | n |  | TRUE
64 | bus_LV_261-825_0_4_node_39 | 0.4 | n |  | TRUE
65 | bus_LV_261-825_0_4_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_261-825_0_4_node_41 | 0.4 | n |  | TRUE
67 | bus_LV_261-825_0_4_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_261-825_0_4_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_261-825_0_4_node_71 | 0.4 | n |  | TRUE
70 | bus_LV_261-825_0_4_node_76 | 0.4 | n |  | TRUE
71 | bus_LV_261-825_0_4_node_75 | 0.4 | n |  | TRUE
72 | bus_MV_541_0_node_56 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-825_0_4_load_0 | 0 | 0.014722 | 0.0036897 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-825_0_4_load_1 | 1 | 0.0042106 | 0.0010553 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-825_0_4_load_2 | 2 | 0.0055353 | 0.0013873 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-825_0_4_load_3 | 3 | 0.0065706 | 0.0016467 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-825_0_4_load_72 | 5 | 0.0045077 | 0.0011297 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-825_0_4_load_59 | 8 | 0.013743 | 0.0034442 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-825_0_4_load_67 | 10 | 0.0075771 | 0.001899 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-825_0_4_load_5 | 12 | 0.0069733 | 0.0017477 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-825_0_4_load_6 | 13 | 0.015894 | 0.0039835 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-825_0_4_load_64 | 20 | 0.003591 | 0.00089998 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-825_0_4_load_23 | 21 | 0.0056107 | 0.0014062 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-825_0_4_load_22 | 22 | 0.019829 | 0.0049696 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-825_0_4_load_18 | 23 | 0.01103 | 0.0027645 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-825_0_4_load_13 | 25 | 0.015343 | 0.0038453 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-825_0_4_load_57 | 28 | 0.0039738 | 0.00099593 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-825_0_4_load_43 | 30 | 0.019102 | 0.0047874 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-825_0_4_load_54 | 31 | 0.0027031 | 0.00067746 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-825_0_4_load_42 | 32 | 0.012813 | 0.0032113 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-825_0_4_load_53 | 33 | 0.011936 | 0.0029913 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-825_0_4_load_25 | 34 | 0.0073935 | 0.001853 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-825_0_4_load_19 | 35 | 0.015191 | 0.0038073 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-825_0_4_load_21 | 36 | 0.0080296 | 0.0020124 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-825_0_4_load_62 | 37 | 0.0050682 | 0.0012702 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-825_0_4_load_47 | 38 | 0.0090336 | 0.002264 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-825_0_4_load_61 | 39 | 0.0057961 | 0.0014526 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-825_0_4_load_24 | 40 | 0.012507 | 0.0031346 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-825_0_4_load_45 | 41 | 0.012249 | 0.00307 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-825_0_4_load_44 | 42 | 0.0094026 | 0.0023565 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-825_0_4_load_78 | 43 | 0.012157 | 0.0030468 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-825_0_4_load_69 | 45 | 0.0046556 | 0.0011668 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-825_0_4_load_70 | 46 | 0.013141 | 0.0032934 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-825_0_4_load_50 | 48 | 0.0061341 | 0.0015373 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-825_0_4_load_46 | 49 | 0.014438 | 0.0036185 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-825_0_4_load_49 | 52 | 0.0046336 | 0.0011613 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-825_0_4_load_36 | 54 | 0.0071134 | 0.0017828 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-825_0_4_load_68 | 55 | 0.012629 | 0.0031651 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-825_0_4_load_77 | 56 | 0.0036444 | 0.00091337 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-825_0_4_load_31 | 57 | 0.018098 | 0.0045358 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-825_0_4_load_32 | 58 | 0.019598 | 0.0049118 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-825_0_4_load_33 | 59 | 0.0040768 | 0.0010217 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-825_0_4_load_34 | 60 | 0.0054046 | 0.0013545 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-825_0_4_load_35 | 61 | 0.011621 | 0.0029126 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-825_0_4_load_37 | 62 | 0.0063526 | 0.0015921 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-825_0_4_load_38 | 63 | 0.00676 | 0.0016942 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-825_0_4_load_39 | 64 | 0.0063545 | 0.0015926 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-825_0_4_load_63 | 67 | 0.0042565 | 0.0010668 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-825_0_4_load_58 | 68 | 0.0043196 | 0.0010826 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-825_0_4_load_71 | 69 | 0.006479 | 0.0016238 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-825_0_4_load_76 | 70 | 0.0051753 | 0.0012971 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-825_0_4_load_75 | 71 | 0.011406 | 0.0028587 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 49 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-825_0_4_line_0 |  | 0 | 1 | 0.0037676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-825_0_4_line_1 |  | 0 | 2 | 0.0020222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-825_0_4_line_2 |  | 1 | 3 | 0.010613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-825_0_4_line_3 |  | 2 | 4 | 0.0059888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-825_0_4_line_4 |  | 3 | 5 | 0.0001604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-825_0_4_line_5 |  | 4 | 6 | 0.008617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-825_0_4_line_6 |  | 5 | 7 | 0.0039176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-825_0_4_line_7 |  | 6 | 8 | 0.0084168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-825_0_4_line_8 |  | 7 | 44 | 0.013832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-825_0_4_line_9 |  | 7 | 71 | 0.0098126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-825_0_4_line_10 |  | 8 | 68 | 0.0026297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-825_0_4_line_11 |  | 9 | 10 | 0.0033211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-825_0_4_line_12 |  | 9 | 11 | 0.012466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-825_0_4_line_13 |  | 11 | 17 | 0.0091671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-825_0_4_line_14 |  | 11 | 13 | 0.0091008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-825_0_4_line_15 |  | 12 | 13 | 0.00093411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-825_0_4_line_16 |  | 12 | 14 | 0.01823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-825_0_4_line_17 |  | 14 | 15 | 0.013456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-825_0_4_line_18 |  | 14 | 16 | 0.016324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_261-825_0_4_line_19 |  | 15 | 18 | 0.001642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_261-825_0_4_line_20 |  | 16 | 19 | 0.006134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_261-825_0_4_line_21 |  | 16 | 20 | 0.0065929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-825_0_4_line_22 |  | 17 | 21 | 0.015916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-825_0_4_line_23 |  | 18 | 22 | 0.010063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-825_0_4_line_24 |  | 18 | 23 | 0.0019075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_261-825_0_4_line_25 |  | 19 | 24 | 0.012092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_261-825_0_4_line_26 |  | 19 | 25 | 0.011043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-825_0_4_line_27 |  | 22 | 38 | 0.0021382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-825_0_4_line_28 |  | 23 | 35 | 0.012911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_261-825_0_4_line_29 |  | 24 | 30 | 0.016258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-825_0_4_line_30 |  | 24 | 31 | 0.012885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_261-825_0_4_line_31 |  | 25 | 29 | 0.0028498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-825_0_4_line_32 |  | 26 | 27 | 0.002844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-825_0_4_line_33 |  | 26 | 28 | 0.0079957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-825_0_4_line_34 |  | 26 | 29 | 0.015704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-825_0_4_line_35 |  | 27 | 34 | 0.0052988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-825_0_4_line_36 |  | 30 | 32 | 0.026952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-825_0_4_line_37 |  | 31 | 33 | 0.0013286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_261-825_0_4_line_38 |  | 32 | 42 | 0.012294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-825_0_4_line_39 |  | 33 | 61 | 0.0072741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_261-825_0_4_line_40 |  | 34 | 40 | 0.004757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-825_0_4_line_41 |  | 35 | 36 | 0.0046622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_261-825_0_4_line_42 |  | 36 | 37 | 0.011396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_261-825_0_4_line_43 |  | 37 | 39 | 0.002038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_261-825_0_4_line_44 |  | 39 | 65 | 0.0096623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_261-825_0_4_line_45 |  | 41 | 42 | 0.013123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-825_0_4_line_46 |  | 43 | 44 | 0.009305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-825_0_4_line_47 |  | 44 | 56 | 0.005574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-825_0_4_line_48 |  | 45 | 46 | 0.0037366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-825_0_4_line_49 |  | 46 | 69 | 0.0048558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-825_0_4_line_50 |  | 47 | 48 | 0.0012078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_261-825_0_4_line_51 |  | 47 | 49 | 0.0028142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_261-825_0_4_line_52 |  | 48 | 53 | 0.017085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_261-825_0_4_line_53 |  | 50 | 51 | 0.001642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-825_0_4_line_54 |  | 50 | 52 | 0.011148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-825_0_4_line_55 |  | 51 | 55 | 0.0044301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-825_0_4_line_56 |  | 51 | 66 | 0.004882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-825_0_4_line_57 |  | 53 | 54 | 0.0061017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_261-825_0_4_line_58 |  | 54 | 60 | 0.0085462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_261-825_0_4_line_59 |  | 57 | 58 | 0.0075064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_261-825_0_4_line_60 |  | 57 | 59 | 0.0062898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_261-825_0_4_line_61 |  | 58 | 60 | 0.0001169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_261-825_0_4_line_62 |  | 59 | 61 | 0.012464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_261-825_0_4_line_63 |  | 62 | 63 | 0.0016551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-825_0_4_line_64 |  | 62 | 64 | 0.0077336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-825_0_4_line_65 |  | 63 | 65 | 0.0099501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_261-825_0_4_line_66 |  | 64 | 66 | 0.0037231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-825_0_4_line_67 |  | 65 | 67 | 0.012308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-825_0_4_line_68 |  | 66 | 68 | 0.0099965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-825_0_4_line_69 |  | 69 | 70 | 0.0080756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-825_0_4_line_70 |  | 70 | 71 | 0.0042178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-825_0_4_trafo_46 | 0.63 MVA 20/0.4 kV | 72 | 49 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2683284.4871 | 1247350.9527 | 2683285.9721 | 1247347.4902
1 | 2683284.4871 | 1247350.9527 | 2683283.69 | 1247352.8112
2 | 2683285.9721 | 1247347.4902 | 2683290.1556 | 1247337.736
3 | 2683281.3294 | 1247358.3151 | 2683283.69 | 1247352.8112
4 | 2683290.2189 | 1247337.5886 | 2683290.1556 | 1247337.736
5 | 2683281.3294 | 1247358.3151 | 2683274.1243 | 1247363.073
6 | 2683291.763 | 1247333.9882 | 2683290.2189 | 1247337.5886
7 | 2683274.1243 | 1247363.073 | 2683266.4228 | 1247359.6774
8 | 2683303.5931 | 1247326.9381 | 2683296.0034 | 1247330.5675 | 2683291.763 | 1247333.9882
9 | 2683291.763 | 1247333.9882 | 2683282.6365 | 1247330.3837
10 | 2683264.0108 | 1247358.6302 | 2683264.5902 | 1247358.8694 | 2683266.4228 | 1247359.6774
11 | 2683216.0881 | 1247409.4259 | 2683219.3253 | 1247408.6842
12 | 2683203.6321 | 1247410.5074 | 2683216.0881 | 1247409.4259
13 | 2683195.6709 | 1247412.6418 | 2683197.3124 | 1247410.3187 | 2683203.6321 | 1247410.5074
14 | 2683203.6321 | 1247410.5074 | 2683203.9011 | 1247401.4106
15 | 2683203.9288 | 1247400.4769 | 2683203.9011 | 1247401.4106
16 | 2683196.9366 | 1247383.8161 | 2683203.9773 | 1247398.837 | 2683203.9288 | 1247400.4769
17 | 2683208.3887 | 1247376.7716 | 2683200.663 | 1247380.9552 | 2683196.9366 | 1247383.8161
18 | 2683182.6746 | 1247375.799 | 2683196.9366 | 1247383.8161
19 | 2683210.0354 | 1247376.7725 | 2683208.3887 | 1247376.7716
20 | 2683182.6746 | 1247375.799 | 2683178.002 | 1247371.8083
21 | 2683182.6746 | 1247375.799 | 2683184.4178 | 1247374.3002 | 2683188.7039 | 1247374.5593
22 | 2683195.6709 | 1247412.6418 | 2683188.9268 | 1247408.7777 | 2683182.0404 | 1247404.4311
23 | 2683210.0354 | 1247376.7725 | 2683212.2513 | 1247366.9561
24 | 2683210.0354 | 1247376.7725 | 2683211.9424 | 1247376.8147
25 | 2683178.002 | 1247371.8083 | 2683183.6362 | 1247361.1017
26 | 2683178.002 | 1247371.8083 | 2683169.6922 | 1247379.0806
27 | 2683212.7221 | 1247364.8704 | 2683212.2513 | 1247366.9561
28 | 2683224.8504 | 1247377.1005 | 2683211.9424 | 1247376.8147
29 | 2683183.6362 | 1247361.1017 | 2683169.0096 | 1247354.0033
30 | 2683183.6362 | 1247361.1017 | 2683188.2593 | 1247355.707 | 2683191.4496 | 1247350.8864
31 | 2683167.5477 | 1247380.9573 | 2683169.6922 | 1247379.0806
32 | 2683153.269 | 1247387.5842 | 2683155.0431 | 1247389.8107
33 | 2683153.269 | 1247387.5842 | 2683146.5095 | 1247391.8553
34 | 2683153.269 | 1247387.5842 | 2683167.5477 | 1247380.9573
35 | 2683155.0431 | 1247389.8107 | 2683159.731 | 1247392.2807
36 | 2683169.0096 | 1247354.0033 | 2683155.9367 | 1247347.6589 | 2683161.0517 | 1247336.3399
37 | 2683192.1829 | 1247349.7784 | 2683191.4496 | 1247350.8864
38 | 2683166.1142 | 1247325.1369 | 2683161.0517 | 1247336.3399
39 | 2683192.1829 | 1247349.7784 | 2683196.1974 | 1247343.7125
40 | 2683159.731 | 1247392.2807 | 2683163.9396 | 1247394.4981
41 | 2683224.8504 | 1247377.1005 | 2683229.5114 | 1247377.2037
42 | 2683240.9048 | 1247377.456 | 2683229.5114 | 1247377.2037
43 | 2683242.9422 | 1247377.5011 | 2683240.9048 | 1247377.456
44 | 2683252.6021 | 1247377.715 | 2683242.9422 | 1247377.5011
45 | 2683171.5185 | 1247313.1779 | 2683166.1142 | 1247325.1369
46 | 2683303.5931 | 1247326.9381 | 2683302.6608 | 1247325.0124 | 2683301.824 | 1247322.2097 | 2683301.9367 | 1247317.9707
47 | 2683303.5931 | 1247326.9381 | 2683305.4092 | 1247328.3201 | 2683308.1191 | 1247328.992 | 2683308.6187 | 1247329.0052
48 | 2683262.9097 | 1247323.5655 | 2683266.454 | 1247324.7488
49 | 2683271.0861 | 1247326.2036 | 2683268.3992 | 1247325.3982 | 2683266.454 | 1247324.7488
50 | 2683224.3184 | 1247347.796 | 2683224.7619 | 1247346.6726
51 | 2683224.3184 | 1247347.796 | 2683224.0378 | 1247348.4147 | 2683223.1569 | 1247350.3594
52 | 2683227.5783 | 1247330.8181 | 2683229.0419 | 1247332.5622 | 2683227.8194 | 1247338.9275 | 2683224.7619 | 1247346.6726
53 | 2683253.1672 | 1247349.858 | 2683254.813 | 1247349.9256
54 | 2683253.1672 | 1247349.858 | 2683250.4616 | 1247349.4197 | 2683242.1578 | 1247348.107
55 | 2683254.813 | 1247349.9256 | 2683254.9671 | 1247345.4981
56 | 2683254.7746 | 1247354.8064 | 2683254.813 | 1247349.9256
57 | 2683227.5783 | 1247330.8181 | 2683223.8095 | 1247330.2426 | 2683221.5311 | 1247330.0203
58 | 2683221.5311 | 1247330.0203 | 2683221.1467 | 1247329.9828 | 2683213.0886 | 1247328.6969
59 | 2683205.5605 | 1247327.4956 | 2683212.9732 | 1247328.6785
60 | 2683202.6853 | 1247333.0898 | 2683205.5605 | 1247327.4956 | 2683205.5605 | 1247327.4956
61 | 2683213.0886 | 1247328.6969 | 2683212.9732 | 1247328.6785
62 | 2683202.6853 | 1247333.0898 | 2683200.8 | 1247336.7579 | 2683196.1974 | 1247343.7125
63 | 2683252.9642 | 1247367.7926 | 2683253.1927 | 1247366.1534
64 | 2683254.2606 | 1247358.4938 | 2683253.1927 | 1247366.1534
65 | 2683252.6021 | 1247377.715 | 2683252.5654 | 1247370.6537 | 2683252.9642 | 1247367.7926
66 | 2683254.7746 | 1247354.8064 | 2683254.2606 | 1247358.4938
67 | 2683252.6021 | 1247377.715 | 2683249.152 | 1247384.5716 | 2683247.7172 | 1247388.9755
68 | 2683254.7746 | 1247354.8064 | 2683257.4255 | 1247355.9111 | 2683264.0108 | 1247358.6302
69 | 2683278.7135 | 1247328.8344 | 2683275.0938 | 1247327.4048 | 2683271.0861 | 1247326.2036
70 | 2683278.7135 | 1247328.8344 | 2683282.6365 | 1247330.3837

## bus_geodata
| x | y | coords
0 | 2683284.4871 | 1247350.9527
1 | 2683285.9721 | 1247347.4902
2 | 2683283.69 | 1247352.8112
3 | 2683290.1556 | 1247337.736
4 | 2683281.3294 | 1247358.3151
5 | 2683290.2189 | 1247337.5886
6 | 2683274.1243 | 1247363.073
7 | 2683291.763 | 1247333.9882
8 | 2683266.4228 | 1247359.6774
9 | 2683216.0881 | 1247409.4259
10 | 2683219.3253 | 1247408.6842
11 | 2683203.6321 | 1247410.5074
12 | 2683203.9288 | 1247400.4769
13 | 2683203.9011 | 1247401.4106
14 | 2683196.9366 | 1247383.8161
15 | 2683208.3887 | 1247376.7716
16 | 2683182.6746 | 1247375.799
17 | 2683195.6709 | 1247412.6418
18 | 2683210.0354 | 1247376.7725
19 | 2683178.002 | 1247371.8083
20 | 2683188.7039 | 1247374.5593
21 | 2683182.0404 | 1247404.4311
22 | 2683212.2513 | 1247366.9561
23 | 2683211.9424 | 1247376.8147
24 | 2683183.6362 | 1247361.1017
25 | 2683169.6922 | 1247379.0806
26 | 2683153.269 | 1247387.5842
27 | 2683155.0431 | 1247389.8107
28 | 2683146.5095 | 1247391.8553
29 | 2683167.5477 | 1247380.9573
30 | 2683169.0097 | 1247354.0033
31 | 2683191.4496 | 1247350.8864
32 | 2683161.0517 | 1247336.3399
33 | 2683192.1829 | 1247349.7784
34 | 2683159.731 | 1247392.2807
35 | 2683224.8504 | 1247377.1005
36 | 2683229.5114 | 1247377.2037
37 | 2683240.9048 | 1247377.456
38 | 2683212.7221 | 1247364.8704
39 | 2683242.9422 | 1247377.5011
40 | 2683163.9396 | 1247394.4981
41 | 2683171.5185 | 1247313.1779
42 | 2683166.1142 | 1247325.1369
43 | 2683301.9367 | 1247317.9707
44 | 2683303.5931 | 1247326.9381
45 | 2683262.9097 | 1247323.5655
46 | 2683266.454 | 1247324.7488
47 | 2683224.3184 | 1247347.796
48 | 2683224.7619 | 1247346.6726
49 | 2683223.1569 | 1247350.3594
50 | 2683253.1672 | 1247349.858
51 | 2683254.813 | 1247349.9256
52 | 2683242.1578 | 1247348.107
53 | 2683227.5783 | 1247330.8181
54 | 2683221.5311 | 1247330.0203
55 | 2683254.9671 | 1247345.4981
56 | 2683308.6187 | 1247329.0052
57 | 2683205.5605 | 1247327.4956
58 | 2683212.9732 | 1247328.6785
59 | 2683202.6853 | 1247333.0898
60 | 2683213.0886 | 1247328.6969
61 | 2683196.1974 | 1247343.7125
62 | 2683253.1927 | 1247366.1534
63 | 2683252.9642 | 1247367.7926
64 | 2683254.2606 | 1247358.4938
65 | 2683252.6021 | 1247377.715
66 | 2683254.7746 | 1247354.8064
67 | 2683247.7172 | 1247388.9755
68 | 2683264.0108 | 1247358.6302
69 | 2683271.0861 | 1247326.2036
70 | 2683278.7135 | 1247328.8344
71 | 2683282.6365 | 1247330.3837
72 | 2683224.3184 | 1247347.796

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98192 | -0.34845 | 0.014722 | 0.0036897
1 | 0.98167 | -0.35335 | 0.0042106 | 0.0010553
2 | 0.98208 | -0.34528 | 0.0055353 | 0.0013873
3 | 0.981 | -0.36636 | 0.0065706 | 0.0016467
4 | 0.98259 | -0.33531 | 0 | 0
5 | 0.981 | -0.36654 | 0.0045077 | 0.0011297
6 | 0.98333 | -0.32097 | 0 | 0
7 | 0.98079 | -0.37056 | 0 | 0
8 | 0.98404 | -0.30699 | 0.013743 | 0.0034442
9 | 0.98922 | -0.20666 | 0 | 0
10 | 0.9892 | -0.20711 | 0.0075771 | 0.001899
11 | 0.98931 | -0.20498 | 0 | 0
12 | 0.98944 | -0.20236 | 0.0069733 | 0.0017477
13 | 0.98942 | -0.20284 | 0.015894 | 0.0039835
14 | 0.99005 | -0.19067 | 0 | 0
15 | 0.98935 | -0.20415 | 0 | 0
16 | 0.99103 | -0.17172 | 0 | 0
17 | 0.98926 | -0.2059 | 0 | 0
18 | 0.98926 | -0.2058 | 0 | 0
19 | 0.9914 | -0.16452 | 0 | 0
20 | 0.99101 | -0.17214 | 0.003591 | 0.00089998
21 | 0.98918 | -0.20749 | 0.0056107 | 0.0014062
22 | 0.989 | -0.21097 | 0.019829 | 0.0049696
23 | 0.98918 | -0.20746 | 0.01103 | 0.0027645
24 | 0.99225 | -0.14823 | 0 | 0
25 | 0.99101 | -0.1722 | 0.015343 | 0.0038453
26 | 0.9906 | -0.18006 | 0 | 0
27 | 0.99055 | -0.18107 | 0 | 0
28 | 0.99057 | -0.18063 | 0.0039738 | 0.00099593
29 | 0.99094 | -0.17341 | 0 | 0
30 | 0.99145 | -0.16366 | 0.019102 | 0.0047874
31 | 0.99331 | -0.12785 | 0.0027031 | 0.00067746
32 | 0.9906 | -0.18014 | 0.012813 | 0.0032113
33 | 0.99342 | -0.12574 | 0.011936 | 0.0029913
34 | 0.99045 | -0.18294 | 0.0073935 | 0.001853
35 | 0.98863 | -0.21813 | 0.015191 | 0.0038073
36 | 0.98844 | -0.22166 | 0.0080296 | 0.0020124
37 | 0.98802 | -0.22991 | 0.0050682 | 0.0012702
38 | 0.98898 | -0.21131 | 0.0090336 | 0.002264
39 | 0.98794 | -0.23134 | 0.0057961 | 0.0014526
40 | 0.9904 | -0.184 | 0.012507 | 0.0031346
41 | 0.99021 | -0.18773 | 0.012249 | 0.00307
42 | 0.99036 | -0.18487 | 0.0094026 | 0.0023565
43 | 0.98048 | -0.37657 | 0.012157 | 0.0030468
44 | 0.98059 | -0.37452 | 0 | 0
45 | 0.98003 | -0.38552 | 0.0046556 | 0.0011668
46 | 0.98004 | -0.3852 | 0.013141 | 0.0032934
47 | 0.99971 | -0.0054509 | 0 | 0
48 | 0.99959 | -0.0077912 | 0.0061341 | 0.0015373
49 | 1 | 0 | -0.45075 | -0.11439
50 | 0.98524 | -0.28382 | 0 | 0
51 | 0.98524 | -0.28368 | 0 | 0
52 | 0.98519 | -0.28475 | 0.0046336 | 0.0011613
53 | 0.99787 | -0.0405 | 0 | 0
54 | 0.99726 | -0.052209 | 0.0071134 | 0.0017828
55 | 0.98519 | -0.28469 | 0.012629 | 0.0031651
56 | 0.98057 | -0.37489 | 0.0036444 | 0.00091337
57 | 0.9957 | -0.081974 | 0.018098 | 0.0045358
58 | 0.9964 | -0.068584 | 0.019598 | 0.0049118
59 | 0.99514 | -0.092707 | 0.0040768 | 0.0010217
60 | 0.99641 | -0.068366 | 0.0054046 | 0.0013545
61 | 0.99404 | -0.11379 | 0.011621 | 0.0029126
62 | 0.98672 | -0.25509 | 0.0063526 | 0.0015921
63 | 0.98693 | -0.25094 | 0.00676 | 0.0016942
64 | 0.98576 | -0.27365 | 0.0063545 | 0.0015926
65 | 0.9876 | -0.23786 | 0 | 0
66 | 0.98532 | -0.28217 | 0 | 0
67 | 0.98756 | -0.2388 | 0.0042565 | 0.0010668
68 | 0.9843 | -0.30198 | 0.0043196 | 0.0010826
69 | 0.98012 | -0.38364 | 0.006479 | 0.0016238
70 | 0.9803 | -0.38008 | 0.0051753 | 0.0012971
71 | 0.98042 | -0.37783 | 0.011406 | 0.0028587
72 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.072045 | 0.018093 | -0.072028 | -0.018082 | 1.6845e-05 | 1.0733e-05 | 0.10919 | 0.10919 | 0.10919 | 0.98192 | -0.34845 | 0.98167 | -0.35335 | 29.9975
1 | -0.086767 | -0.021783 | 0.08678 | 0.021791 | 1.3113e-05 | 8.3668e-06 | 0.1315 | 0.1315 | 0.1315 | 0.98192 | -0.34845 | 0.98208 | -0.34528 | 36.1266
2 | 0.067817 | 0.017027 | -0.067775 | -0.017 | 4.2067e-05 | 2.6789e-05 | 0.10281 | 0.10281 | 0.10281 | 0.98167 | -0.35335 | 0.981 | -0.36636 | 28.244
3 | -0.092315 | -0.023178 | 0.092359 | 0.023206 | 4.3947e-05 | 2.8051e-05 | 0.13989 | 0.13989 | 0.13989 | 0.98208 | -0.34528 | 0.98259 | -0.33531 | 38.4307
4 | 0.061205 | 0.015353 | -0.061204 | -0.015353 | 5.1847e-07 | 3.298e-07 | 0.092842 | 0.092842 | 0.092842 | 0.981 | -0.36636 | 0.981 | -0.36654 | 25.506
5 | -0.092359 | -0.023206 | 0.092422 | 0.023247 | 6.3233e-05 | 4.036e-05 | 0.13989 | 0.13989 | 0.13989 | 0.98259 | -0.33531 | 0.98333 | -0.32097 | 38.4307
6 | 0.056696 | 0.014223 | -0.056685 | -0.014216 | 1.0866e-05 | 6.9051e-06 | 0.086004 | 0.086004 | 0.086004 | 0.981 | -0.36654 | 0.98079 | -0.37056 | 23.6276
7 | -0.092422 | -0.023247 | 0.092484 | 0.023286 | 6.1764e-05 | 3.9422e-05 | 0.13989 | 0.13989 | 0.13989 | 0.98333 | -0.32097 | 0.98404 | -0.30699 | 38.4307
8 | 0.015806 | 0.0039625 | -0.015803 | -0.0039608 | 2.9828e-06 | 1.7345e-06 | 0.02398 | 0.02398 | 0.02398 | 0.98079 | -0.37056 | 0.98059 | -0.37452 | 6.588
9 | 0.04088 | 0.010254 | -0.040866 | -0.010245 | 1.4156e-05 | 8.936e-06 | 0.062024 | 0.062024 | 0.062024 | 0.98079 | -0.37056 | 0.98042 | -0.37783 | 17.0396
10 | -0.10623 | -0.02673 | 0.10625 | 0.026747 | 2.5456e-05 | 1.6258e-05 | 0.16067 | 0.16067 | 0.16067 | 0.98404 | -0.30699 | 0.9843 | -0.30198 | 44.1397
11 | 0.0075773 | 0.0018991 | -0.0075771 | -0.001899 | 1.618e-07 | 6.0914e-08 | 0.011398 | 0.011398 | 0.011398 | 0.98922 | -0.20666 | 0.9892 | -0.20711 | 3.1313
12 | -0.0075773 | -0.0018991 | 0.0075779 | 0.0018993 | 6.0731e-07 | 2.2863e-07 | 0.011398 | 0.011398 | 0.011398 | 0.98922 | -0.20666 | 0.98931 | -0.20498 | 3.1313
13 | 0.0056114 | 0.0014063 | -0.0056111 | -0.0014062 | 2.4488e-07 | 3.9022e-08 | 0.0084401 | 0.0084401 | 0.0084401 | 0.98931 | -0.20498 | 0.98926 | -0.2059 | 2.3187
14 | -0.013189 | -0.0033056 | 0.013191 | 0.0033063 | 1.3431e-06 | 7.4271e-07 | 0.019838 | 0.019838 | 0.019838 | 0.98931 | -0.20498 | 0.98942 | -0.20284 | 5.45
15 | 0.029086 | 0.0072903 | -0.029085 | -0.0072898 | 6.7023e-07 | 4.1695e-07 | 0.043742 | 0.043742 | 0.043742 | 0.98944 | -0.20236 | 0.98942 | -0.20284 | 12.017
16 | -0.036059 | -0.0090379 | 0.036079 | 0.0090506 | 2.0104e-05 | 1.2632e-05 | 0.054229 | 0.054229 | 0.054229 | 0.98944 | -0.20236 | 0.99005 | -0.19067 | 14.8981
17 | 0.22637 | 0.057171 | -0.22622 | -0.057078 | 0.00014616 | 9.285e-05 | 0.34038 | 0.34038 | 0.34038 | 0.99005 | -0.19067 | 0.98935 | -0.20415 | 23.378
18 | -0.26245 | -0.066222 | 0.26269 | 0.066373 | 0.00023831 | 0.00015168 | 0.39461 | 0.39461 | 0.39461 | 0.99005 | -0.19067 | 0.99103 | -0.17172 | 27.1025
19 | 0.22622 | 0.057078 | -0.22621 | -0.057067 | 1.7835e-05 | 1.133e-05 | 0.34038 | 0.34038 | 0.34038 | 0.98935 | -0.20415 | 0.98926 | -0.2058 | 23.378
20 | -0.26628 | -0.067273 | 0.26637 | 0.067332 | 9.2012e-05 | 5.8571e-05 | 0.4 | 0.4 | 0.4 | 0.99103 | -0.17172 | 0.9914 | -0.16452 | 27.4728
21 | 0.0035911 | 0.00089995 | -0.003591 | -0.00089998 | 7.1878e-08 | -3.8946e-08 | 0.0053919 | 0.0053919 | 0.0053919 | 0.99103 | -0.17172 | 0.99101 | -0.17214 | 1.4813
22 | 0.0056111 | 0.0014062 | -0.0056107 | -0.0014062 | 4.2517e-07 | 6.778e-08 | 0.0084401 | 0.0084402 | 0.0084402 | 0.98926 | -0.2059 | 0.98918 | -0.20749 | 2.3187
23 | 0.02887 | 0.0072382 | -0.028863 | -0.0072337 | 7.1166e-06 | 4.4255e-06 | 0.043426 | 0.043426 | 0.043426 | 0.98926 | -0.2058 | 0.989 | -0.21097 | 11.9303
24 | 0.19734 | 0.049829 | -0.19732 | -0.049819 | 1.5769e-05 | 9.9944e-06 | 0.29696 | 0.29696 | 0.29696 | 0.98926 | -0.2058 | 0.98918 | -0.20746 | 20.3954
25 | -0.30561 | -0.077177 | 0.30585 | 0.077329 | 0.00023874 | 0.00015217 | 0.45891 | 0.45891 | 0.45891 | 0.9914 | -0.16452 | 0.99225 | -0.14823 | 31.5185
26 | 0.039244 | 0.0098454 | -0.03923 | -0.0098363 | 1.4369e-05 | 9.0538e-06 | 0.058906 | 0.058906 | 0.058906 | 0.9914 | -0.16452 | 0.99101 | -0.1722 | 16.1831
27 | 0.0090338 | 0.0022641 | -0.0090336 | -0.002264 | 1.4813e-07 | 6.7366e-08 | 0.013592 | 0.013592 | 0.013592 | 0.989 | -0.21097 | 0.98898 | -0.21131 | 3.7341
28 | 0.18629 | 0.047054 | -0.18619 | -0.046994 | 9.5144e-05 | 6.023e-05 | 0.28036 | 0.28036 | 0.28036 | 0.98918 | -0.20746 | 0.98863 | -0.21813 | 19.2558
29 | 0.05364 | 0.013471 | -0.053601 | -0.013446 | 3.9461e-05 | 2.5045e-05 | 0.080451 | 0.080451 | 0.080451 | 0.99225 | -0.14823 | 0.99145 | -0.16366 | 22.102
30 | -0.35949 | -0.0908 | 0.35984 | 0.091025 | 0.00035142 | 0.00022424 | 0.53936 | 0.53936 | 0.53936 | 0.99225 | -0.14823 | 0.99331 | -0.12785 | 37.044
31 | 0.023887 | 0.005991 | -0.023886 | -0.0059902 | 1.3749e-06 | 8.4321e-07 | 0.035869 | 0.035869 | 0.035869 | 0.99101 | -0.1722 | 0.99094 | -0.17341 | 9.854
32 | 0.019904 | 0.0049896 | -0.019903 | -0.004989 | 9.5342e-07 | 5.7358e-07 | 0.029899 | 0.029899 | 0.029899 | 0.9906 | -0.18006 | 0.99055 | -0.18107 | 8.2141
33 | 0.0039739 | 0.00099589 | -0.0039738 | -0.00099593 | 1.0684e-07 | -3.4554e-08 | 0.0059693 | 0.0059694 | 0.0059694 | 0.9906 | -0.18006 | 0.99057 | -0.18063 | 1.6399
34 | -0.023878 | -0.0059855 | 0.023886 | 0.0059902 | 7.5765e-06 | 4.6467e-06 | 0.035869 | 0.035869 | 0.035869 | 0.9906 | -0.18006 | 0.99094 | -0.17341 | 9.854
35 | 0.019903 | 0.004989 | -0.019902 | -0.004988 | 1.7764e-06 | 1.0687e-06 | 0.029899 | 0.029899 | 0.029899 | 0.99055 | -0.18107 | 0.99045 | -0.18294 | 8.2141
36 | 0.034499 | 0.0086587 | -0.034472 | -0.0086417 | 2.7101e-05 | 1.6997e-05 | 0.051782 | 0.051782 | 0.051782 | 0.99145 | -0.16366 | 0.9906 | -0.18014 | 14.2258
37 | -0.36255 | -0.091702 | 0.36258 | 0.091726 | 3.6781e-05 | 2.3471e-05 | 0.54341 | 0.54341 | 0.54341 | 0.99331 | -0.12785 | 0.99342 | -0.12574 | 37.3221
38 | 0.021658 | 0.0054303 | -0.021654 | -0.0054274 | 4.8799e-06 | 2.9649e-06 | 0.032535 | 0.032535 | 0.032535 | 0.9906 | -0.18014 | 0.99036 | -0.18487 | 8.9381
39 | -0.37452 | -0.094717 | 0.37473 | 0.094854 | 0.00021484 | 0.00013712 | 0.56129 | 0.56129 | 0.56129 | 0.99342 | -0.12574 | 0.99404 | -0.11379 | 38.55
40 | 0.012508 | 0.003135 | -0.012507 | -0.0031346 | 6.2993e-07 | 3.4193e-07 | 0.018792 | 0.018792 | 0.018792 | 0.99045 | -0.18294 | 0.9904 | -0.184 | 5.1625
41 | 0.171 | 0.043187 | -0.17097 | -0.043168 | 2.8981e-05 | 1.8309e-05 | 0.2575 | 0.2575 | 0.2575 | 0.98863 | -0.21813 | 0.98844 | -0.22166 | 17.6854
42 | 0.16294 | 0.041156 | -0.16288 | -0.041115 | 6.4345e-05 | 4.0597e-05 | 0.24541 | 0.24541 | 0.24541 | 0.98844 | -0.22166 | 0.98802 | -0.22991 | 16.8552
43 | 0.15781 | 0.039845 | -0.1578 | -0.039838 | 1.0802e-05 | 6.809e-06 | 0.23778 | 0.23778 | 0.23778 | 0.98802 | -0.22991 | 0.98794 | -0.23134 | 16.331
44 | 0.152 | 0.038386 | -0.15196 | -0.038356 | 4.7523e-05 | 2.992e-05 | 0.22905 | 0.22905 | 0.22905 | 0.98794 | -0.23134 | 0.9876 | -0.23786 | 15.7314
45 | -0.012249 | -0.00307 | 0.012251 | 0.0030709 | 1.6675e-06 | 8.9835e-07 | 0.018407 | 0.018407 | 0.018407 | 0.99021 | -0.18773 | 0.99036 | -0.18487 | 5.057
46 | -0.012157 | -0.0030468 | 0.012158 | 0.0030475 | 1.1878e-06 | 6.4281e-07 | 0.01845 | 0.01845 | 0.01845 | 0.98048 | -0.37657 | 0.98059 | -0.37452 | 5.0687
47 | 0.0036444 | 0.00091334 | -0.0036444 | -0.00091337 | 6.3929e-08 | -2.9399e-08 | 0.0055303 | 0.0055303 | 0.0055303 | 0.98059 | -0.37452 | 0.98057 | -0.37489 | 1.5193
48 | -0.0046556 | -0.0011668 | 0.0046557 | 0.0011668 | 7.0017e-08 | -2.2731e-09 | 0.0070688 | 0.0070688 | 0.0070688 | 0.98003 | -0.38552 | 0.98004 | -0.3852 | 1.942
49 | -0.017797 | -0.0044602 | 0.017798 | 0.004461 | 1.3295e-06 | 7.8969e-07 | 0.027021 | 0.027021 | 0.027021 | 0.98004 | -0.3852 | 0.98012 | -0.38364 | 7.4233
50 | 0.44898 | 0.11431 | -0.44893 | -0.11428 | 5.0664e-05 | 3.2362e-05 | 0.66891 | 0.66891 | 0.66891 | 0.99971 | -0.0054509 | 0.99959 | -0.0077912 | 45.9416
51 | -0.44898 | -0.11431 | 0.4491 | 0.11439 | 0.00011805 | 7.5404e-05 | 0.66891 | 0.66891 | 0.66891 | 0.99971 | -0.0054509 | 1 | 0 | 45.9416
52 | 0.44279 | 0.11274 | -0.4421 | -0.1123 | 0.00069725 | 0.00044534 | 0.65978 | 0.65978 | 0.65978 | 0.99959 | -0.0077912 | 0.99787 | -0.0405 | 45.3145
53 | -0.0046338 | -0.0011613 | 0.0046339 | 0.0011613 | 3.0159e-08 | -1.6088e-09 | 0.0069985 | 0.0069985 | 0.0069985 | 0.98524 | -0.28382 | 0.98524 | -0.28368 | 1.9227
54 | 0.0046338 | 0.0011613 | -0.0046336 | -0.0011613 | 2.0476e-07 | -1.0914e-08 | 0.0069985 | 0.0069986 | 0.0069986 | 0.98524 | -0.28382 | 0.98519 | -0.28475 | 1.9227
55 | 0.012629 | 0.0031654 | -0.012629 | -0.0031651 | 6.0442e-07 | 3.3041e-07 | 0.019074 | 0.019074 | 0.019074 | 0.98524 | -0.28368 | 0.98519 | -0.28469 | 5.2402
56 | -0.017263 | -0.0043267 | 0.017264 | 0.0043274 | 1.2445e-06 | 7.3431e-07 | 0.026073 | 0.026073 | 0.026073 | 0.98524 | -0.28368 | 0.98532 | -0.28217 | 7.1628
57 | 0.4421 | 0.1123 | -0.44185 | -0.11214 | 0.00024901 | 0.00015905 | 0.65978 | 0.65978 | 0.65978 | 0.99787 | -0.0405 | 0.99726 | -0.052209 | 45.3145
58 | 0.43473 | 0.11036 | -0.43439 | -0.11014 | 0.00033764 | 0.00021565 | 0.64916 | 0.64916 | 0.64916 | 0.99726 | -0.052209 | 0.99641 | -0.068366 | 44.5855
59 | -0.40912 | -0.1037 | 0.40939 | 0.10387 | 0.00026343 | 0.0001682 | 0.61183 | 0.61183 | 0.61183 | 0.9957 | -0.081974 | 0.9964 | -0.068584 | 42.021
60 | 0.39103 | 0.099167 | -0.39082 | -0.099038 | 0.00020165 | 0.00012873 | 0.58478 | 0.58478 | 0.58478 | 0.9957 | -0.081974 | 0.99514 | -0.092707 | 40.1634
61 | -0.42899 | -0.10878 | 0.42899 | 0.10879 | 4.5042e-06 | 2.8766e-06 | 0.64109 | 0.64109 | 0.64109 | 0.9964 | -0.068584 | 0.99641 | -0.068366 | 44.0312
62 | 0.38675 | 0.098016 | -0.38636 | -0.097767 | 0.0003913 | 0.00024978 | 0.57868 | 0.57868 | 0.57868 | 0.99514 | -0.092707 | 0.99404 | -0.11379 | 39.7448
63 | -0.14082 | -0.035518 | 0.14085 | 0.035536 | 2.8012e-05 | 1.7906e-05 | 0.21244 | 0.21244 | 0.21244 | 0.98672 | -0.25509 | 0.98693 | -0.25094 | 58.3635
64 | 0.13447 | 0.033926 | -0.13435 | -0.03385 | 0.00011935 | 7.6285e-05 | 0.20286 | 0.20286 | 0.20286 | 0.98672 | -0.25509 | 0.98576 | -0.27365 | 55.7317
65 | -0.14761 | -0.03723 | 0.1477 | 0.037289 | 9.2474e-05 | 5.8929e-05 | 0.22264 | 0.22264 | 0.22264 | 0.98693 | -0.25094 | 0.9876 | -0.23786 | 30.5818
66 | 0.12799 | 0.032257 | -0.12794 | -0.032224 | 5.2151e-05 | 3.3329e-05 | 0.19327 | 0.19327 | 0.19327 | 0.98576 | -0.27365 | 0.98532 | -0.28217 | 53.0964
67 | 0.0042566 | 0.0010667 | -0.0042565 | -0.0010668 | 1.8984e-07 | -3.5984e-08 | 0.0064134 | 0.0064135 | 0.0064135 | 0.9876 | -0.23786 | 0.98756 | -0.2388 | 1.7619
68 | 0.11068 | 0.027896 | -0.11057 | -0.027829 | 0.0001048 | 6.6942e-05 | 0.1672 | 0.1672 | 0.1672 | 0.98532 | -0.28217 | 0.9843 | -0.30198 | 45.9336
69 | -0.024277 | -0.0060848 | 0.024281 | 0.0060873 | 4.1139e-06 | 2.5311e-06 | 0.036857 | 0.036857 | 0.036857 | 0.98012 | -0.38364 | 0.9803 | -0.38008 | 10.1256
70 | -0.029456 | -0.0073844 | 0.029459 | 0.0073864 | 3.1622e-06 | 1.9706e-06 | 0.044713 | 0.044713 | 0.044713 | 0.9803 | -0.38008 | 0.98042 | -0.37783 | 12.2837

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46518 | 0.11801

## res_load
| p_mw | q_mvar
0 | 0.014722 | 0.0036897
1 | 0.0042106 | 0.0010553
2 | 0.0055353 | 0.0013873
3 | 0.0065706 | 0.0016467
4 | 0.0045077 | 0.0011297
5 | 0.013743 | 0.0034442
6 | 0.0075771 | 0.001899
7 | 0.0069733 | 0.0017477
8 | 0.015894 | 0.0039835
9 | 0.003591 | 0.00089998
10 | 0.0056107 | 0.0014062
11 | 0.019829 | 0.0049696
12 | 0.01103 | 0.0027645
13 | 0.015343 | 0.0038453
14 | 0.0039738 | 0.00099593
15 | 0.019102 | 0.0047874
16 | 0.0027031 | 0.00067746
17 | 0.012813 | 0.0032113
18 | 0.011936 | 0.0029913
19 | 0.0073935 | 0.001853
20 | 0.015191 | 0.0038073
21 | 0.0080296 | 0.0020124
22 | 0.0050682 | 0.0012702
23 | 0.0090336 | 0.002264
24 | 0.0057961 | 0.0014526
25 | 0.012507 | 0.0031346
26 | 0.012249 | 0.00307
27 | 0.0094026 | 0.0023565
28 | 0.012157 | 0.0030468
29 | 0.0046556 | 0.0011668
30 | 0.013141 | 0.0032934
31 | 0.0061341 | 0.0015373
32 | 0.014438 | 0.0036185
33 | 0.0046336 | 0.0011613
34 | 0.0071134 | 0.0017828
35 | 0.012629 | 0.0031651
36 | 0.0036444 | 0.00091337
37 | 0.018098 | 0.0045358
38 | 0.019598 | 0.0049118
39 | 0.0040768 | 0.0010217
40 | 0.0054046 | 0.0013545
41 | 0.011621 | 0.0029126
42 | 0.0063526 | 0.0015921
43 | 0.00676 | 0.0016942
44 | 0.0063545 | 0.0015926
45 | 0.0042565 | 0.0010668
46 | 0.0043196 | 0.0010826
47 | 0.006479 | 0.0016238
48 | 0.0051753 | 0.0012971
49 | 0.011406 | 0.0028587

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1