## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-827_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-827_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-827_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-827_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-827_0_3_node_22 | 0.4 | n |  | TRUE
5 | bus_LV_261-827_0_3_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_261-827_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_261-827_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-827_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_261-827_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_261-827_0_3_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_261-827_0_3_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_261-827_0_3_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_261-827_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_261-827_0_3_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_261-827_0_3_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_261-827_0_3_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_261-827_0_3_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_261-827_0_3_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_261-827_0_3_node_18 | 0.4 | n |  | TRUE
20 | bus_MV_537_0_node_73 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-827_0_3_load_0 | 0 | 0.0036568 | 0.00091649 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-827_0_3_load_1 | 1 | 0.0058153 | 0.0014574 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-827_0_3_load_4 | 3 | 0.023754 | 0.0059534 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-827_0_3_load_22 | 4 | 0.015406 | 0.0038612 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-827_0_3_load_20 | 5 | 0.0072714 | 0.0018224 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-827_0_3_load_5 | 6 | 0.02203 | 0.0055212 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-827_0_3_load_6 | 7 | 0.036947 | 0.0092599 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-827_0_3_load_8 | 8 | 0.014944 | 0.0037452 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-827_0_3_load_9 | 9 | 0.013386 | 0.0033548 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-827_0_3_load_13 | 11 | 0.011327 | 0.0028387 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-827_0_3_load_11 | 12 | 0.017912 | 0.0044891 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-827_0_3_load_14 | 13 | 0.011341 | 0.0028423 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-827_0_3_load_15 | 14 | 0.013639 | 0.0034181 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-827_0_3_load_16 | 15 | 0.014938 | 0.0037437 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-827_0_3_load_21 | 16 | 0.010948 | 0.0027438 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-827_0_3_load_17 | 18 | 0.015253 | 0.0038228 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-827_0_3_load_18 | 19 | 0.032853 | 0.0082338 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-827_0_3_line_0 |  | 0 | 1 | 0.0062036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-827_0_3_line_1 |  | 0 | 2 | 0.011535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-827_0_3_line_2 |  | 2 | 3 | 0.00015105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-827_0_3_line_3 |  | 3 | 4 | 0.016746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-827_0_3_line_4 |  | 4 | 5 | 0.023496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-827_0_3_line_5 |  | 5 | 19 | 0.0015063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-827_0_3_line_6 |  | 6 | 7 | 0.021624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-827_0_3_line_7 |  | 7 | 8 | 0.016529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-827_0_3_line_8 |  | 8 | 9 | 0.005779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-827_0_3_line_9 |  | 9 | 10 | 0.016326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-827_0_3_line_10 |  | 10 | 11 | 0.030837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-827_0_3_line_11 |  | 10 | 12 | 0.011856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-827_0_3_line_12 |  | 11 | 13 | 0.014538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-827_0_3_line_13 |  | 13 | 14 | 0.003701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-827_0_3_line_14 |  | 14 | 15 | 0.0068529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-827_0_3_line_15 |  | 15 | 16 | 0.0098208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-827_0_3_line_16 |  | 16 | 17 | 0.026564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-827_0_3_line_17 |  | 17 | 18 | 0.014232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-827_0_3_line_18 |  | 18 | 19 | 0.026295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-827_0_3_trafo_14 | 0.63 MVA 20/0.4 kV | 20 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2683630.6179 | 1248481.3436 | 2683624.7156 | 1248479.4337
1 | 2683641.5928 | 1248484.8948 | 2683630.6179 | 1248481.3436
2 | 2683641.5928 | 1248484.8948 | 2683641.7375 | 1248484.938
3 | 2683641.7375 | 1248484.938 | 2683657.7854 | 1248489.7222
4 | 2683680.3021 | 1248496.4349 | 2683657.7854 | 1248489.7222
5 | 2683680.3021 | 1248496.4349 | 2683681.7457 | 1248496.8652
6 | 2683627.1066 | 1248555.4113 | 2683644.9707 | 1248567.5961
7 | 2683658.6257 | 1248576.91 | 2683644.9707 | 1248567.5961
8 | 2683658.6257 | 1248576.91 | 2683663.3999 | 1248580.1664
9 | 2683676.9511 | 1248589.271 | 2683669.9852 | 1248584.6581 | 2683663.3999 | 1248580.1664
10 | 2683676.9511 | 1248589.271 | 2683685.2275 | 1248570.0736 | 2683690.2956 | 1248561.5326
11 | 2683676.9511 | 1248589.271 | 2683672.4552 | 1248600.2416
12 | 2683690.2956 | 1248561.5326 | 2683696.2595 | 1248551.4822 | 2683697.7144 | 1248549.03
13 | 2683699.6029 | 1248545.8471 | 2683697.7144 | 1248549.03
14 | 2683699.6029 | 1248545.8471 | 2683703.0997 | 1248539.9534
15 | 2683703.0997 | 1248539.9534 | 2683708.111 | 1248531.5074
16 | 2683720.6689 | 1248508.1391 | 2683716.2272 | 1248517.828 | 2683708.111 | 1248531.5074
17 | 2683720.6689 | 1248508.1391 | 2683713.9244 | 1248506.0201 | 2683707.0164 | 1248504.1272
18 | 2683681.7457 | 1248496.8652 | 2683695.7411 | 1248501.0375 | 2683707.0164 | 1248504.1272

## bus_geodata
| x | y | coords
0 | 2683630.6179 | 1248481.3436
1 | 2683624.7156 | 1248479.4337
2 | 2683641.5928 | 1248484.8948
3 | 2683641.7375 | 1248484.938
4 | 2683657.7854 | 1248489.7222
5 | 2683680.3021 | 1248496.4349
6 | 2683627.1066 | 1248555.4113
7 | 2683644.9707 | 1248567.5961
8 | 2683658.6257 | 1248576.91
9 | 2683663.3998 | 1248580.1664
10 | 2683676.9511 | 1248589.271
11 | 2683690.2956 | 1248561.5326
12 | 2683672.4552 | 1248600.2416
13 | 2683697.7144 | 1248549.03
14 | 2683699.6029 | 1248545.8471
15 | 2683703.0997 | 1248539.9534
16 | 2683708.111 | 1248531.5074
17 | 2683720.6689 | 1248508.1391
18 | 2683707.0164 | 1248504.1272
19 | 2683681.7457 | 1248496.8652
20 | 2683676.9511 | 1248589.271

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99016 | -0.18934 | 0.0036568 | 0.00091649
1 | 0.99013 | -0.18998 | 0.0058153 | 0.0014574
2 | 0.99026 | -0.18739 | 0 | 0
3 | 0.99026 | -0.18737 | 0.023754 | 0.0059534
4 | 0.99077 | -0.17748 | 0.015406 | 0.0038612
5 | 0.99182 | -0.15722 | 0.0072714 | 0.0018224
6 | 0.99248 | -0.14476 | 0.02203 | 0.0055212
7 | 0.99291 | -0.13633 | 0.036947 | 0.0092599
8 | 0.9938 | -0.11911 | 0.014944 | 0.0037452
9 | 0.99419 | -0.11158 | 0.013386 | 0.0033548
10 | 0.99549 | -0.086475 | 0 | 0
11 | 0.99845 | -0.029578 | 0.011327 | 0.0028387
12 | 0.9953 | -0.090211 | 0.017912 | 0.0044891
13 | 1 | 0 | -0.26323 | -0.066138
14 | 0.99976 | -0.0046307 | 0.013639 | 0.0034181
15 | 0.99894 | -0.020166 | 0.014938 | 0.0037437
16 | 0.99791 | -0.039907 | 0.010948 | 0.0027438
17 | 0.99538 | -0.08839 | 0 | 0
18 | 0.99403 | -0.11447 | 0.015253 | 0.0038228
19 | 0.99189 | -0.15572 | 0.032853 | 0.0082338
20 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0058154 | 0.0014575 | -0.0058153 | -0.0014574 | 1.7768e-07 | 3.3927e-08 | 0.0087395 | 0.0087395 | 0.0087395 | 0.99016 | -0.18934 | 0.99013 | -0.18998 | 2.401
1 | -0.0094723 | -0.002374 | 0.0094731 | 0.0023744 | 8.7653e-07 | 4.1259e-07 | 0.014235 | 0.014235 | 0.014235 | 0.99016 | -0.18934 | 0.99026 | -0.18739 | 3.9107
2 | -0.0094731 | -0.0023744 | 0.0094732 | 0.0023744 | 1.1479e-08 | 5.4023e-09 | 0.014235 | 0.014235 | 0.014235 | 0.99026 | -0.18739 | 0.99026 | -0.18737 | 3.9107
3 | -0.033227 | -0.0083278 | 0.033243 | 0.0083376 | 1.5655e-05 | 9.8035e-06 | 0.049929 | 0.049929 | 0.049929 | 0.99026 | -0.18737 | 0.99077 | -0.17748 | 13.7168
4 | -0.048649 | -0.012199 | 0.048697 | 0.012229 | 4.7041e-05 | 2.9803e-05 | 0.073068 | 0.073068 | 0.073068 | 0.99077 | -0.17748 | 0.99182 | -0.15722 | 20.0735
5 | -0.055968 | -0.014051 | 0.055972 | 0.014054 | 3.9835e-06 | 2.53e-06 | 0.083977 | 0.083977 | 0.083977 | 0.99182 | -0.15722 | 0.99189 | -0.15572 | 23.0706
6 | -0.02203 | -0.0055212 | 0.022039 | 0.0055266 | 8.8463e-06 | 5.3821e-06 | 0.033029 | 0.033029 | 0.033029 | 0.99248 | -0.14476 | 0.99291 | -0.13633 | 9.074
7 | -0.058986 | -0.014786 | 0.059034 | 0.014817 | 4.8437e-05 | 3.0786e-05 | 0.0884 | 0.0884 | 0.0884 | 0.99291 | -0.13633 | 0.9938 | -0.11911 | 24.2857
8 | -0.073978 | -0.018562 | 0.074005 | 0.018579 | 2.6593e-05 | 1.6944e-05 | 0.11077 | 0.11077 | 0.11077 | 0.9938 | -0.11911 | 0.99419 | -0.11158 | 30.4326
9 | -0.087391 | -0.021934 | 0.087495 | 0.022001 | 0.00010476 | 6.6834e-05 | 0.13081 | 0.13081 | 0.13081 | 0.99419 | -0.11158 | 0.99549 | -0.086475 | 35.9367
10 | -0.10541 | -0.026492 | 0.1057 | 0.026675 | 0.00028718 | 0.00018339 | 0.15759 | 0.15759 | 0.15759 | 0.99549 | -0.086475 | 0.99845 | -0.029578 | 43.2936
11 | 0.017915 | 0.004491 | -0.017912 | -0.0044891 | 3.1883e-06 | 1.8864e-06 | 0.026779 | 0.026779 | 0.026779 | 0.99549 | -0.086475 | 0.9953 | -0.090211 | 7.3569
12 | -0.11702 | -0.029514 | 0.11719 | 0.02962 | 0.00016595 | 0.00010602 | 0.17447 | 0.17447 | 0.17447 | 0.99845 | -0.029578 | 1 | 0 | 47.9309
13 | 0.14439 | 0.036518 | -0.14436 | -0.036498 | 3.2068e-05 | 2.0426e-05 | 0.21497 | 0.21497 | 0.21497 | 1 | 0 | 0.99976 | -0.0046307 | 29.5288
14 | 0.13072 | 0.03308 | -0.13062 | -0.033017 | 9.7389e-05 | 6.2239e-05 | 0.19467 | 0.19467 | 0.19467 | 0.99976 | -0.0046307 | 0.99894 | -0.020166 | 53.4809
15 | 0.11568 | 0.029274 | -0.11557 | -0.029204 | 0.00010948 | 6.9942e-05 | 0.17242 | 0.17242 | 0.17242 | 0.99894 | -0.020166 | 0.99791 | -0.039907 | 47.3681
16 | 0.10463 | 0.02646 | -0.10438 | -0.026305 | 0.00024272 | 0.000155 | 0.1561 | 0.1561 | 0.1561 | 0.99791 | -0.039907 | 0.99538 | -0.08839 | 42.8833
17 | 0.10438 | 0.026305 | -0.10425 | -0.026222 | 0.00013004 | 8.3042e-05 | 0.1561 | 0.1561 | 0.1561 | 0.99538 | -0.08839 | 0.99403 | -0.11447 | 42.8833
18 | 0.089 | 0.022399 | -0.088825 | -0.022287 | 0.00017511 | 0.00011173 | 0.13326 | 0.13326 | 0.13326 | 0.99403 | -0.11447 | 0.99189 | -0.15572 | 36.6105

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27457 | 0.068981

## res_load
| p_mw | q_mvar
0 | 0.0036568 | 0.00091649
1 | 0.0058153 | 0.0014574
2 | 0.023754 | 0.0059534
3 | 0.015406 | 0.0038612
4 | 0.0072714 | 0.0018224
5 | 0.02203 | 0.0055212
6 | 0.036947 | 0.0092599
7 | 0.014944 | 0.0037452
8 | 0.013386 | 0.0033548
9 | 0.011327 | 0.0028387
10 | 0.017912 | 0.0044891
11 | 0.011341 | 0.0028423
12 | 0.013639 | 0.0034181
13 | 0.014938 | 0.0037437
14 | 0.010948 | 0.0027438
15 | 0.015253 | 0.0038228
16 | 0.032853 | 0.0082338

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1