## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-82_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-82_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-82_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-82_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-82_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-82_0_5_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_261-82_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_261-82_0_5_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-82_0_5_node_39 | 0.4 | n |  | TRUE
9 | bus_LV_261-82_0_5_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_261-82_0_5_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_261-82_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_261-82_0_5_node_41 | 0.4 | n |  | TRUE
13 | bus_LV_261-82_0_5_node_25 | 0.4 | n |  | TRUE
14 | bus_LV_261-82_0_5_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_261-82_0_5_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_261-82_0_5_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_261-82_0_5_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_261-82_0_5_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_261-82_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_261-82_0_5_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_261-82_0_5_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_261-82_0_5_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_261-82_0_5_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_261-82_0_5_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_261-82_0_5_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_261-82_0_5_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_261-82_0_5_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_261-82_0_5_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_261-82_0_5_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_261-82_0_5_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_261-82_0_5_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_261-82_0_5_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_261-82_0_5_node_14 | 0.4 | n |  | TRUE
34 | bus_LV_261-82_0_5_node_12 | 0.4 | n |  | TRUE
35 | bus_LV_261-82_0_5_node_8 | 0.4 | n |  | TRUE
36 | bus_LV_261-82_0_5_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_261-82_0_5_node_18 | 0.4 | n |  | TRUE
38 | bus_MV_526_0_node_95 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-82_0_5_load_0 | 0 | 0.088194 | 0.022103 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-82_0_5_load_3 | 3 | 0.077114 | 0.019327 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-82_0_5_load_36 | 5 | 0.012611 | 0.0031605 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-82_0_5_load_39 | 8 | 0.021062 | 0.0052787 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-82_0_5_load_9 | 11 | 0.018202 | 0.0045618 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-82_0_5_load_41 | 12 | 0.027632 | 0.0069253 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-82_0_5_load_37 | 14 | 0.0063872 | 0.0016008 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-82_0_5_load_34 | 15 | 0.026143 | 0.0065521 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-82_0_5_load_38 | 18 | 0.0008365 | 0.00020965 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-82_0_5_load_40 | 21 | 0.025437 | 0.006375 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-82_0_5_load_20 | 27 | 0.007303 | 0.0018303 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-82_0_5_load_21 | 29 | 0.011196 | 0.0028061 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-82_0_5_load_33 | 31 | 0.007469 | 0.0018719 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-82_0_5_load_35 | 32 | 0.063724 | 0.015971 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-82_0_5_load_12 | 34 | 0.025428 | 0.0063729 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-82_0_5_load_8 | 35 | 0.041721 | 0.010456 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-82_0_5_load_19 | 36 | 0.07475 | 0.018734 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-82_0_5_load_18 | 37 | 0.024867 | 0.0062323 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 33 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-82_0_5_line_0 |  | 0 | 1 | 0.044867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-82_0_5_line_1 |  | 0 | 2 | 0.042985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_261-82_0_5_line_2 |  | 1 | 3 | 0.066582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-82_0_5_line_3 |  | 2 | 4 | 0.065859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_261-82_0_5_line_4 |  | 4 | 5 | 0.012085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_261-82_0_5_line_5 |  | 5 | 6 | 0.012135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_261-82_0_5_line_6 |  | 6 | 7 | 0.089676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_261-82_0_5_line_7 |  | 7 | 8 | 0.028407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_261-82_0_5_line_8 |  | 8 | 21 | 0.02329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_261-82_0_5_line_9 |  | 9 | 10 | 0.010417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_261-82_0_5_line_10 |  | 9 | 11 | 0.027104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_261-82_0_5_line_11 |  | 10 | 12 | 0.013219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_261-82_0_5_line_12 |  | 11 | 35 | 0.029463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_261-82_0_5_line_13 |  | 12 | 24 | 0.0089058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-82_0_5_line_14 |  | 13 | 14 | 0.042895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-82_0_5_line_15 |  | 13 | 15 | 0.02159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-82_0_5_line_16 |  | 15 | 30 | 0.038332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-82_0_5_line_17 |  | 16 | 17 | 0.057594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-82_0_5_line_18 |  | 16 | 18 | 0.010237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-82_0_5_line_19 |  | 17 | 32 | 0.0099168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-82_0_5_line_20 |  | 18 | 23 | 0.0044739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-82_0_5_line_21 |  | 19 | 20 | 0.08504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-82_0_5_line_22 |  | 19 | 21 | 0.026965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_261-82_0_5_line_23 |  | 19 | 22 | 0.025533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_261-82_0_5_line_24 |  | 20 | 31 | 0.027495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-82_0_5_line_25 |  | 20 | 23 | 0.013679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-82_0_5_line_26 |  | 22 | 34 | 0.019233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_261-82_0_5_line_27 |  | 22 | 35 | 0.019514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_261-82_0_5_line_28 |  | 24 | 25 | 0.043768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-82_0_5_line_29 |  | 25 | 36 | 0.033088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-82_0_5_line_30 |  | 25 | 26 | 0.023527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-82_0_5_line_31 |  | 26 | 27 | 0.039269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-82_0_5_line_32 |  | 26 | 28 | 0.037284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-82_0_5_line_33 |  | 27 | 37 | 0.00029231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-82_0_5_line_34 |  | 28 | 29 | 0.070447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-82_0_5_line_35 |  | 30 | 31 | 0.024924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-82_0_5_line_36 |  | 33 | 34 | 0.021787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-82_0_5_trafo_14 | 0.63 MVA 20/0.4 kV | 38 | 33 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2681578.8642 | 1249300.7137 | 2681538.1375 | 1249319.5397
1 | 2681499.1302 | 1249337.5998 | 2681501.3116 | 1249336.5624 | 2681503.8346 | 1249335.3962 | 2681538.1375 | 1249319.5397
2 | 2681578.8642 | 1249300.7137 | 2681639.3015 | 1249272.7764
3 | 2681472.0397 | 1249277.5388 | 2681499.1302 | 1249337.5998
4 | 2681472.0397 | 1249277.5388 | 2681467.4158 | 1249266.3736
5 | 2681462.7725 | 1249255.1616 | 2681467.4158 | 1249266.3736
6 | 2681424.9816 | 1249180.7766 | 2681443.7194 | 1249212.4128 | 2681461.5035 | 1249238.7098 | 2681464.6325 | 1249245.6468 | 2681459.3863 | 1249248.2544 | 2681462.7725 | 1249255.1616
7 | 2681424.9816 | 1249180.7766 | 2681448.0801 | 1249164.2412
8 | 2681448.0801 | 1249164.2412 | 2681467.0178 | 1249150.6845
9 | 2681572.2146 | 1249076.7348 | 2681575.5488 | 1249075.8912 | 2681579.0172 | 1249076.2725 | 2681582.254 | 1249077.5736
10 | 2681572.2146 | 1249076.7348 | 2681566.8505 | 1249079.6632 | 2681549.7344 | 1249091.8176
11 | 2681582.254 | 1249077.5736 | 2681584.5045 | 1249079.2057 | 2681586.3487 | 1249081.2771 | 2681590.5676 | 1249087.6772
12 | 2681525.7118 | 1249108.8765 | 2681549.7344 | 1249091.8176
13 | 2681595.4691 | 1249095.1128 | 2681590.5676 | 1249087.6772
14 | 2681390.4308 | 1249061.7589 | 2681403.3407 | 1249052.0846 | 2681425.5614 | 1249037.1689
15 | 2681390.4308 | 1249061.7589 | 2681393.8169 | 1249068.1323 | 2681405.9029 | 1249060.3538
16 | 2681438.1357 | 1249039.6088 | 2681405.9029 | 1249060.3538
17 | 2681492.4751 | 1249064.9407 | 2681489.9843 | 1249069.243 | 2681486.6216 | 1249071.6096 | 2681483.8767 | 1249074.0737 | 2681483.5675 | 1249075.6929 | 2681484.4999 | 1249077.0845 | 2681486.9385 | 1249078.2189 | 2681488.2275 | 1249078.3811 | 2681490.9266 | 1249077.0506 | 2681496.3865 | 1249073.1894 | 2681505.3677 | 1249066.419 | 2681511.2882 | 1249062.5642 | 2681513.5224 | 1249062.0946 | 2681515.6528 | 1249062.0238 | 2681517.9734 | 1249062.9564 | 2681519.8958 | 1249064.8398
18 | 2681492.4751 | 1249064.9407 | 2681484.1069 | 1249070.8379
19 | 2681519.8958 | 1249064.8398 | 2681511.7685 | 1249070.5222
20 | 2681480.4499 | 1249073.415 | 2681484.1069 | 1249070.8379
21 | 2681469.478 | 1249081.6259 | 2681467.1368 | 1249086.0414 | 2681466.7245 | 1249089.1158 | 2681466.9555 | 1249090.987 | 2681467.6325 | 1249093.3758 | 2681469.216 | 1249096.8335 | 2681470.55 | 1249099.2202 | 2681474.5328 | 1249106.1245 | 2681476.5241 | 1249109.5877 | 2681478.6459 | 1249113.4419 | 2681477.039 | 1249120.4695 | 2681473.873 | 1249126.6528 | 2681464.6933 | 1249133.0424 | 2681476.0001 | 1249133.9652 | 2681480.1328 | 1249134.3556 | 2681488.9441 | 1249134.9882
22 | 2681488.9441 | 1249134.9882 | 2681467.0178 | 1249150.6845
23 | 2681509.8009 | 1249120.1751 | 2681488.9441 | 1249134.9882
24 | 2681469.478 | 1249081.6259 | 2681453.0382 | 1249059.5869
25 | 2681469.478 | 1249081.6259 | 2681480.4499 | 1249073.415
26 | 2681509.8009 | 1249120.1751 | 2681520.4573 | 1249136.1864
27 | 2681509.8009 | 1249120.1751 | 2681525.7118 | 1249108.8765
28 | 2681595.4691 | 1249095.1128 | 2681601.7566 | 1249105.1845 | 2681603.4103 | 1249107.9315 | 2681613.3911 | 1249124.5367 | 2681605.6994 | 1249129.7903
29 | 2681605.6994 | 1249129.7903 | 2681578.2479 | 1249148.262
30 | 2681605.6994 | 1249129.7903 | 2681613.3911 | 1249124.5367 | 2681621.1713 | 1249136.4303
31 | 2681621.1713 | 1249136.4303 | 2681588.7404 | 1249158.5735
32 | 2681621.1713 | 1249136.4303 | 2681623.7632 | 1249140.1354 | 2681619.6416 | 1249142.7695 | 2681634.6244 | 1249166.2709
33 | 2681588.7404 | 1249158.5735 | 2681588.499 | 1249158.7383
34 | 2681634.6244 | 1249166.2709 | 2681590.8735 | 1249186.4502 | 2681570.7145 | 1249195.9068
35 | 2681438.1357 | 1249039.6088 | 2681453.0382 | 1249059.5869
36 | 2681532.5288 | 1249154.3239 | 2681520.4573 | 1249136.1864

## bus_geodata
| x | y | coords
0 | 2681538.1375 | 1249319.5397
1 | 2681578.8642 | 1249300.7137
2 | 2681499.1302 | 1249337.5998
3 | 2681639.3015 | 1249272.7764
4 | 2681472.0397 | 1249277.5388
5 | 2681467.4158 | 1249266.3736
6 | 2681462.7725 | 1249255.1616
7 | 2681424.9816 | 1249180.7766
8 | 2681448.0801 | 1249164.2412
9 | 2681572.2146 | 1249076.7348
10 | 2681582.254 | 1249077.5736
11 | 2681549.7344 | 1249091.8176
12 | 2681590.5676 | 1249087.6772
13 | 2681390.4308 | 1249061.7589
14 | 2681425.5614 | 1249037.1689
15 | 2681405.9029 | 1249060.3538
16 | 2681492.4751 | 1249064.9407
17 | 2681519.8958 | 1249064.8398
18 | 2681484.1069 | 1249070.8379
19 | 2681488.9441 | 1249134.9882
20 | 2681469.478 | 1249081.6259
21 | 2681467.0178 | 1249150.6845
22 | 2681509.8009 | 1249120.1751
23 | 2681480.4499 | 1249073.415
24 | 2681595.4691 | 1249095.1128
25 | 2681605.6994 | 1249129.7903
26 | 2681621.1713 | 1249136.4303
27 | 2681588.7404 | 1249158.5735
28 | 2681634.6244 | 1249166.2709
29 | 2681570.7145 | 1249195.9068
30 | 2681438.1357 | 1249039.6088
31 | 2681453.0382 | 1249059.5869
32 | 2681511.7685 | 1249070.5222
33 | 2681532.5288 | 1249154.3239
34 | 2681520.4573 | 1249136.1864
35 | 2681525.7118 | 1249108.8765
36 | 2681578.2479 | 1249148.262
37 | 2681588.499 | 1249158.7383
38 | 2681510.7739 | 1249168.5575

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98235 | -0.33853 | 0.088194 | 0.022103
1 | 0.97912 | -0.40123 | 0 | 0
2 | 0.98564 | -0.27457 | 0 | 0
3 | 0.97435 | -0.49503 | 0.077114 | 0.019327
4 | 0.98766 | -0.23558 | 0 | 0
5 | 0.98803 | -0.22845 | 0.012611 | 0.0031605
6 | 0.98843 | -0.22074 | 0 | 0
7 | 0.99139 | -0.16397 | 0 | 0
8 | 0.99232 | -0.14606 | 0.021062 | 0.0052787
9 | 0.9935 | -0.1238 | 0 | 0
10 | 0.99322 | -0.12917 | 0 | 0
11 | 0.99423 | -0.10986 | 0.018202 | 0.0045618
12 | 0.99234 | -0.14621 | 0.027632 | 0.0069253
13 | 0.98304 | -0.32564 | 0 | 0
14 | 0.98279 | -0.33058 | 0.0063872 | 0.0016008
15 | 0.98317 | -0.32315 | 0.026143 | 0.0065521
16 | 0.98439 | -0.29914 | 0 | 0
17 | 0.981 | -0.36538 | 0 | 0
18 | 0.985 | -0.28741 | 0.0008365 | 0.00020965
19 | 0.9943 | -0.1083 | 0 | 0
20 | 0.98608 | -0.26638 | 0 | 0
21 | 0.99318 | -0.12966 | 0.025437 | 0.006375
22 | 0.99585 | -0.078722 | 0 | 0
23 | 0.98526 | -0.28222 | 0 | 0
24 | 0.99137 | -0.16484 | 0 | 0
25 | 0.9866 | -0.25697 | 0 | 0
26 | 0.98566 | -0.27526 | 0 | 0
27 | 0.9845 | -0.29795 | 0.007303 | 0.0018303
28 | 0.98528 | -0.28276 | 0 | 0
29 | 0.98455 | -0.29693 | 0.011196 | 0.0028061
30 | 0.98432 | -0.30069 | 0 | 0
31 | 0.98507 | -0.28612 | 0.007469 | 0.0018719
32 | 0.98041 | -0.37683 | 0.063724 | 0.015971
33 | 1 | 0 | -0.56952 | -0.14532
34 | 0.99775 | -0.04264 | 0.025428 | 0.0063729
35 | 0.99512 | -0.092841 | 0.041721 | 0.010456
36 | 0.98432 | -0.30136 | 0.07475 | 0.018734
37 | 0.98449 | -0.29808 | 0.024867 | 0.0062323
38 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.077694 | 0.019696 | -0.07746 | -0.019547 | 0.00023335 | 0.00014878 | 0.11777 | 0.11777 | 0.11777 | 0.98235 | -0.33853 | 0.97912 | -0.40123 | 32.3538
1 | -0.16589 | -0.0418 | 0.1664 | 0.042124 | 0.00050923 | 0.00032481 | 0.25136 | 0.25136 | 0.25136 | 0.98235 | -0.33853 | 0.98564 | -0.27457 | 34.5274
2 | 0.07746 | 0.019547 | -0.077114 | -0.019327 | 0.00034629 | 0.00022079 | 0.11777 | 0.11777 | 0.11777 | 0.97912 | -0.40123 | 0.97435 | -0.49503 | 32.3539
3 | -0.1664 | -0.042124 | 0.16671 | 0.04232 | 0.00031208 | 0.00019552 | 0.25136 | 0.25136 | 0.25136 | 0.98564 | -0.27457 | 0.98766 | -0.23558 | 13.8109
4 | -0.16671 | -0.04232 | 0.16677 | 0.042356 | 5.7264e-05 | 3.5875e-05 | 0.25136 | 0.25136 | 0.25136 | 0.98766 | -0.23558 | 0.98803 | -0.22845 | 13.8109
5 | -0.17938 | -0.045516 | 0.17944 | 0.045558 | 6.6522e-05 | 4.1797e-05 | 0.27035 | 0.27035 | 0.27035 | 0.98803 | -0.22845 | 0.98843 | -0.22074 | 14.8544
6 | -0.17944 | -0.045558 | 0.17993 | 0.045867 | 0.00049157 | 0.00030884 | 0.27035 | 0.27035 | 0.27035 | 0.98843 | -0.22074 | 0.99139 | -0.16397 | 14.8543
7 | -0.17993 | -0.045867 | 0.18009 | 0.045965 | 0.00015571 | 9.7824e-05 | 0.27035 | 0.27035 | 0.27035 | 0.99139 | -0.16397 | 0.99232 | -0.14606 | 14.8542
8 | -0.20115 | -0.051243 | 0.20131 | 0.051344 | 0.00015924 | 0.0001004 | 0.30193 | 0.30193 | 0.30193 | 0.99232 | -0.14606 | 0.99318 | -0.12966 | 16.5895
9 | 0.14678 | 0.037183 | -0.14674 | -0.03716 | 3.7807e-05 | 2.3522e-05 | 0.21998 | 0.21998 | 0.21998 | 0.9935 | -0.1238 | 0.99322 | -0.12917 | 12.0868
10 | -0.14678 | -0.037183 | 0.14688 | 0.037244 | 9.8368e-05 | 6.12e-05 | 0.21998 | 0.21998 | 0.21998 | 0.9935 | -0.1238 | 0.99423 | -0.10986 | 12.0867
11 | 0.14674 | 0.03716 | -0.14662 | -0.037083 | 0.00011994 | 7.6419e-05 | 0.21998 | 0.21998 | 0.21998 | 0.99322 | -0.12917 | 0.99234 | -0.14621 | 30.2169
12 | -0.16508 | -0.041806 | 0.16521 | 0.041891 | 0.00013506 | 8.4523e-05 | 0.24722 | 0.24722 | 0.24722 | 0.99423 | -0.10986 | 0.99512 | -0.092841 | 13.5835
13 | 0.11899 | 0.030158 | -0.11888 | -0.03009 | 0.00010646 | 6.8021e-05 | 0.17854 | 0.17854 | 0.17854 | 0.99234 | -0.14621 | 0.99137 | -0.16484 | 49.0506
14 | 0.0063887 | 0.0016012 | -0.0063872 | -0.0016008 | 1.5043e-06 | 4.1908e-07 | 0.0096704 | 0.0096706 | 0.0096706 | 0.98304 | -0.32564 | 0.98279 | -0.33058 | 2.6568
15 | -0.0063887 | -0.0016012 | 0.0063894 | 0.0016014 | 7.5713e-07 | 2.1081e-07 | 0.0096704 | 0.0096703 | 0.0096704 | 0.98304 | -0.32564 | 0.98317 | -0.32315 | 2.6567
16 | -0.032533 | -0.0081535 | 0.032568 | 0.0081754 | 3.4849e-05 | 2.1817e-05 | 0.049238 | 0.049238 | 0.049238 | 0.98317 | -0.32315 | 0.98432 | -0.30069 | 13.5269
17 | 0.06396 | 0.016121 | -0.063758 | -0.015993 | 0.00020202 | 0.00012857 | 0.096716 | 0.096716 | 0.096716 | 0.98439 | -0.29914 | 0.981 | -0.36538 | 26.5703
18 | -0.06396 | -0.016121 | 0.063996 | 0.016144 | 3.5909e-05 | 2.2852e-05 | 0.096716 | 0.096716 | 0.096716 | 0.98439 | -0.29914 | 0.985 | -0.28741 | 26.5702
19 | 0.063758 | 0.015993 | -0.063724 | -0.015971 | 3.4785e-05 | 2.2138e-05 | 0.096716 | 0.096716 | 0.096716 | 0.981 | -0.36538 | 0.98041 | -0.37683 | 26.5703
20 | -0.064833 | -0.016354 | 0.064849 | 0.016364 | 1.6106e-05 | 1.0251e-05 | 0.097979 | 0.097979 | 0.097979 | 0.985 | -0.28741 | 0.98526 | -0.28222 | 26.9174
21 | 0.1058 | 0.026992 | -0.105 | -0.026481 | 0.00080114 | 0.00051164 | 0.1585 | 0.1585 | 0.1585 | 0.9943 | -0.1083 | 0.98608 | -0.26638 | 43.5437
22 | 0.22698 | 0.057867 | -0.22675 | -0.057719 | 0.00023384 | 0.00014791 | 0.34004 | 0.34004 | 0.34004 | 0.9943 | -0.1083 | 0.99318 | -0.12966 | 18.6834
23 | -0.33278 | -0.084859 | 0.33325 | 0.085162 | 0.00047594 | 0.00030295 | 0.49854 | 0.49854 | 0.49854 | 0.9943 | -0.1083 | 0.99585 | -0.078722 | 27.3921
24 | 0.040097 | 0.010085 | -0.040059 | -0.010061 | 3.7765e-05 | 2.3819e-05 | 0.06052 | 0.06052 | 0.06052 | 0.98608 | -0.26638 | 0.98507 | -0.28612 | 16.6264
25 | 0.064898 | 0.016395 | -0.064849 | -0.016364 | 4.9244e-05 | 3.1342e-05 | 0.097979 | 0.097979 | 0.097979 | 0.98608 | -0.26638 | 0.98526 | -0.28222 | 26.9174
26 | -0.54033 | -0.1376 | 0.54127 | 0.1382 | 0.00094208 | 0.00060168 | 0.80814 | 0.80814 | 0.80814 | 0.99585 | -0.078722 | 0.99775 | -0.04264 | 44.4033
27 | 0.20708 | 0.052435 | -0.20694 | -0.052347 | 0.00014029 | 8.8518e-05 | 0.3096 | 0.30961 | 0.30961 | 0.99585 | -0.078722 | 0.99512 | -0.092841 | 17.0113
28 | 0.11888 | 0.03009 | -0.11836 | -0.029756 | 0.00052322 | 0.0003343 | 0.17854 | 0.17854 | 0.17854 | 0.99137 | -0.16484 | 0.9866 | -0.25697 | 49.0507
29 | 0.074908 | 0.018835 | -0.07475 | -0.018734 | 0.00015844 | 0.00010098 | 0.113 | 0.113 | 0.113 | 0.9866 | -0.25697 | 0.98432 | -0.30136 | 31.044
30 | 0.043451 | 0.010921 | -0.043413 | -0.010897 | 3.7903e-05 | 2.3958e-05 | 0.065544 | 0.065545 | 0.065545 | 0.9866 | -0.25697 | 0.98566 | -0.27526 | 18.0067
31 | 0.032205 | 0.0080844 | -0.03217 | -0.0080627 | 3.4816e-05 | 2.1782e-05 | 0.048623 | 0.048623 | 0.048623 | 0.98566 | -0.27526 | 0.9845 | -0.29795 | 13.3581
32 | 0.011208 | 0.0028121 | -0.011204 | -0.00281 | 4.0034e-06 | 2.0871e-06 | 0.016921 | 0.016921 | 0.016921 | 0.98566 | -0.27526 | 0.98528 | -0.28276 | 4.6488
33 | 0.024867 | 0.0062324 | -0.024867 | -0.0062323 | 1.5485e-07 | 9.5388e-08 | 0.037585 | 0.037585 | 0.037585 | 0.9845 | -0.29795 | 0.98449 | -0.29808 | 10.3257
34 | 0.011204 | 0.00281 | -0.011196 | -0.0028061 | 7.5645e-06 | 3.9447e-06 | 0.016921 | 0.016922 | 0.016922 | 0.98528 | -0.28276 | 0.98455 | -0.29693 | 4.6488
35 | -0.032568 | -0.0081754 | 0.03259 | 0.0081895 | 2.2659e-05 | 1.4185e-05 | 0.049238 | 0.049238 | 0.049238 | 0.98432 | -0.30069 | 0.98507 | -0.28612 | 13.5269
36 | 0.56787 | 0.14532 | -0.5667 | -0.14457 | 0.0011697 | 0.00074718 | 0.84606 | 0.84606 | 0.84606 | 1 | 0 | 0.99775 | -0.04264 | 46.4869

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56952 | 0.14532

## res_load
| p_mw | q_mvar
0 | 0.088194 | 0.022103
1 | 0.077114 | 0.019327
2 | 0.012611 | 0.0031605
3 | 0.021062 | 0.0052787
4 | 0.018202 | 0.0045618
5 | 0.027632 | 0.0069253
6 | 0.0063872 | 0.0016008
7 | 0.026143 | 0.0065521
8 | 0.0008365 | 0.00020965
9 | 0.025437 | 0.006375
10 | 0.007303 | 0.0018303
11 | 0.011196 | 0.0028061
12 | 0.007469 | 0.0018719
13 | 0.063724 | 0.015971
14 | 0.025428 | 0.0063729
15 | 0.041721 | 0.010456
16 | 0.07475 | 0.018734
17 | 0.024867 | 0.0062323

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1