## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-832_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-832_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_261-832_0_4_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_261-832_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-832_0_4_node_37 | 0.4 | n |  | TRUE
5 | bus_LV_261-832_0_4_node_40 | 0.4 | n |  | TRUE
6 | bus_LV_261-832_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_261-832_0_4_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_261-832_0_4_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_261-832_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_261-832_0_4_node_36 | 0.4 | n |  | TRUE
11 | bus_LV_261-832_0_4_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_261-832_0_4_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_261-832_0_4_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_261-832_0_4_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_261-832_0_4_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_261-832_0_4_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_261-832_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_261-832_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_261-832_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_261-832_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_261-832_0_4_node_39 | 0.4 | n |  | TRUE
22 | bus_LV_261-832_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_261-832_0_4_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_261-832_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_261-832_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_261-832_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_261-832_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_261-832_0_4_node_35 | 0.4 | n |  | TRUE
29 | bus_LV_261-832_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_261-832_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_261-832_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_261-832_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_261-832_0_4_node_41 | 0.4 | n |  | TRUE
34 | bus_LV_261-832_0_4_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_261-832_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_261-832_0_4_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_261-832_0_4_node_34 | 0.4 | n |  | TRUE
38 | bus_MV_538_0_node_77 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-832_0_4_load_0 | 0 | 0.0078893 | 0.0019772 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-832_0_4_load_8 | 2 | 0.0090964 | 0.0022798 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-832_0_4_load_40 | 5 | 0.0087188 | 0.0021851 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-832_0_4_load_16 | 7 | 0.0055718 | 0.0013964 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-832_0_4_load_24 | 8 | 0.011385 | 0.0028533 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-832_0_4_load_9 | 9 | 0.007632 | 0.0019128 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-832_0_4_load_36 | 10 | 0.022235 | 0.0055726 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-832_0_4_load_15 | 11 | 0.0067353 | 0.001688 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-832_0_4_load_25 | 12 | 0.02059 | 0.0051605 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-832_0_4_load_31 | 13 | 0.047331 | 0.011862 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-832_0_4_load_38 | 15 | 0.013515 | 0.0033873 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-832_0_4_load_12 | 19 | 0.012796 | 0.0032069 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-832_0_4_load_14 | 20 | 0.0069053 | 0.0017306 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-832_0_4_load_39 | 21 | 0.012637 | 0.003167 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-832_0_4_load_13 | 22 | 0.0063636 | 0.0015949 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-832_0_4_load_32 | 23 | 0.011471 | 0.0028749 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-832_0_4_load_17 | 24 | 0.048956 | 0.01227 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-832_0_4_load_18 | 25 | 0.043757 | 0.010966 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-832_0_4_load_20 | 27 | 0.0072233 | 0.0018103 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-832_0_4_load_35 | 28 | 0.019813 | 0.0049657 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-832_0_4_load_26 | 30 | 0.019681 | 0.0049325 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-832_0_4_load_41 | 33 | 0.025512 | 0.0063939 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-832_0_4_load_33 | 34 | 0.023729 | 0.0059471 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-832_0_4_load_28 | 35 | 0.016556 | 0.0041493 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-832_0_4_load_27 | 36 | 0.010739 | 0.0026914 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-832_0_4_load_34 | 37 | 0.035871 | 0.0089901 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-832_0_4_line_0 |  | 0 | 1 | 0.012504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-832_0_4_line_1 |  | 1 | 2 | 0.0052133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-832_0_4_line_2 |  | 2 | 9 | 9.9793e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-832_0_4_line_3 |  | 3 | 4 | 0.002688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-832_0_4_line_4 |  | 3 | 5 | 0.014008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-832_0_4_line_5 |  | 4 | 10 | 0.01469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-832_0_4_line_6 |  | 6 | 7 | 0.012066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_261-832_0_4_line_7 |  | 6 | 8 | 0.0076847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-832_0_4_line_8 |  | 7 | 11 | 0.0027076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_261-832_0_4_line_9 |  | 8 | 12 | 0.0052057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-832_0_4_line_10 |  | 9 | 17 | 0.0087574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-832_0_4_line_11 |  | 10 | 37 | 0.001823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-832_0_4_line_12 |  | 11 | 22 | 0.0036237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_261-832_0_4_line_13 |  | 12 | 30 | 0.0088975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-832_0_4_line_14 |  | 13 | 14 | 0.028769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-832_0_4_line_15 |  | 14 | 36 | 0.012137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-832_0_4_line_16 |  | 14 | 32 | 0.014746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-832_0_4_line_17 |  | 15 | 16 | 0.015981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-832_0_4_line_18 |  | 16 | 28 | 0.010469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-832_0_4_line_19 |  | 16 | 26 | 0.018772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-832_0_4_line_20 |  | 17 | 18 | 0.005516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-832_0_4_line_21 |  | 17 | 19 | 0.011483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-832_0_4_line_22 |  | 18 | 20 | 0.0077254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_261-832_0_4_line_23 |  | 18 | 21 | 0.013691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_261-832_0_4_line_24 |  | 20 | 22 | 7.0816e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_261-832_0_4_line_25 |  | 21 | 23 | 0.0010981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_261-832_0_4_line_26 |  | 23 | 27 | 0.007774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_261-832_0_4_line_27 |  | 24 | 25 | 0.0017403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_261-832_0_4_line_28 |  | 24 | 26 | 0.015442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-832_0_4_line_29 |  | 25 | 27 | 0.013924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_261-832_0_4_line_30 |  | 28 | 34 | 0.0075588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-832_0_4_line_31 |  | 29 | 30 | 0.0023014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-832_0_4_line_32 |  | 29 | 31 | 0.001077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-832_0_4_line_33 |  | 31 | 35 | 0.0071601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-832_0_4_line_34 |  | 32 | 33 | 0.0096641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-832_0_4_line_35 |  | 34 | 37 | 0.0056774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-832_0_4_line_36 |  | 35 | 36 | 0.008917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-832_0_4_trafo_20 | 0.63 MVA 20/0.4 kV | 38 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2683264.33 | 1247229.5372 | 2683266.5096 | 1247241.8502
1 | 2683264.33 | 1247229.5372 | 2683269.2251 | 1247227.7439
2 | 2683269.3188 | 1247227.7095 | 2683269.2251 | 1247227.7439
3 | 2683287.963 | 1247253.3977 | 2683289.3051 | 1247255.7294
4 | 2683289.3051 | 1247255.7294 | 2683294.6205 | 1247268.6896
5 | 2683287.963 | 1247253.3977 | 2683302.5167 | 1247251.4008
6 | 2683276.9499 | 1247193.1654 | 2683276.9812 | 1247202.7618 | 2683276.8679 | 1247205.2284
7 | 2683276.9499 | 1247193.1654 | 2683281.3973 | 1247193.2947 | 2683284.6315 | 1247193.3841
8 | 2683276.7436 | 1247207.9332 | 2683276.8679 | 1247205.2284
9 | 2683289.8352 | 1247193.5279 | 2683284.6315 | 1247193.3841
10 | 2683277.5417 | 1247224.697 | 2683269.3188 | 1247227.7095
11 | 2683304.3227 | 1247251.153 | 2683302.5167 | 1247251.4008
12 | 2683276.5773 | 1247211.5531 | 2683276.7436 | 1247207.9332
13 | 2683289.8352 | 1247193.5279 | 2683298.7293 | 1247193.7738
14 | 2683330.2245 | 1247196.0714 | 2683329.3672 | 1247167.3154
15 | 2683330.2245 | 1247196.0714 | 2683318.1439 | 1247194.9073
16 | 2683330.2245 | 1247196.0714 | 2683329.8057 | 1247210.8097
17 | 2683327.8779 | 1247248.5326 | 2683327.1957 | 1247264.4993
18 | 2683327.8779 | 1247248.5326 | 2683317.4543 | 1247249.5111
19 | 2683328.8515 | 1247229.7881 | 2683327.8779 | 1247248.5326
20 | 2683276.2195 | 1247219.3411 | 2683277.5417 | 1247224.697
21 | 2683277.5417 | 1247224.697 | 2683280.1946 | 1247235.8693
22 | 2683276.2195 | 1247219.3411 | 2683276.5741 | 1247211.6238
23 | 2683276.2195 | 1247219.3411 | 2683289.6931 | 1247221.7733
24 | 2683276.5741 | 1247211.6238 | 2683276.5773 | 1247211.5531
25 | 2683290.7737 | 1247221.9684 | 2683289.6931 | 1247221.7733
26 | 2683290.7737 | 1247221.9684 | 2683298.4241 | 1247223.3494
27 | 2683312.0833 | 1247226.037 | 2683313.7816 | 1247226.4169
28 | 2683328.8515 | 1247229.7881 | 2683313.7816 | 1247226.4169
29 | 2683312.0833 | 1247226.037 | 2683306.9462 | 1247224.8878 | 2683298.4241 | 1247223.3494
30 | 2683309.9474 | 1247250.3812 | 2683313.7638 | 1247249.8575 | 2683317.4543 | 1247249.5111
31 | 2683301.0298 | 1247193.8374 | 2683298.7293 | 1247193.7738
32 | 2683301.0298 | 1247193.8374 | 2683302.1097 | 1247193.8637
33 | 2683302.1097 | 1247193.8637 | 2683309.2668 | 1247194.0712
34 | 2683329.8057 | 1247210.8097 | 2683320.2838 | 1247209.1586
35 | 2683309.9474 | 1247250.3812 | 2683304.3227 | 1247251.153
36 | 2683309.2668 | 1247194.0712 | 2683309.5548 | 1247194.0796 | 2683318.1439 | 1247194.9073

## bus_geodata
| x | y | coords
0 | 2683266.5096 | 1247241.8502
1 | 2683264.33 | 1247229.5372
2 | 2683269.2251 | 1247227.7439
3 | 2683289.3051 | 1247255.7294
4 | 2683287.963 | 1247253.3977
5 | 2683294.6205 | 1247268.6896
6 | 2683276.9499 | 1247193.1654
7 | 2683276.8679 | 1247205.2284
8 | 2683284.6315 | 1247193.3841
9 | 2683269.3188 | 1247227.7095
10 | 2683302.5167 | 1247251.4008
11 | 2683276.7436 | 1247207.9332
12 | 2683289.8352 | 1247193.5279
13 | 2683329.3672 | 1247167.3154
14 | 2683330.2245 | 1247196.0714
15 | 2683327.1957 | 1247264.4993
16 | 2683327.8779 | 1247248.5326
17 | 2683277.5417 | 1247224.697
18 | 2683276.2195 | 1247219.3411
19 | 2683280.1946 | 1247235.8693
20 | 2683276.5741 | 1247211.6238
21 | 2683289.6931 | 1247221.7733
22 | 2683276.5773 | 1247211.5531
23 | 2683290.7737 | 1247221.9684
24 | 2683313.7816 | 1247226.4169
25 | 2683312.0833 | 1247226.037
26 | 2683328.8515 | 1247229.7881
27 | 2683298.4241 | 1247223.3494
28 | 2683317.4543 | 1247249.5111
29 | 2683301.0298 | 1247193.8374
30 | 2683298.7293 | 1247193.7738
31 | 2683302.1097 | 1247193.8637
32 | 2683329.8057 | 1247210.8097
33 | 2683320.2838 | 1247209.1586
34 | 2683309.9474 | 1247250.3812
35 | 2683309.2668 | 1247194.0712
36 | 2683318.1439 | 1247194.9073
37 | 2683304.3227 | 1247251.153
38 | 2683276.2195 | 1247219.3411

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99718 | -0.053962 | 0.0078893 | 0.0019772
1 | 0.99727 | -0.052233 | 0 | 0
2 | 0.99731 | -0.051512 | 0.0090964 | 0.0022798
3 | 0.9924 | -0.1462 | 0 | 0
4 | 0.99242 | -0.14578 | 0 | 0
5 | 0.99229 | -0.14836 | 0.0087188 | 0.0021851
6 | 0.99576 | -0.081238 | 0 | 0
7 | 0.9966 | -0.065154 | 0.0055718 | 0.0013964
8 | 0.99523 | -0.091496 | 0.011385 | 0.0028533
9 | 0.99731 | -0.051483 | 0.007632 | 0.0019128
10 | 0.99254 | -0.14352 | 0.022235 | 0.0055726
11 | 0.99679 | -0.061416 | 0.0067353 | 0.001688
12 | 0.99456 | -0.10437 | 0.02059 | 0.0051605
13 | 0.98988 | -0.19488 | 0.047331 | 0.011862
14 | 0.99113 | -0.17069 | 0 | 0
15 | 0.99442 | -0.10714 | 0.013515 | 0.0033873
16 | 0.99462 | -0.10334 | 0 | 0
17 | 0.99751 | -0.047705 | 0 | 0
18 | 0.9977 | -0.044091 | 0 | 0
19 | 0.99738 | -0.05028 | 0.012796 | 0.0032069
20 | 0.99707 | -0.056096 | 0.0069053 | 0.0017306
21 | 0.99904 | -0.018379 | 0.012637 | 0.003167
22 | 0.99706 | -0.056201 | 0.0063636 | 0.0015949
23 | 0.99915 | -0.016199 | 0.011471 | 0.0028749
24 | 0.99849 | -0.028948 | 0.048956 | 0.01227
25 | 0.99863 | -0.026319 | 0.043757 | 0.010966
26 | 0.99674 | -0.062451 | 0 | 0
27 | 1 | 0 | -0.45937 | -0.11558
28 | 0.99356 | -0.12372 | 0.019813 | 0.0049657
29 | 0.99337 | -0.12724 | 0 | 0
30 | 0.99358 | -0.12317 | 0.019681 | 0.0049325
31 | 0.99327 | -0.12915 | 0 | 0
32 | 0.99078 | -0.17737 | 0 | 0
33 | 0.99056 | -0.18174 | 0.025512 | 0.0063939
34 | 0.99294 | -0.13581 | 0.023729 | 0.0059471
35 | 0.99262 | -0.14182 | 0.016556 | 0.0041493
36 | 0.99194 | -0.15502 | 0.010739 | 0.0026914
37 | 0.99259 | -0.14252 | 0.035871 | 0.0089901
38 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0078893 | -0.0019772 | 0.00789 | 0.0019775 | 6.4988e-07 | 2.5278e-07 | 0.011773 | 0.011773 | 0.011773 | 0.99718 | -0.053962 | 0.99727 | -0.052233 | 3.2342
1 | -0.00789 | -0.0019775 | 0.0078902 | 0.0019776 | 2.7094e-07 | 1.0538e-07 | 0.011773 | 0.011772 | 0.011773 | 0.99727 | -0.052233 | 0.99731 | -0.051512 | 3.2342
2 | -0.016987 | -0.0042574 | 0.016987 | 0.0042574 | 2.4037e-08 | 1.4082e-08 | 0.025345 | 0.025345 | 0.025345 | 0.99731 | -0.051512 | 0.99731 | -0.051483 | 6.9628
3 | -0.0087197 | -0.0021855 | 0.0087199 | 0.0021856 | 1.7231e-07 | 7.5546e-08 | 0.013074 | 0.013074 | 0.013074 | 0.9924 | -0.1462 | 0.99242 | -0.14578 | 3.5919
4 | 0.0087197 | 0.0021855 | -0.0087188 | -0.0021851 | 8.9795e-07 | 3.9372e-07 | 0.013074 | 0.013075 | 0.013075 | 0.9924 | -0.1462 | 0.99229 | -0.14836 | 3.5919
5 | -0.0087199 | -0.0021856 | 0.0087208 | 0.002186 | 9.4167e-07 | 4.1283e-07 | 0.013074 | 0.013074 | 0.013074 | 0.99242 | -0.14578 | 0.99254 | -0.14352 | 3.5919
6 | -0.15233 | -0.038384 | 0.15245 | 0.038458 | 0.0001173 | 7.4758e-05 | 0.22771 | 0.22771 | 0.22771 | 0.99576 | -0.081238 | 0.9966 | -0.065154 | 31.2782
7 | 0.15233 | 0.038384 | -0.15225 | -0.038336 | 7.4709e-05 | 4.7614e-05 | 0.22771 | 0.22771 | 0.22771 | 0.99576 | -0.081238 | 0.99523 | -0.091496 | 31.2782
8 | -0.15802 | -0.039855 | 0.15805 | 0.039873 | 2.8282e-05 | 1.803e-05 | 0.23602 | 0.23602 | 0.23602 | 0.9966 | -0.065154 | 0.99679 | -0.061416 | 32.4209
9 | 0.14087 | 0.035483 | -0.14078 | -0.035427 | 8.6651e-05 | 5.5389e-05 | 0.21068 | 0.21068 | 0.21068 | 0.99523 | -0.091496 | 0.99456 | -0.10437 | 57.88
10 | -0.024619 | -0.0061702 | 0.024623 | 0.0061729 | 4.4309e-06 | 2.7215e-06 | 0.036732 | 0.036732 | 0.036732 | 0.99731 | -0.051483 | 0.99751 | -0.047705 | 10.0911
11 | -0.030956 | -0.0077586 | 0.030957 | 0.0077595 | 1.4724e-06 | 9.1877e-07 | 0.046409 | 0.046409 | 0.046409 | 0.99254 | -0.14352 | 0.99259 | -0.14252 | 12.7497
12 | -0.16478 | -0.041561 | 0.16482 | 0.041587 | 4.1144e-05 | 2.6237e-05 | 0.24608 | 0.24608 | 0.24608 | 0.99679 | -0.061416 | 0.99706 | -0.056201 | 33.802
13 | 0.12019 | 0.030267 | -0.12008 | -0.030198 | 0.00010796 | 6.8977e-05 | 0.17988 | 0.17988 | 0.17988 | 0.99456 | -0.10437 | 0.99358 | -0.12317 | 49.4167
14 | -0.047331 | -0.011862 | 0.047386 | 0.011897 | 5.4613e-05 | 3.4582e-05 | 0.07115 | 0.071149 | 0.07115 | 0.98988 | -0.19488 | 0.99113 | -0.17069 | 19.5466
15 | -0.072911 | -0.018299 | 0.072966 | 0.018334 | 5.4544e-05 | 3.4752e-05 | 0.10947 | 0.10947 | 0.10947 | 0.99113 | -0.17069 | 0.99194 | -0.15502 | 30.0752
16 | 0.025526 | 0.0064022 | -0.025517 | -0.0063972 | 8.1219e-06 | 5.008e-06 | 0.038324 | 0.038324 | 0.038324 | 0.99113 | -0.17069 | 0.99078 | -0.17737 | 10.5287
17 | -0.013515 | -0.0033873 | 0.013518 | 0.0033886 | 2.4512e-06 | 1.3614e-06 | 0.020224 | 0.020224 | 0.020224 | 0.99442 | -0.10714 | 0.99462 | -0.10334 | 5.5561
18 | 0.11055 | 0.027778 | -0.11044 | -0.027709 | 0.00010743 | 6.8618e-05 | 0.16542 | 0.16542 | 0.16542 | 0.99462 | -0.10334 | 0.99356 | -0.12372 | 45.4445
19 | -0.12407 | -0.031167 | 0.12431 | 0.031322 | 0.0002426 | 0.00015502 | 0.18564 | 0.18564 | 0.18564 | 0.99462 | -0.10334 | 0.99674 | -0.062451 | 51.0005
20 | -0.03742 | -0.0093806 | 0.037427 | 0.0093846 | 6.4456e-06 | 4.0531e-06 | 0.055822 | 0.055822 | 0.055822 | 0.99751 | -0.047705 | 0.9977 | -0.044091 | 15.3356
21 | 0.012797 | 0.0032077 | -0.012796 | -0.0032069 | 1.5693e-06 | 8.5445e-07 | 0.01909 | 0.01909 | 0.01909 | 0.99751 | -0.047705 | 0.99738 | -0.05028 | 5.2445
22 | 0.17819 | 0.044978 | -0.17809 | -0.044913 | 0.0001024 | 6.5334e-05 | 0.26588 | 0.26588 | 0.26588 | 0.9977 | -0.044091 | 0.99707 | -0.056096 | 36.5221
23 | -0.21562 | -0.054363 | 0.21589 | 0.054533 | 0.00026568 | 0.00016968 | 0.3217 | 0.3217 | 0.3217 | 0.9977 | -0.044091 | 0.99904 | -0.018379 | 44.1899
24 | 0.17119 | 0.043182 | -0.17119 | -0.043182 | 8.673e-07 | 5.5323e-07 | 0.25558 | 0.25558 | 0.25558 | 0.99707 | -0.056096 | 0.99706 | -0.056201 | 35.1065
25 | -0.22852 | -0.0577 | 0.22855 | 0.057715 | 2.3875e-05 | 1.5252e-05 | 0.34052 | 0.34052 | 0.34052 | 0.99904 | -0.018379 | 0.99915 | -0.016199 | 46.7753
26 | -0.24002 | -0.06059 | 0.2402 | 0.060709 | 0.00018641 | 0.0001191 | 0.35761 | 0.35761 | 0.35761 | 0.99915 | -0.016199 | 1 | 0 | 49.1219
27 | -0.17347 | -0.043719 | 0.17349 | 0.043733 | 2.1821e-05 | 1.392e-05 | 0.2586 | 0.2586 | 0.2586 | 0.99849 | -0.028948 | 0.99863 | -0.026319 | 35.5219
28 | 0.12451 | 0.031449 | -0.12431 | -0.031322 | 0.00019957 | 0.00012752 | 0.18564 | 0.18564 | 0.18564 | 0.99849 | -0.028948 | 0.99674 | -0.062451 | 51.0005
29 | -0.21725 | -0.054699 | 0.21752 | 0.054874 | 0.00027373 | 0.00017482 | 0.3238 | 0.3238 | 0.3238 | 0.99863 | -0.026319 | 1 | 0 | 44.4779
30 | 0.090631 | 0.022744 | -0.090579 | -0.02271 | 5.2231e-05 | 3.333e-05 | 0.13574 | 0.13574 | 0.13574 | 0.99356 | -0.12372 | 0.99294 | -0.13581 | 37.2924
31 | -0.10038 | -0.025253 | 0.1004 | 0.025265 | 1.9522e-05 | 1.2464e-05 | 0.1504 | 0.1504 | 0.1504 | 0.99337 | -0.12724 | 0.99358 | -0.12317 | 41.3192
32 | 0.10038 | 0.025253 | -0.10037 | -0.025247 | 9.1359e-06 | 5.8331e-06 | 0.1504 | 0.1504 | 0.1504 | 0.99337 | -0.12724 | 0.99327 | -0.12915 | 41.3192
33 | 0.10037 | 0.025247 | -0.10031 | -0.025208 | 6.0738e-05 | 3.878e-05 | 0.1504 | 0.1504 | 0.1504 | 0.99327 | -0.12915 | 0.99262 | -0.14182 | 41.3192
34 | 0.025517 | 0.0063972 | -0.025512 | -0.0063939 | 5.3228e-06 | 3.2822e-06 | 0.038324 | 0.038324 | 0.038324 | 0.99078 | -0.17737 | 0.99056 | -0.18174 | 10.5287
35 | 0.066849 | 0.016763 | -0.066828 | -0.01675 | 2.1369e-05 | 1.3602e-05 | 0.10018 | 0.10018 | 0.10018 | 0.99294 | -0.13581 | 0.99259 | -0.14252 | 27.523
36 | 0.083757 | 0.021059 | -0.083705 | -0.021025 | 5.2737e-05 | 3.3636e-05 | 0.12558 | 0.12558 | 0.12558 | 0.99262 | -0.14182 | 0.99194 | -0.15502 | 34.5009

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4666 | 0.11739

## res_load
| p_mw | q_mvar
0 | 0.0078893 | 0.0019772
1 | 0.0090964 | 0.0022798
2 | 0.0087188 | 0.0021851
3 | 0.0055718 | 0.0013964
4 | 0.011385 | 0.0028533
5 | 0.007632 | 0.0019128
6 | 0.022235 | 0.0055726
7 | 0.0067353 | 0.001688
8 | 0.02059 | 0.0051605
9 | 0.047331 | 0.011862
10 | 0.013515 | 0.0033873
11 | 0.012796 | 0.0032069
12 | 0.0069053 | 0.0017306
13 | 0.012637 | 0.003167
14 | 0.0063636 | 0.0015949
15 | 0.011471 | 0.0028749
16 | 0.048956 | 0.01227
17 | 0.043757 | 0.010966
18 | 0.0072233 | 0.0018103
19 | 0.019813 | 0.0049657
20 | 0.019681 | 0.0049325
21 | 0.025512 | 0.0063939
22 | 0.023729 | 0.0059471
23 | 0.016556 | 0.0041493
24 | 0.010739 | 0.0026914
25 | 0.035871 | 0.0089901

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1