## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-845_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-845_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-845_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-845_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-845_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-845_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-845_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_261-845_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-845_0_4_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_261-845_0_4_node_57 | 0.4 | n |  | TRUE
10 | bus_LV_261-845_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_261-845_0_4_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_261-845_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_261-845_0_4_node_50 | 0.4 | n |  | TRUE
14 | bus_LV_261-845_0_4_node_51 | 0.4 | n |  | TRUE
15 | bus_LV_261-845_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_261-845_0_4_node_48 | 0.4 | n |  | TRUE
17 | bus_LV_261-845_0_4_node_52 | 0.4 | n |  | TRUE
18 | bus_LV_261-845_0_4_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_261-845_0_4_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_261-845_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_261-845_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_261-845_0_4_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_261-845_0_4_node_53 | 0.4 | n |  | TRUE
24 | bus_LV_261-845_0_4_node_37 | 0.4 | n |  | TRUE
25 | bus_LV_261-845_0_4_node_38 | 0.4 | n |  | TRUE
26 | bus_LV_261-845_0_4_node_43 | 0.4 | n |  | TRUE
27 | bus_LV_261-845_0_4_node_39 | 0.4 | n |  | TRUE
28 | bus_LV_261-845_0_4_node_40 | 0.4 | n |  | TRUE
29 | bus_LV_261-845_0_4_node_41 | 0.4 | n |  | TRUE
30 | bus_LV_261-845_0_4_node_42 | 0.4 | n |  | TRUE
31 | bus_LV_261-845_0_4_node_54 | 0.4 | n |  | TRUE
32 | bus_LV_261-845_0_4_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_261-845_0_4_node_46 | 0.4 | n |  | TRUE
34 | bus_LV_261-845_0_4_node_47 | 0.4 | n |  | TRUE
35 | bus_LV_261-845_0_4_node_49 | 0.4 | n |  | TRUE
36 | bus_LV_261-845_0_4_node_55 | 0.4 | n |  | TRUE
37 | bus_LV_261-845_0_4_node_56 | 0.4 | n |  | TRUE
38 | bus_MV_551_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-845_0_4_load_0 | 0 | 0.0021531 | 0.00053962 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-845_0_4_load_1 | 1 | 0.0025558 | 0.00064054 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-845_0_4_load_2 | 2 | 0.01211 | 0.0030351 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-845_0_4_load_32 | 8 | 0.003371 | 0.00084485 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-845_0_4_load_57 | 9 | 0.0021282 | 0.00053339 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-845_0_4_load_36 | 11 | 0.035328 | 0.008854 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-845_0_4_load_50 | 13 | 0.0071953 | 0.0018033 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-845_0_4_load_51 | 14 | 0.0040997 | 0.0010275 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-845_0_4_load_48 | 16 | 0.0072551 | 0.0018183 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-845_0_4_load_52 | 17 | 0.0040063 | 0.0010041 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-845_0_4_load_35 | 18 | 0.014241 | 0.003569 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-845_0_4_load_34 | 19 | 0.023539 | 0.0058993 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-845_0_4_load_33 | 22 | 0.0063484 | 0.0015911 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-845_0_4_load_53 | 23 | 0.0019538 | 0.00048968 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-845_0_4_load_37 | 24 | 0.0042562 | 0.0010667 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-845_0_4_load_38 | 25 | 0.0014458 | 0.00036235 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-845_0_4_load_43 | 26 | 0.0074054 | 0.001856 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-845_0_4_load_39 | 27 | 0.011385 | 0.0028535 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-845_0_4_load_42 | 30 | 0.01268 | 0.003178 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-845_0_4_load_54 | 31 | 0.012648 | 0.00317 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-845_0_4_load_44 | 32 | 0.0019696 | 0.00049362 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-845_0_4_load_47 | 34 | 0.0016815 | 0.00042143 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-845_0_4_load_49 | 35 | 0.012584 | 0.0031538 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-845_0_4_load_55 | 36 | 0.0023845 | 0.00059762 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-845_0_4_load_56 | 37 | 0.0039713 | 0.00099529 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-845_0_4_line_0 |  | 0 | 1 | 0.019023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-845_0_4_line_1 |  | 0 | 2 | 0.039132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-845_0_4_line_2 |  | 1 | 3 | 0.023599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-845_0_4_line_3 |  | 2 | 4 | 0.024173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-845_0_4_line_4 |  | 3 | 5 | 0.006898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-845_0_4_line_5 |  | 4 | 6 | 0.009996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-845_0_4_line_6 |  | 4 | 7 | 0.057551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-845_0_4_line_7 |  | 5 | 8 | 0.015927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-845_0_4_line_8 |  | 6 | 10 | 0.02574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-845_0_4_line_9 |  | 6 | 11 | 0.051239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-845_0_4_line_10 |  | 7 | 9 | 0.017499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-845_0_4_line_11 |  | 9 | 37 | 0.024271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-845_0_4_line_12 |  | 10 | 17 | 0.030038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-845_0_4_line_13 |  | 10 | 13 | 0.026297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-845_0_4_line_14 |  | 12 | 13 | 0.028444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-845_0_4_line_15 |  | 12 | 14 | 0.03419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-845_0_4_line_16 |  | 12 | 15 | 0.041944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-845_0_4_line_17 |  | 12 | 16 | 0.025884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-845_0_4_line_18 |  | 15 | 18 | 0.027478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-845_0_4_line_19 |  | 15 | 19 | 0.044721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-845_0_4_line_20 |  | 16 | 35 | 0.021734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-845_0_4_line_21 |  | 17 | 29 | 0.016935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-845_0_4_line_22 |  | 18 | 24 | 0.045508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-845_0_4_line_23 |  | 19 | 22 | 0.016889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-845_0_4_line_24 |  | 20 | 21 | 0.0082618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-845_0_4_line_25 |  | 20 | 22 | 0.024066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-845_0_4_line_26 |  | 21 | 23 | 0.052968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-845_0_4_line_27 |  | 23 | 34 | 0.022289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-845_0_4_line_28 |  | 24 | 25 | 0.0089451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-845_0_4_line_29 |  | 25 | 26 | 0.010308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-845_0_4_line_30 |  | 27 | 28 | 0.0020782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-845_0_4_line_31 |  | 28 | 29 | 0.022444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-845_0_4_line_32 |  | 28 | 30 | 0.025361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-845_0_4_line_33 |  | 30 | 31 | 0.01965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-845_0_4_line_34 |  | 32 | 33 | 0.0097855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-845_0_4_line_35 |  | 33 | 34 | 0.0068227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-845_0_4_line_36 |  | 36 | 37 | 0.025425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-845_0_4_trafo_9 | 0.63 MVA 20/0.4 kV | 38 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2685259.0785 | 1251219.807 | 2685275.4594 | 1251210.1359
1 | 2685259.0785 | 1251219.807 | 2685228.9389 | 1251237.6011 | 2685225.5188 | 1251239.9187
2 | 2685296.395 | 1251199.3427 | 2685294.8644 | 1251199.7432 | 2685279.0588 | 1251208.0109 | 2685275.4594 | 1251210.1359
3 | 2685205.6683 | 1251253.7008 | 2685209.1111 | 1251251.0372 | 2685225.5188 | 1251239.9187
4 | 2685303.0309 | 1251200.8838 | 2685301.119 | 1251199.9779 | 2685298.8026 | 1251199.3774 | 2685296.395 | 1251199.3427
5 | 2685204.7604 | 1251263.2838 | 2685203.8422 | 1251259.9459 | 2685204.5179 | 1251256.5308 | 2685205.6683 | 1251253.7008
6 | 2685163.3137 | 1251232.5873 | 2685175.9646 | 1251245.2453 | 2685179.3662 | 1251242.8257 | 2685184.8433 | 1251242.0038 | 2685194.4154 | 1251237.7937 | 2685198.0925 | 1251242.9838 | 2685201.1627 | 1251247.3312 | 2685205.6683 | 1251253.7008
7 | 2685303.0309 | 1251200.8838 | 2685305.8863 | 1251203.8939 | 2685310.4428 | 1251214.7545
8 | 2685204.7604 | 1251263.2838 | 2685201.0557 | 1251266.3106 | 2685197.4692 | 1251269.517 | 2685197.9275 | 1251269.6682 | 2685202.1418 | 1251273.1981 | 2685208.474 | 1251281.1507
9 | 2685204.7604 | 1251263.2838 | 2685204.9182 | 1251263.8643 | 2685206.23 | 1251266.0737 | 2685215.5358 | 1251276.1707 | 2685227.2897 | 1251290.3059 | 2685237.0104 | 1251302.9553
10 | 2685163.3137 | 1251232.5873 | 2685155.6362 | 1251235.7571 | 2685148.7468 | 1251241.844
11 | 2685148.7468 | 1251241.844 | 2685138.41 | 1251250.9766 | 2685130.5182 | 1251257.8689
12 | 2685208.474 | 1251281.1507 | 2685199.478 | 1251288.349 | 2685192.54 | 1251292.0743 | 2685183.9636 | 1251298.3746
13 | 2685208.474 | 1251281.1507 | 2685224.8549 | 1251301.7221
14 | 2685242.4752 | 1251324.0496 | 2685239.3935 | 1251319.98 | 2685224.8549 | 1251301.7221
15 | 2685242.4752 | 1251324.0496 | 2685263.12 | 1251351.303
16 | 2685242.4752 | 1251324.0496 | 2685245.7959 | 1251321.4732 | 2685266.4193 | 1251348.19 | 2685269.624 | 1251345.8121
17 | 2685242.4752 | 1251324.0496 | 2685220.1677 | 1251337.1784
18 | 2685269.624 | 1251345.8121 | 2685286.2771 | 1251367.6682
19 | 2685269.624 | 1251345.8121 | 2685291.9447 | 1251330.6663 | 2685306.6294 | 1251320.7012
20 | 2685200.4257 | 1251345.7835 | 2685209.7766 | 1251343.2939 | 2685220.1677 | 1251337.1784
21 | 2685170.3157 | 1251308.4004 | 2685183.9636 | 1251298.3746
22 | 2685313.8584 | 1251403.8657 | 2685305.3632 | 1251392.7172 | 2685286.2771 | 1251367.6682
23 | 2685306.6294 | 1251320.7012 | 2685319.0452 | 1251312.2759 | 2685320.6045 | 1251311.218
24 | 2685340.5199 | 1251297.7075 | 2685344.0754 | 1251296.6579 | 2685345.9708 | 1251300.7994
25 | 2685340.5199 | 1251297.7075 | 2685320.6045 | 1251311.218
26 | 2685345.9708 | 1251300.7994 | 2685364.8843 | 1251350.2755
27 | 2685372.8432 | 1251371.0951 | 2685364.8843 | 1251350.2755
28 | 2685313.8584 | 1251403.8657 | 2685319.2799 | 1251410.9806
29 | 2685325.5275 | 1251419.1795 | 2685319.2799 | 1251410.9806
30 | 2685152.1886 | 1251321.7055 | 2685150.513 | 1251322.9348
31 | 2685152.1886 | 1251321.7055 | 2685170.3157 | 1251308.4004
32 | 2685152.1886 | 1251321.7055 | 2685167.8265 | 1251341.6709
33 | 2685176.7764 | 1251357.8082 | 2685177.6805 | 1251354.2519 | 2685167.8265 | 1251341.6709
34 | 2685375.2794 | 1251377.4681 | 2685376.5305 | 1251380.7441 | 2685378.81 | 1251386.5944
35 | 2685375.2794 | 1251377.4681 | 2685372.8432 | 1251371.0951
36 | 2685111.3684 | 1251274.5931 | 2685130.5182 | 1251257.8689

## bus_geodata
| x | y | coords
0 | 2685259.0785 | 1251219.807
1 | 2685275.4594 | 1251210.1359
2 | 2685225.5188 | 1251239.9187
3 | 2685296.395 | 1251199.3427
4 | 2685205.6683 | 1251253.7008
5 | 2685303.0309 | 1251200.8838
6 | 2685204.7604 | 1251263.2838
7 | 2685163.3137 | 1251232.5873
8 | 2685310.4428 | 1251214.7545
9 | 2685148.7468 | 1251241.844
10 | 2685208.474 | 1251281.1507
11 | 2685237.0104 | 1251302.9553
12 | 2685242.4752 | 1251324.0496
13 | 2685224.8549 | 1251301.7221
14 | 2685263.12 | 1251351.303
15 | 2685269.624 | 1251345.8121
16 | 2685220.1677 | 1251337.1784
17 | 2685183.9636 | 1251298.3746
18 | 2685286.2771 | 1251367.6682
19 | 2685306.6294 | 1251320.7012
20 | 2685340.5199 | 1251297.7074
21 | 2685345.9708 | 1251300.7994
22 | 2685320.6045 | 1251311.218
23 | 2685364.8843 | 1251350.2755
24 | 2685313.8584 | 1251403.8657
25 | 2685319.2799 | 1251410.9806
26 | 2685325.5275 | 1251419.1795
27 | 2685150.513 | 1251322.9348
28 | 2685152.1886 | 1251321.7055
29 | 2685170.3157 | 1251308.4004
30 | 2685167.8265 | 1251341.6709
31 | 2685176.7764 | 1251357.8082
32 | 2685378.81 | 1251386.5944
33 | 2685375.2794 | 1251377.4681
34 | 2685372.8432 | 1251371.0951
35 | 2685200.4257 | 1251345.7835
36 | 2685111.3684 | 1251274.5931
37 | 2685130.5182 | 1251257.8689
38 | 2685245.7959 | 1251321.4732

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99207 | -0.15244 | 0.0021531 | 0.00053962
1 | 0.99196 | -0.15444 | 0.0025558 | 0.00064054
2 | 0.99236 | -0.14684 | 0.01211 | 0.0030351
3 | 0.99189 | -0.15585 | 0 | 0
4 | 0.9928 | -0.13821 | 0 | 0
5 | 0.99187 | -0.15626 | 0 | 0
6 | 0.99306 | -0.13314 | 0 | 0
7 | 0.99236 | -0.14685 | 0 | 0
8 | 0.99182 | -0.15721 | 0.003371 | 0.00084485
9 | 0.99222 | -0.14948 | 0.0021282 | 0.00053339
10 | 0.99457 | -0.10406 | 0 | 0
11 | 0.99141 | -0.16519 | 0.035328 | 0.008854
12 | 1 | 0 | -0.20139 | -0.050453
13 | 0.99709 | -0.055655 | 0.0071953 | 0.0018033
14 | 0.99987 | -0.0024437 | 0.0040997 | 0.0010275
15 | 0.9976 | -0.046058 | 0 | 0
16 | 0.99953 | -0.0089548 | 0.0072551 | 0.0018183
17 | 0.99345 | -0.12564 | 0.0040063 | 0.0010041
18 | 0.99692 | -0.059229 | 0.014241 | 0.003569
19 | 0.99616 | -0.0739 | 0.023539 | 0.0058993
20 | 0.99585 | -0.07982 | 0 | 0
21 | 0.99581 | -0.080634 | 0 | 0
22 | 0.99597 | -0.077448 | 0.0063484 | 0.0015911
23 | 0.99554 | -0.085856 | 0.0019538 | 0.00048968
24 | 0.99637 | -0.069696 | 0.0042562 | 0.0010667
25 | 0.9963 | -0.071086 | 0.0014458 | 0.00036235
26 | 0.99623 | -0.072427 | 0.0074054 | 0.001856
27 | 0.99211 | -0.15163 | 0.011385 | 0.0028535
28 | 0.99213 | -0.15121 | 0 | 0
29 | 0.99288 | -0.13663 | 0 | 0
30 | 0.99154 | -0.16259 | 0.01268 | 0.003178
31 | 0.99132 | -0.167 | 0.012648 | 0.00317
32 | 0.99543 | -0.087863 | 0.0019696 | 0.00049362
33 | 0.99545 | -0.087524 | 0 | 0
34 | 0.99546 | -0.087287 | 0.0016815 | 0.00042143
35 | 0.99929 | -0.013727 | 0.012584 | 0.0031538
36 | 0.99202 | -0.15328 | 0.0023845 | 0.00059762
37 | 0.99208 | -0.15221 | 0.0039713 | 0.00099529
38 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0059278 | 0.0014852 | -0.0059272 | -0.0014851 | 5.6391e-07 | 1.1531e-07 | 0.008891 | 0.0088911 | 0.0088911 | 0.99207 | -0.15244 | 0.99196 | -0.15444 | 2.4426
1 | -0.0080809 | -0.0020248 | 0.0080831 | 0.0020257 | 2.1557e-06 | 8.7425e-07 | 0.01212 | 0.01212 | 0.01212 | 0.99207 | -0.15244 | 0.99236 | -0.14684 | 3.3298
2 | 0.0033715 | 0.00084454 | -0.0033712 | -0.0008447 | 2.2635e-07 | -1.5977e-07 | 0.0050573 | 0.0050574 | 0.0050574 | 0.99196 | -0.15444 | 0.99189 | -0.15585 | 1.3894
3 | -0.020193 | -0.0050608 | 0.020202 | 0.0050658 | 8.3111e-06 | 5.0066e-06 | 0.03028 | 0.030279 | 0.03028 | 0.99236 | -0.14684 | 0.9928 | -0.13821 | 8.3186
4 | 0.0033712 | 0.0008447 | -0.0033712 | -0.00084475 | 6.6162e-08 | -4.669e-08 | 0.0050574 | 0.0050574 | 0.0050574 | 0.99189 | -0.15585 | 0.99187 | -0.15626 | 1.3894
5 | -0.028691 | -0.007194 | 0.028698 | 0.0071984 | 6.9322e-06 | 4.3073e-06 | 0.043004 | 0.043004 | 0.043004 | 0.9928 | -0.13821 | 0.99306 | -0.13314 | 11.8142
6 | 0.0084895 | 0.0021282 | -0.008486 | -0.0021267 | 3.4943e-06 | 1.4925e-06 | 0.012724 | 0.012725 | 0.012725 | 0.9928 | -0.13821 | 0.99236 | -0.14685 | 3.4958
7 | 0.0033712 | 0.00084475 | -0.003371 | -0.00084485 | 1.5276e-07 | -1.0779e-07 | 0.0050574 | 0.0050575 | 0.0050575 | 0.99187 | -0.15626 | 0.99182 | -0.15721 | 1.3894
8 | -0.06408 | -0.016086 | 0.064169 | 0.016143 | 8.901e-05 | 5.6633e-05 | 0.096028 | 0.096027 | 0.096028 | 0.99306 | -0.13314 | 0.99457 | -0.10406 | 26.3812
9 | 0.035382 | 0.0088879 | -0.035328 | -0.008854 | 5.4023e-05 | 3.3913e-05 | 0.053024 | 0.053024 | 0.053024 | 0.99306 | -0.13314 | 0.99141 | -0.16519 | 14.5671
10 | 0.008486 | 0.0021267 | -0.008485 | -0.0021263 | 1.0625e-06 | 4.5397e-07 | 0.012725 | 0.012725 | 0.012725 | 0.99236 | -0.14685 | 0.99222 | -0.14948 | 3.4958
11 | 0.0063567 | 0.0015929 | -0.0063559 | -0.0015927 | 8.2714e-07 | 2.1593e-07 | 0.009533 | 0.0095331 | 0.0095331 | 0.99222 | -0.14948 | 0.99208 | -0.15221 | 2.619
12 | 0.040824 | 0.01027 | -0.040782 | -0.010244 | 4.2041e-05 | 2.6517e-05 | 0.061092 | 0.061092 | 0.061092 | 0.99457 | -0.10406 | 0.99345 | -0.12564 | 16.7836
13 | -0.10499 | -0.026413 | 0.10524 | 0.026569 | 0.00024344 | 0.00015546 | 0.15712 | 0.15712 | 0.15712 | 0.99457 | -0.10406 | 0.99709 | -0.055655 | 43.1647
14 | 0.11273 | 0.028564 | -0.11243 | -0.028372 | 0.00030054 | 0.00019197 | 0.16786 | 0.16786 | 0.16786 | 1 | 0 | 0.99709 | -0.055655 | 46.1146
15 | 0.0041002 | 0.0010273 | -0.0040997 | -0.0010275 | 4.7726e-07 | -1.4305e-07 | 0.0061011 | 0.0061012 | 0.0061012 | 1 | 0 | 0.99987 | -0.0024437 | 1.6762
16 | 0.063055 | 0.015883 | -0.062916 | -0.015795 | 0.00013855 | 8.8125e-05 | 0.093855 | 0.093855 | 0.093855 | 1 | 0 | 0.9976 | -0.046058 | 25.7844
17 | 0.01985 | 0.0049787 | -0.019842 | -0.0049736 | 8.4692e-06 | 5.0809e-06 | 0.029538 | 0.029539 | 0.029539 | 1 | 0 | 0.99953 | -0.0089548 | 8.115
18 | 0.027373 | 0.0068687 | -0.027356 | -0.0068581 | 1.718e-05 | 1.0636e-05 | 0.040832 | 0.040832 | 0.040832 | 0.9976 | -0.046058 | 0.99692 | -0.059229 | 11.2176
19 | 0.035544 | 0.0089258 | -0.035497 | -0.0088962 | 4.7149e-05 | 2.9592e-05 | 0.053023 | 0.053023 | 0.053023 | 0.9976 | -0.046058 | 0.99616 | -0.0739 | 14.5668
20 | 0.012586 | 0.0031553 | -0.012584 | -0.0031538 | 2.8616e-06 | 1.5466e-06 | 0.018738 | 0.018738 | 0.018738 | 0.99953 | -0.0089548 | 0.99929 | -0.013727 | 5.1478
21 | 0.036776 | 0.0092396 | -0.036756 | -0.0092275 | 1.9274e-05 | 1.2116e-05 | 0.055091 | 0.055091 | 0.055091 | 0.99345 | -0.12564 | 0.99288 | -0.13663 | 15.135
22 | 0.013115 | 0.003289 | -0.013108 | -0.0032854 | 6.5402e-06 | 3.5927e-06 | 0.019576 | 0.019577 | 0.019577 | 0.99692 | -0.059229 | 0.99637 | -0.069696 | 5.3782
23 | 0.011958 | 0.0029969 | -0.011956 | -0.0029958 | 2.0207e-06 | 1.0734e-06 | 0.017862 | 0.017862 | 0.017862 | 0.99616 | -0.0739 | 0.99597 | -0.077448 | 4.9072
24 | 0.0056068 | 0.0014046 | -0.0056066 | -0.0014046 | 2.1745e-07 | 3.1679e-08 | 0.0083776 | 0.0083777 | 0.0083777 | 0.99585 | -0.07982 | 0.99581 | -0.080634 | 2.3016
25 | -0.0056068 | -0.0014046 | 0.0056075 | 0.0014047 | 6.3338e-07 | 9.2217e-08 | 0.0083776 | 0.0083775 | 0.0083776 | 0.99585 | -0.07982 | 0.99597 | -0.077448 | 2.3015
26 | 0.0056066 | 0.0014046 | -0.0056052 | -0.0014044 | 1.3941e-06 | 2.0334e-07 | 0.0083777 | 0.0083779 | 0.0083779 | 0.99581 | -0.080634 | 0.99554 | -0.085856 | 2.3016
27 | 0.0036514 | 0.00091474 | -0.0036511 | -0.00091487 | 2.4896e-07 | -1.3046e-07 | 0.0054575 | 0.0054576 | 0.0054576 | 0.99554 | -0.085856 | 0.99546 | -0.087287 | 1.4994
28 | 0.0088522 | 0.0022187 | -0.0088516 | -0.0022185 | 5.8626e-07 | 2.5871e-07 | 0.01322 | 0.01322 | 0.01322 | 0.99637 | -0.069696 | 0.9963 | -0.071086 | 3.6319
29 | 0.0074059 | 0.0018561 | -0.0074054 | -0.001856 | 4.7292e-07 | 1.6845e-07 | 0.011061 | 0.011061 | 0.011061 | 0.9963 | -0.071086 | 0.99623 | -0.072427 | 3.0387
30 | -0.011385 | -0.0028535 | 0.011386 | 0.0028536 | 2.2725e-07 | 1.1861e-07 | 0.017076 | 0.017076 | 0.017076 | 0.99211 | -0.15163 | 0.99213 | -0.15121 | 4.6913
31 | -0.036731 | -0.0092115 | 0.036756 | 0.0092275 | 2.5545e-05 | 1.6059e-05 | 0.055092 | 0.055091 | 0.055092 | 0.99213 | -0.15121 | 0.99288 | -0.13663 | 15.135
32 | 0.025345 | 0.0063579 | -0.025331 | -0.0063494 | 1.3744e-05 | 8.4687e-06 | 0.038015 | 0.038015 | 0.038015 | 0.99213 | -0.15121 | 0.99154 | -0.16259 | 10.4437
33 | 0.012651 | 0.0031714 | -0.012648 | -0.00317 | 2.6561e-06 | 1.4465e-06 | 0.018986 | 0.018986 | 0.018986 | 0.99154 | -0.16259 | 0.99132 | -0.167 | 5.2159
34 | -0.0019696 | -0.00049362 | 0.0019696 | 0.00049351 | 3.1808e-08 | -1.0685e-07 | 0.0029442 | 0.0029441 | 0.0029442 | 0.99543 | -0.087863 | 0.99545 | -0.087524 | 0.80884
35 | -0.0019696 | -0.00049351 | 0.0019696 | 0.00049344 | 2.2177e-08 | -7.4504e-08 | 0.0029441 | 0.0029441 | 0.0029441 | 0.99545 | -0.087524 | 0.99546 | -0.087287 | 0.80883
36 | -0.0023845 | -0.00059762 | 0.0023846 | 0.00059737 | 1.2197e-07 | -2.5021e-07 | 0.0035767 | 0.0035766 | 0.0035767 | 0.99202 | -0.15328 | 0.99208 | -0.15221 | 0.98262

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.20139 | 0.050453

## res_load
| p_mw | q_mvar
0 | 0.0021531 | 0.00053962
1 | 0.0025558 | 0.00064054
2 | 0.01211 | 0.0030351
3 | 0.003371 | 0.00084485
4 | 0.0021282 | 0.00053339
5 | 0.035328 | 0.008854
6 | 0.0071953 | 0.0018033
7 | 0.0040997 | 0.0010275
8 | 0.0072551 | 0.0018183
9 | 0.0040063 | 0.0010041
10 | 0.014241 | 0.003569
11 | 0.023539 | 0.0058993
12 | 0.0063484 | 0.0015911
13 | 0.0019538 | 0.00048968
14 | 0.0042562 | 0.0010667
15 | 0.0014458 | 0.00036235
16 | 0.0074054 | 0.001856
17 | 0.011385 | 0.0028535
18 | 0.01268 | 0.003178
19 | 0.012648 | 0.00317
20 | 0.0019696 | 0.00049362
21 | 0.0016815 | 0.00042143
22 | 0.012584 | 0.0031538
23 | 0.0023845 | 0.00059762
24 | 0.0039713 | 0.00099529

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1