## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-85_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-85_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-85_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-85_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-85_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_261-85_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_261-85_0_4_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_261-85_0_4_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_261-85_0_4_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_261-85_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_261-85_0_4_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_261-85_0_4_node_22 | 0.4 | n |  | TRUE
12 | bus_LV_261-85_0_4_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_261-85_0_4_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_261-85_0_4_node_42 | 0.4 | n |  | TRUE
15 | bus_LV_261-85_0_4_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_261-85_0_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_261-85_0_4_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_261-85_0_4_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_261-85_0_4_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_261-85_0_4_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_261-85_0_4_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_261-85_0_4_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_261-85_0_4_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_261-85_0_4_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_261-85_0_4_node_10 | 0.4 | n |  | TRUE
26 | bus_LV_261-85_0_4_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_261-85_0_4_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_261-85_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_261-85_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_261-85_0_4_node_44 | 0.4 | n |  | TRUE
31 | bus_LV_261-85_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_261-85_0_4_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_261-85_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_261-85_0_4_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_261-85_0_4_node_38 | 0.4 | n |  | TRUE
36 | bus_MV_544_0_node_108 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-85_0_4_load_0 | 0 | 0.083323 | 0.020883 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-85_0_4_load_7 | 4 | 0.017714 | 0.0044395 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-85_0_4_load_27 | 8 | 0.0094991 | 0.0023807 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-85_0_4_load_28 | 10 | 0.073969 | 0.018538 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-85_0_4_load_24 | 12 | 0.034783 | 0.0087173 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-85_0_4_load_42 | 14 | 0.0060231 | 0.0015095 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-85_0_4_load_34 | 15 | 0.0067337 | 0.0016876 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-85_0_4_load_20 | 17 | 0.010664 | 0.0026726 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-85_0_4_load_31 | 18 | 0.015049 | 0.0037717 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-85_0_4_load_40 | 21 | 0.0091285 | 0.0022878 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-85_0_4_load_37 | 22 | 0.0052182 | 0.0013078 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-85_0_4_load_43 | 23 | 0.0072713 | 0.0018224 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-85_0_4_load_33 | 24 | 0.0066539 | 0.0016676 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-85_0_4_load_10 | 25 | 0.014916 | 0.0037384 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-85_0_4_load_13 | 27 | 0.0062331 | 0.0015622 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-85_0_4_load_14 | 28 | 0.0089599 | 0.0022456 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-85_0_4_load_18 | 29 | 0.0065709 | 0.0016468 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-85_0_4_load_44 | 30 | 0.0078913 | 0.0019777 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-85_0_4_load_19 | 31 | 0.0091887 | 0.0023029 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-85_0_4_load_21 | 32 | 0.009257 | 0.00232 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-85_0_4_load_23 | 33 | 0.0085364 | 0.0021394 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-85_0_4_load_36 | 34 | 0.0072499 | 0.001817 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-85_0_4_load_38 | 35 | 0.0021524 | 0.00053944 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-85_0_4_line_0 |  | 0 | 1 | 0.020057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_261-85_0_4_line_1 |  | 0 | 2 | 0.037843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-85_0_4_line_2 |  | 1 | 3 | 0.032618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_261-85_0_4_line_3 |  | 2 | 4 | 0.066552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-85_0_4_line_4 |  | 2 | 5 | 0.010868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-85_0_4_line_5 |  | 2 | 6 | 0.0087193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-85_0_4_line_6 |  | 3 | 9 | 0.017216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-85_0_4_line_7 |  | 3 | 10 | 0.026466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-85_0_4_line_8 |  | 3 | 7 | 0.058721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-85_0_4_line_9 |  | 5 | 13 | 0.041366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-85_0_4_line_10 |  | 5 | 14 | 0.01641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-85_0_4_line_11 |  | 6 | 15 | 0.0099757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-85_0_4_line_12 |  | 7 | 8 | 0.017954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-85_0_4_line_13 |  | 9 | 11 | 0.020121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-85_0_4_line_14 |  | 9 | 12 | 0.009678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-85_0_4_line_15 |  | 11 | 16 | 0.055592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-85_0_4_line_16 |  | 11 | 17 | 0.019386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-85_0_4_line_17 |  | 13 | 18 | 0.0096536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-85_0_4_line_18 |  | 14 | 19 | 0.021528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-85_0_4_line_19 |  | 15 | 24 | 0.03482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-85_0_4_line_20 |  | 16 | 29 | 0.011123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-85_0_4_line_21 |  | 17 | 31 | 0.018668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-85_0_4_line_22 |  | 19 | 23 | 0.002901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-85_0_4_line_23 |  | 19 | 20 | 0.10561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-85_0_4_line_24 |  | 20 | 21 | 0.04663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-85_0_4_line_25 |  | 20 | 22 | 0.018175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-85_0_4_line_26 |  | 22 | 34 | 0.024076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-85_0_4_line_27 |  | 25 | 26 | 0.015115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-85_0_4_line_28 |  | 26 | 27 | 0.013974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-85_0_4_line_29 |  | 26 | 28 | 0.035606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-85_0_4_line_30 |  | 27 | 29 | 0.016573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-85_0_4_line_31 |  | 28 | 30 | 0.019158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-85_0_4_line_32 |  | 31 | 32 | 0.01656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-85_0_4_line_33 |  | 32 | 33 | 0.016766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-85_0_4_line_34 |  | 34 | 35 | 0.02502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-85_0_4_trafo_1 | 0.63 MVA 20/0.4 kV | 36 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2681492.5298 | 1249947.4816 | 2681491.3161 | 1249929.2292 | 2681491.1811 | 1249927.4698
1 | 2681481.888 | 1249893.3843 | 2681483.6239 | 1249892.8855 | 2681486.5339 | 1249896.506 | 2681488.5712 | 1249904.829 | 2681490.0228 | 1249912.3768 | 2681491.1811 | 1249927.4698
2 | 2681492.5298 | 1249947.4816 | 2681497.2882 | 1249947.3581 | 2681498.5737 | 1249957.0941 | 2681499.3574 | 1249964.3435 | 2681497.1084 | 1249967.5594 | 2681498.9812 | 1249969.7312 | 2681502.8506 | 1249968.9171
3 | 2681481.888 | 1249893.3843 | 2681477.4001 | 1249894.7013 | 2681457.5698 | 1249899.31 | 2681444.1893 | 1249902.1394 | 2681441.6614 | 1249902.5827 | 2681417.6313 | 1249906.778 | 2681416.7655 | 1249906.9321
4 | 2681488.1577 | 1249888.2333 | 2681481.0677 | 1249889.8926 | 2681481.888 | 1249893.3843
5 | 2681479.8982 | 1249884.8951 | 2681481.0677 | 1249889.8926 | 2681481.888 | 1249893.3843
6 | 2681496.0577 | 1249979.7206 | 2681495.7953 | 1249974.6466 | 2681495.551 | 1249969.9064 | 2681498.9812 | 1249969.7312 | 2681502.8506 | 1249968.9171
7 | 2681502.8506 | 1249968.9171 | 2681503.8309 | 1249959.1345 | 2681520.0951 | 1249955.6439
8 | 2681445.387 | 1249964.4018 | 2681460.9656 | 1249965.3277 | 2681479.8981 | 1249967.2448 | 2681492.3686 | 1249966.8827 | 2681497.1084 | 1249967.5594 | 2681498.9812 | 1249969.7312 | 2681502.8506 | 1249968.9171
9 | 2681488.1577 | 1249888.2333 | 2681492.5015 | 1249907.2738 | 2681493.6178 | 1249917.7858 | 2681494.1185 | 1249923.6525 | 2681499.4864 | 1249923.1371
10 | 2681488.1577 | 1249888.2333 | 2681503.9106 | 1249883.6355
11 | 2681479.8982 | 1249884.8951 | 2681470.1943 | 1249887.2081
12 | 2681445.387 | 1249964.4018 | 2681437.98 | 1249965.512 | 2681428.6407 | 1249966.0285 | 2681427.5635 | 1249966.3002
13 | 2681496.0577 | 1249979.7206 | 2681491.6659 | 1249982.8403 | 2681489.9544 | 1249997.4832
14 | 2681496.0577 | 1249979.7206 | 2681505.6511 | 1249978.4434
15 | 2681466.5715 | 1250043.0288 | 2681469.126 | 1250037.9046 | 2681476.5946 | 1250034.5047 | 2681483.6646 | 1250028.7977 | 2681486.738 | 1250024.9259 | 2681489.9544 | 1249997.4832
16 | 2681489.9544 | 1249997.4832 | 2681473.0043 | 1250001.3086 | 2681471.0001 | 1250001.4502
17 | 2681499.4864 | 1249923.1371 | 2681509.1058 | 1249922.3251
18 | 2681524.5761 | 1249877.6039 | 2681503.9106 | 1249883.6355
19 | 2681470.1943 | 1249887.2081 | 2681454.5818 | 1249890.9294 | 2681436.1771 | 1249894.6126
20 | 2681466.5715 | 1250043.0288 | 2681455.4501 | 1250043.2034
21 | 2681471.0001 | 1250001.4502 | 2681455.3497 | 1250002.5558 | 2681452.373 | 1250002.6685
22 | 2681524.5761 | 1249877.6039 | 2681525.6793 | 1249880.2878
23 | 2681486.3584 | 1249814.2984 | 2681488.0376 | 1249819.025 | 2681489.535 | 1249823.2375 | 2681491.682 | 1249822.4998 | 2681493.8784 | 1249824.7539 | 2681496.2047 | 1249835.6717 | 2681496.4726 | 1249844.1928 | 2681494.432 | 1249853.1158 | 2681490.6472 | 1249865.8843 | 2681491.7752 | 1249868.4128 | 2681494.7678 | 1249869.3213 | 2681499.8139 | 1249869.6909 | 2681521.3615 | 1249869.7873 | 2681527.6469 | 1249871.7307 | 2681523.105 | 1249873.1248 | 2681524.5761 | 1249877.6039
24 | 2681486.3584 | 1249814.2984 | 2681477.4511 | 1249791.6259 | 2681462.6204 | 1249775.0114
25 | 2681486.3584 | 1249814.2984 | 2681478.9745 | 1249817.01 | 2681470.6025 | 1249819.0965 | 2681468.9391 | 1249819.3395
26 | 2681445.1134 | 1249822.803 | 2681452.3768 | 1249821.7591 | 2681468.9391 | 1249819.3395
27 | 2681424.9075 | 1250043.7236 | 2681409.793 | 1250043.8779
28 | 2681424.9075 | 1250043.7236 | 2681438.8794 | 1250043.476
29 | 2681424.9075 | 1250043.7236 | 2681426.1272 | 1250053.8589 | 2681425.9227 | 1250066.5433 | 2681413.3917 | 1250068.6802
30 | 2681438.8794 | 1250043.476 | 2681445.0488 | 1250043.3667 | 2681455.4501 | 1250043.2034
31 | 2681413.3917 | 1250068.6802 | 2681405.6483 | 1250070.0007 | 2681394.3795 | 1250070.8714
32 | 2681435.8264 | 1250003.3185 | 2681437.0308 | 1250003.2491 | 2681452.373 | 1250002.6685
33 | 2681435.8264 | 1250003.3185 | 2681420.0595 | 1250004.2278 | 2681419.087 | 1250004.2513
34 | 2681445.1134 | 1249822.803 | 2681420.348 | 1249826.3622

## bus_geodata
| x | y | coords
0 | 2681491.1811 | 1249927.4698
1 | 2681492.5298 | 1249947.4816
2 | 2681481.888 | 1249893.3843
3 | 2681502.8506 | 1249968.9171
4 | 2681416.7655 | 1249906.9321
5 | 2681488.1577 | 1249888.2333
6 | 2681479.8982 | 1249884.8951
7 | 2681445.387 | 1249964.4018
8 | 2681427.5635 | 1249966.3002
9 | 2681496.0577 | 1249979.7206
10 | 2681520.0951 | 1249955.6439
11 | 2681489.9544 | 1249997.4832
12 | 2681505.6511 | 1249978.4434
13 | 2681499.4864 | 1249923.1371
14 | 2681503.9106 | 1249883.6355
15 | 2681470.1943 | 1249887.2081
16 | 2681466.5715 | 1250043.0288
17 | 2681471.0001 | 1250001.4502
18 | 2681509.1058 | 1249922.3251
19 | 2681524.5761 | 1249877.6039
20 | 2681486.3584 | 1249814.2984
21 | 2681462.6204 | 1249775.0114
22 | 2681468.9391 | 1249819.3395
23 | 2681525.6793 | 1249880.2878
24 | 2681436.1771 | 1249894.6126
25 | 2681409.793 | 1250043.8779
26 | 2681424.9075 | 1250043.7236
27 | 2681438.8794 | 1250043.476
28 | 2681413.3917 | 1250068.6802
29 | 2681455.4501 | 1250043.2034
30 | 2681394.3795 | 1250070.8714
31 | 2681452.373 | 1250002.6685
32 | 2681435.8264 | 1250003.3185
33 | 2681419.087 | 1250004.2513
34 | 2681445.1134 | 1249822.803
35 | 2681420.348 | 1249826.3622
36 | 2681499.3574 | 1249964.3435

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99848 | -0.029153 | 0.083323 | 0.020883
1 | 1 | 0 | -0.37044 | -0.093117
2 | 0.99561 | -0.084363 | 0 | 0
3 | 0.99702 | -0.057159 | 0 | 0
4 | 0.99453 | -0.10512 | 0.017714 | 0.0044395
5 | 0.99509 | -0.094326 | 0 | 0
6 | 0.9955 | -0.086416 | 0 | 0
7 | 0.99651 | -0.066946 | 0 | 0
8 | 0.99635 | -0.06994 | 0.0094991 | 0.0023807
9 | 0.99517 | -0.092546 | 0 | 0
10 | 0.99523 | -0.091546 | 0.073969 | 0.018538
11 | 0.99366 | -0.12171 | 0 | 0
12 | 0.99487 | -0.098472 | 0.034783 | 0.0087173
13 | 0.99452 | -0.10529 | 0 | 0
14 | 0.99453 | -0.10503 | 0.0060231 | 0.0015095
15 | 0.99538 | -0.088766 | 0.0067337 | 0.0016876
16 | 0.99139 | -0.16555 | 0 | 0
17 | 0.99299 | -0.1346 | 0.010664 | 0.0026726
18 | 0.99439 | -0.10785 | 0.015049 | 0.0037717
19 | 0.99392 | -0.11681 | 0 | 0
20 | 0.99163 | -0.16118 | 0 | 0
21 | 0.99124 | -0.16872 | 0.0091285 | 0.0022878
22 | 0.99139 | -0.16589 | 0.0052182 | 0.0013078
23 | 0.9939 | -0.11718 | 0.0072713 | 0.0018224
24 | 0.99517 | -0.092843 | 0.0066539 | 0.0016676
25 | 0.98975 | -0.19744 | 0.014916 | 0.0037384
26 | 0.98995 | -0.19343 | 0 | 0
27 | 0.99036 | -0.18553 | 0.0062331 | 0.0015622
28 | 0.9894 | -0.2041 | 0.0089599 | 0.0022456
29 | 0.99094 | -0.17435 | 0.0065709 | 0.0016468
30 | 0.98926 | -0.2068 | 0.0078913 | 0.0019777
31 | 0.99253 | -0.14351 | 0.0091887 | 0.0023029
32 | 0.99226 | -0.14872 | 0.009257 | 0.00232
33 | 0.99213 | -0.15126 | 0.0085364 | 0.0021394
34 | 0.99118 | -0.1699 | 0.0072499 | 0.001817
35 | 0.99113 | -0.17086 | 0.0021524 | 0.00053944
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.16689 | -0.041965 | 0.16712 | 0.042113 | 0.00023272 | 0.00014842 | 0.24876 | 0.24876 | 0.24876 | 0.99848 | -0.029153 | 1 | 0 | 34.1705
1 | 0.083566 | 0.021082 | -0.083346 | -0.020942 | 0.00022027 | 0.00014048 | 0.12459 | 0.12459 | 0.12459 | 0.99848 | -0.029153 | 0.99561 | -0.084363 | 34.2269
2 | 0.20167 | 0.051003 | -0.20112 | -0.050651 | 0.00055134 | 0.000352 | 0.30025 | 0.30025 | 0.30025 | 1 | 0 | 0.99702 | -0.057159 | 41.2426
3 | 0.017732 | 0.0044499 | -0.017714 | -0.0044395 | 1.7531e-05 | 1.0355e-05 | 0.026503 | 0.026504 | 0.026504 | 0.99561 | -0.084363 | 0.99453 | -0.10512 | 7.2812
4 | 0.052223 | 0.013135 | -0.052198 | -0.013119 | 2.4839e-05 | 1.5756e-05 | 0.078067 | 0.078067 | 0.078067 | 0.99561 | -0.084363 | 0.99509 | -0.094326 | 21.4471
5 | 0.013392 | 0.0033572 | -0.01339 | -0.0033565 | 1.3099e-06 | 7.2496e-07 | 0.020015 | 0.020015 | 0.020015 | 0.99561 | -0.084363 | 0.9955 | -0.086416 | 5.4987
6 | 0.11752 | 0.029652 | -0.11732 | -0.029525 | 0.00019877 | 0.00012699 | 0.17547 | 0.17547 | 0.17547 | 0.99702 | -0.057159 | 0.99517 | -0.092546 | 48.205
7 | 0.07409 | 0.018616 | -0.073969 | -0.018538 | 0.00012139 | 7.7345e-05 | 0.11059 | 0.11059 | 0.11059 | 0.99702 | -0.057159 | 0.99523 | -0.091546 | 30.3829
8 | 0.0095048 | 0.0023834 | -0.0095004 | -0.0023813 | 4.4316e-06 | 2.0708e-06 | 0.014186 | 0.014186 | 0.014186 | 0.99702 | -0.057159 | 0.99651 | -0.066946 | 3.8974
9 | 0.015059 | 0.0037772 | -0.015051 | -0.0037727 | 7.8668e-06 | 4.4977e-06 | 0.02252 | 0.02252 | 0.02252 | 0.99509 | -0.094326 | 0.99452 | -0.10529 | 6.1867
10 | 0.037139 | 0.0093416 | -0.03712 | -0.0093297 | 1.8988e-05 | 1.1939e-05 | 0.055548 | 0.055548 | 0.055548 | 0.99509 | -0.094326 | 0.99453 | -0.10503 | 15.2604
11 | 0.01339 | 0.0033565 | -0.013389 | -0.0033556 | 1.4987e-06 | 8.2946e-07 | 0.020015 | 0.020015 | 0.020015 | 0.9955 | -0.086416 | 0.99538 | -0.088766 | 5.4987
12 | 0.0095004 | 0.0023813 | -0.0094991 | -0.0023807 | 1.355e-06 | 6.3335e-07 | 0.014186 | 0.014186 | 0.014186 | 0.99651 | -0.066946 | 0.99635 | -0.06994 | 3.8974
13 | 0.082529 | 0.020802 | -0.082414 | -0.020729 | 0.00011498 | 7.3324e-05 | 0.12344 | 0.12344 | 0.12344 | 0.99517 | -0.092546 | 0.99366 | -0.12171 | 33.9127
14 | 0.034792 | 0.0087235 | -0.034783 | -0.0087173 | 9.8225e-06 | 6.1607e-06 | 0.052024 | 0.052024 | 0.052024 | 0.99517 | -0.092546 | 0.99487 | -0.098472 | 14.2923
15 | 0.044728 | 0.011269 | -0.044635 | -0.01121 | 9.3588e-05 | 5.9178e-05 | 0.067002 | 0.067003 | 0.067003 | 0.99366 | -0.12171 | 0.99139 | -0.16555 | 18.4073
16 | 0.037686 | 0.0094596 | -0.037663 | -0.0094451 | 2.3157e-05 | 1.457e-05 | 0.05644 | 0.05644 | 0.05644 | 0.99366 | -0.12171 | 0.99299 | -0.1346 | 15.5055
17 | 0.015051 | 0.0037727 | -0.015049 | -0.0037717 | 1.8359e-06 | 1.0497e-06 | 0.02252 | 0.02252 | 0.02252 | 0.99452 | -0.10529 | 0.99439 | -0.10785 | 6.1868
18 | 0.031097 | 0.0078202 | -0.031079 | -0.0078092 | 1.7483e-05 | 1.091e-05 | 0.046536 | 0.046536 | 0.046536 | 0.99453 | -0.10503 | 0.99392 | -0.11681 | 12.7847
19 | 0.0066552 | 0.001668 | -0.0066539 | -0.0016676 | 1.2925e-06 | 3.7468e-07 | 0.009949 | 0.0099492 | 0.0099492 | 0.99538 | -0.088766 | 0.99517 | -0.092843 | 2.7333
20 | 0.044635 | 0.01121 | -0.044616 | -0.011198 | 1.8725e-05 | 1.1841e-05 | 0.067003 | 0.067003 | 0.067003 | 0.99139 | -0.16555 | 0.99094 | -0.17435 | 18.4073
21 | 0.026999 | 0.0067725 | -0.026988 | -0.0067654 | 1.146e-05 | 7.0932e-06 | 0.040461 | 0.040461 | 0.040461 | 0.99299 | -0.1346 | 0.99253 | -0.14351 | 11.1155
22 | 0.0072714 | 0.0018224 | -0.0072713 | -0.0018224 | 1.2892e-07 | 4.4913e-08 | 0.010886 | 0.010886 | 0.010886 | 0.99392 | -0.11681 | 0.9939 | -0.11718 | 2.9907
23 | 0.023808 | 0.0059868 | -0.023757 | -0.005956 | 5.0335e-05 | 3.0849e-05 | 0.03565 | 0.03565 | 0.03565 | 0.99392 | -0.11681 | 0.99163 | -0.16118 | 9.7941
24 | 0.0091318 | 0.0022893 | -0.0091285 | -0.0022878 | 3.2836e-06 | 1.5002e-06 | 0.013703 | 0.013703 | 0.013703 | 0.99163 | -0.16118 | 0.99124 | -0.16872 | 3.7647
25 | 0.014626 | 0.0036667 | -0.014622 | -0.0036648 | 3.283e-06 | 1.8667e-06 | 0.021947 | 0.021947 | 0.021947 | 0.99163 | -0.16118 | 0.99139 | -0.16589 | 6.0295
26 | 0.0094041 | 0.002357 | -0.0094024 | -0.0023562 | 1.7988e-06 | 8.4088e-07 | 0.014115 | 0.014115 | 0.014115 | 0.99139 | -0.16589 | 0.99118 | -0.1699 | 3.8778
27 | -0.014916 | -0.0037384 | 0.014919 | 0.00374 | 2.8506e-06 | 1.6301e-06 | 0.022426 | 0.022426 | 0.022426 | 0.98975 | -0.19744 | 0.98995 | -0.19343 | 6.1609
28 | -0.03178 | -0.0079688 | 0.031792 | 0.0079762 | 1.1958e-05 | 7.4736e-06 | 0.04777 | 0.04777 | 0.04777 | 0.98995 | -0.19343 | 0.99036 | -0.18553 | 13.1238
29 | 0.016861 | 0.0042287 | -0.016852 | -0.0042237 | 8.5771e-06 | 5.0318e-06 | 0.025345 | 0.025345 | 0.025345 | 0.98995 | -0.19343 | 0.9894 | -0.2041 | 6.9629
30 | -0.038025 | -0.0095384 | 0.038045 | 0.0095512 | 2.0288e-05 | 1.2771e-05 | 0.057136 | 0.057136 | 0.057136 | 0.99036 | -0.18553 | 0.99094 | -0.17435 | 15.6966
31 | 0.0078923 | 0.0019781 | -0.0078913 | -0.0019777 | 1.0122e-06 | 4.0179e-07 | 0.01187 | 0.01187 | 0.01187 | 0.9894 | -0.2041 | 0.98926 | -0.2068 | 3.2609
32 | 0.017799 | 0.0044625 | -0.017794 | -0.0044599 | 4.4219e-06 | 2.6161e-06 | 0.026685 | 0.026685 | 0.026685 | 0.99253 | -0.14351 | 0.99226 | -0.14872 | 7.331
33 | 0.0085374 | 0.0021399 | -0.0085364 | -0.0021394 | 1.0306e-06 | 4.4303e-07 | 0.012803 | 0.012803 | 0.012803 | 0.99226 | -0.14872 | 0.99213 | -0.15126 | 3.5173
34 | 0.0021525 | 0.00053918 | -0.0021524 | -0.00053944 | 9.7971e-08 | -2.5976e-07 | 0.0032313 | 0.0032314 | 0.0032314 | 0.99118 | -0.1699 | 0.99113 | -0.17086 | 0.88776

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37044 | 0.093117

## res_load
| p_mw | q_mvar
0 | 0.083323 | 0.020883
1 | 0.017714 | 0.0044395
2 | 0.0094991 | 0.0023807
3 | 0.073969 | 0.018538
4 | 0.034783 | 0.0087173
5 | 0.0060231 | 0.0015095
6 | 0.0067337 | 0.0016876
7 | 0.010664 | 0.0026726
8 | 0.015049 | 0.0037717
9 | 0.0091285 | 0.0022878
10 | 0.0052182 | 0.0013078
11 | 0.0072713 | 0.0018224
12 | 0.0066539 | 0.0016676
13 | 0.014916 | 0.0037384
14 | 0.0062331 | 0.0015622
15 | 0.0089599 | 0.0022456
16 | 0.0065709 | 0.0016468
17 | 0.0078913 | 0.0019777
18 | 0.0091887 | 0.0023029
19 | 0.009257 | 0.00232
20 | 0.0085364 | 0.0021394
21 | 0.0072499 | 0.001817
22 | 0.0021524 | 0.00053944

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1