## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-866_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-866_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-866_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-866_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-866_0_4_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_261-866_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-866_0_4_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_261-866_0_4_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_261-866_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_261-866_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_261-866_0_4_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_261-866_0_4_node_48 | 0.4 | n |  | TRUE
12 | bus_LV_261-866_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_261-866_0_4_node_50 | 0.4 | n |  | TRUE
14 | bus_LV_261-866_0_4_node_33 | 0.4 | n |  | TRUE
15 | bus_LV_261-866_0_4_node_46 | 0.4 | n |  | TRUE
16 | bus_LV_261-866_0_4_node_55 | 0.4 | n |  | TRUE
17 | bus_LV_261-866_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_261-866_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_261-866_0_4_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_261-866_0_4_node_47 | 0.4 | n |  | TRUE
21 | bus_LV_261-866_0_4_node_44 | 0.4 | n |  | TRUE
22 | bus_LV_261-866_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_261-866_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_261-866_0_4_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_261-866_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_261-866_0_4_node_38 | 0.4 | n |  | TRUE
27 | bus_LV_261-866_0_4_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_261-866_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_261-866_0_4_node_39 | 0.4 | n |  | TRUE
30 | bus_LV_261-866_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_261-866_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_261-866_0_4_node_52 | 0.4 | n |  | TRUE
33 | bus_LV_261-866_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_261-866_0_4_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_261-866_0_4_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_261-866_0_4_node_54 | 0.4 | n |  | TRUE
37 | bus_LV_261-866_0_4_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_261-866_0_4_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_261-866_0_4_node_49 | 0.4 | n |  | TRUE
40 | bus_LV_261-866_0_4_node_51 | 0.4 | n |  | TRUE
41 | bus_LV_261-866_0_4_node_45 | 0.4 | n |  | TRUE
42 | bus_LV_261-866_0_4_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_261-866_0_4_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_261-866_0_4_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_261-866_0_4_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_261-866_0_4_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_261-866_0_4_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_261-866_0_4_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_261-866_0_4_node_28 | 0.4 | n |  | TRUE
50 | bus_MV_546_0_node_25 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-866_0_4_load_0 | 0 | 0.021182 | 0.0053087 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-866_0_4_load_25 | 6 | 0.021153 | 0.0053014 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-866_0_4_load_23 | 7 | 0.010278 | 0.0025759 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-866_0_4_load_32 | 10 | 0.032501 | 0.0081456 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-866_0_4_load_48 | 11 | 0.017337 | 0.004345 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-866_0_4_load_50 | 13 | 0.017947 | 0.0044978 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-866_0_4_load_33 | 14 | 0.022944 | 0.0057504 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-866_0_4_load_46 | 15 | 0.0088476 | 0.0022174 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-866_0_4_load_55 | 16 | 0.0097502 | 0.0024436 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-866_0_4_load_24 | 19 | 0.020195 | 0.0050613 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-866_0_4_load_47 | 20 | 0.023398 | 0.005864 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-866_0_4_load_44 | 21 | 0.0088246 | 0.0022117 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-866_0_4_load_26 | 24 | 0.015153 | 0.0037977 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-866_0_4_load_38 | 26 | 0.022515 | 0.0056428 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-866_0_4_load_36 | 27 | 0.013083 | 0.0032789 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-866_0_4_load_39 | 29 | 0.012901 | 0.0032333 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-866_0_4_load_52 | 32 | 0.021308 | 0.0053403 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-866_0_4_load_34 | 35 | 0.0073231 | 0.0018353 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-866_0_4_load_54 | 36 | 0.014044 | 0.0035198 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-866_0_4_load_31 | 38 | 0.0090022 | 0.0022562 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-866_0_4_load_49 | 39 | 0.0046517 | 0.0011658 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-866_0_4_load_51 | 40 | 0.0095062 | 0.0023825 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-866_0_4_load_45 | 41 | 0.023311 | 0.0058424 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-866_0_4_load_42 | 45 | 0.054356 | 0.013623 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-866_0_4_load_37 | 47 | 0.022391 | 0.0056116 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-866_0_4_load_27 | 48 | 0.01382 | 0.0034637 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-866_0_4_load_28 | 49 | 0.013763 | 0.0034493 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-866_0_4_line_0 |  | 0 | 1 | 0.030677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-866_0_4_line_1 |  | 0 | 2 | 0.031687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-866_0_4_line_2 |  | 1 | 3 | 0.036003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-866_0_4_line_3 |  | 2 | 4 | 0.013656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-866_0_4_line_4 |  | 2 | 5 | 0.034548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-866_0_4_line_5 |  | 3 | 6 | 0.030777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-866_0_4_line_6 |  | 4 | 14 | 0.0079268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_261-866_0_4_line_7 |  | 4 | 15 | 0.008618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_261-866_0_4_line_8 |  | 5 | 7 | 0.031467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-866_0_4_line_9 |  | 8 | 9 | 0.023915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-866_0_4_line_10 |  | 8 | 10 | 0.03292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-866_0_4_line_11 |  | 8 | 11 | 0.021646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-866_0_4_line_12 |  | 9 | 12 | 0.049682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-866_0_4_line_13 |  | 9 | 13 | 0.049597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-866_0_4_line_14 |  | 10 | 38 | 0.016708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-866_0_4_line_15 |  | 11 | 39 | 0.0059167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-866_0_4_line_16 |  | 12 | 16 | 0.014466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-866_0_4_line_17 |  | 13 | 40 | 0.045528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-866_0_4_line_18 |  | 14 | 38 | 0.016671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-866_0_4_line_19 |  | 15 | 41 | 0.016625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_261-866_0_4_line_20 |  | 17 | 18 | 0.012653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-866_0_4_line_21 |  | 17 | 19 | 0.031663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-866_0_4_line_22 |  | 18 | 20 | 0.032554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_261-866_0_4_line_23 |  | 18 | 21 | 0.035445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_261-866_0_4_line_24 |  | 20 | 28 | 0.048827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_261-866_0_4_line_25 |  | 21 | 41 | 0.016665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_261-866_0_4_line_26 |  | 22 | 23 | 0.07725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-866_0_4_line_27 |  | 22 | 24 | 0.0016503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-866_0_4_line_28 |  | 23 | 28 | 0.032371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_261-866_0_4_line_29 |  | 23 | 29 | 0.031964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_261-866_0_4_line_30 |  | 25 | 26 | 0.0043214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-866_0_4_line_31 |  | 25 | 27 | 0.014522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-866_0_4_line_32 |  | 27 | 42 | 0.0048171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-866_0_4_line_33 |  | 29 | 43 | 0.0053734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_261-866_0_4_line_34 |  | 30 | 31 | 0.079127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-866_0_4_line_35 |  | 30 | 32 | 0.082084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-866_0_4_line_36 |  | 31 | 36 | 0.008581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-866_0_4_line_37 |  | 31 | 37 | 0.009168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-866_0_4_line_38 |  | 33 | 34 | 0.044434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-866_0_4_line_39 |  | 33 | 35 | 0.023469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-866_0_4_line_40 |  | 34 | 45 | 0.028191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-866_0_4_line_41 |  | 34 | 49 | 0.027568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-866_0_4_line_42 |  | 35 | 37 | 0.01599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-866_0_4_line_43 |  | 42 | 47 | 0.018803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-866_0_4_line_44 |  | 43 | 46 | 0.015164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_261-866_0_4_line_45 |  | 44 | 45 | 0.014703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_261-866_0_4_line_46 |  | 44 | 46 | 0.031273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_261-866_0_4_line_47 |  | 46 | 47 | 0.0014482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-866_0_4_line_48 |  | 48 | 49 | 0.024136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-866_0_4_trafo_42 | 0.63 MVA 20/0.4 kV | 50 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2684641.1442 | 1251650.065 | 2684640.6495 | 1251663.0233 | 2684641.3053 | 1251664.1446 | 2684640.5739 | 1251680.5389
1 | 2684639.1617 | 1251712.1945 | 2684640.5739 | 1251680.5389
2 | 2684677.1855 | 1251652.2927 | 2684641.1442 | 1251650.065
3 | 2684639.1617 | 1251712.1945 | 2684639.8634 | 1251712.2157 | 2684639.6833 | 1251717.9507 | 2684639.5726 | 1251725.1657
4 | 2684639.1617 | 1251712.1945 | 2684621.5044 | 1251711.2861 | 2684604.6626 | 1251710.3561
5 | 2684677.1855 | 1251652.2927 | 2684680.6001 | 1251658.435 | 2684680.2003 | 1251663.1661 | 2684679.2795 | 1251682.1447
6 | 2684639.5726 | 1251725.1657 | 2684631.6513 | 1251724.872
7 | 2684639.5726 | 1251725.1657 | 2684648.1857 | 1251725.4573
8 | 2684604.6626 | 1251710.3561 | 2684605.4544 | 1251678.8987
9 | 2684542.9948 | 1251725.0982 | 2684546.0851 | 1251721.7064 | 2684565.3983 | 1251722.4158
10 | 2684565.3983 | 1251722.4158 | 2684598.2957 | 1251723.6354
11 | 2684565.3983 | 1251722.4158 | 2684564.421 | 1251744.0399
12 | 2684540.2478 | 1251680.6479 | 2684539.9838 | 1251687.5048 | 2684539.3753 | 1251703.1634 | 2684539.2711 | 1251705.1746 | 2684538.8155 | 1251714.3527 | 2684538.2485 | 1251725.5197 | 2684542.9948 | 1251725.0982
13 | 2684542.9948 | 1251725.0982 | 2684542.664 | 1251730.82 | 2684540.8165 | 1251774.6467
14 | 2684598.2957 | 1251723.6354 | 2684614.9922 | 1251724.2544
15 | 2684564.421 | 1251744.0399 | 2684564.1539 | 1251749.9506
16 | 2684540.2478 | 1251680.6479 | 2684552.8972 | 1251678.6268 | 2684554.5952 | 1251678.651
17 | 2684540.8165 | 1251774.6467 | 2684540.0275 | 1251793.3627 | 2684541.3227 | 1251795.1604 | 2684543.3752 | 1251796.7909 | 2684546.6819 | 1251797.2717 | 2684565.2829 | 1251798.0316
18 | 2684631.6513 | 1251724.872 | 2684614.9922 | 1251724.2544
19 | 2684648.1857 | 1251725.4573 | 2684664.801 | 1251726.0199
20 | 2684716.8813 | 1251727.7834 | 2684717.1803 | 1251721.1271 | 2684717.9748 | 1251715.1896
21 | 2684717.9748 | 1251715.1896 | 2684718.0975 | 1251713.4678 | 2684718.4724 | 1251708.3693 | 2684719.8882 | 1251683.5849
22 | 2684716.8813 | 1251727.7834 | 2684714.8445 | 1251760.2739
23 | 2684716.8813 | 1251727.7834 | 2684681.4562 | 1251726.5839
24 | 2684713.3139 | 1251808.8378 | 2684712.0696 | 1251804.539 | 2684714.8445 | 1251760.2739
25 | 2684681.4562 | 1251726.5839 | 2684664.801 | 1251726.0199
26 | 2684710.7313 | 1251841.1029 | 2684707.7121 | 1251883.8475 | 2684706.8811 | 1251889.1729 | 2684705.6287 | 1251918.1546
27 | 2684705.6287 | 1251918.1546 | 2684705.5574 | 1251919.8034
28 | 2684713.3139 | 1251808.8378 | 2684710.7313 | 1251841.1029
29 | 2684710.7313 | 1251841.1029 | 2684678.8575 | 1251838.7052
30 | 2684671.8776 | 1251863.0308 | 2684672.1604 | 1251858.7186
31 | 2684671.8776 | 1251863.0308 | 2684657.3612 | 1251862.612
32 | 2684657.5961 | 1251857.8006 | 2684657.3612 | 1251862.612
33 | 2684673.4992 | 1251838.3021 | 2684678.8575 | 1251838.7052
34 | 2684532.819 | 1251889.0763 | 2684531.6566 | 1251882.7327 | 2684530.2838 | 1251875.2631 | 2684531.7125 | 1251873.5266 | 2684532.6421 | 1251871.3271 | 2684533.0221 | 1251866.3844 | 2684533.9881 | 1251839.4334 | 2684562.4012 | 1251841.9073
35 | 2684532.819 | 1251889.0763 | 2684559.1211 | 1251897.1799 | 2684558.8556 | 1251912.5988 | 2684597.9634 | 1251914.1998
36 | 2684562.4012 | 1251841.9073 | 2684561.9166 | 1251850.4735
37 | 2684562.4012 | 1251841.9073 | 2684571.5895 | 1251842.2721
38 | 2684572.3869 | 1251802.8205 | 2684616.9305 | 1251804.2351
39 | 2684572.3869 | 1251802.8205 | 2684571.9126 | 1251826.285
40 | 2684616.9305 | 1251804.2351 | 2684645.0878 | 1251805.6095
41 | 2684616.9305 | 1251804.2351 | 2684615.2029 | 1251831.7485
42 | 2684571.5895 | 1251842.2721 | 2684571.9126 | 1251826.285
43 | 2684657.5961 | 1251857.8006 | 2684658.2572 | 1251839.0096
44 | 2684658.3081 | 1251837.5623 | 2684673.4992 | 1251838.3021
45 | 2684659.7736 | 1251806.3264 | 2684645.0878 | 1251805.6095
46 | 2684659.7736 | 1251806.3264 | 2684658.3081 | 1251837.5623
47 | 2684658.3081 | 1251837.5623 | 2684658.2572 | 1251839.0096
48 | 2684615.2029 | 1251831.7485 | 2684614.6439 | 1251840.6521 | 2684618.0574 | 1251841.0567 | 2684617.7125 | 1251852.8287

## bus_geodata
| x | y | coords
0 | 2684640.5739 | 1251680.5389
1 | 2684641.1442 | 1251650.065
2 | 2684639.1617 | 1251712.1945
3 | 2684677.1855 | 1251652.2927
4 | 2684639.5726 | 1251725.1657
5 | 2684604.6626 | 1251710.3561
6 | 2684679.2795 | 1251682.1447
7 | 2684605.4544 | 1251678.8987
8 | 2684565.3983 | 1251722.4158
9 | 2684542.9948 | 1251725.0982
10 | 2684598.2957 | 1251723.6354
11 | 2684564.421 | 1251744.0399
12 | 2684540.2478 | 1251680.6479
13 | 2684540.8165 | 1251774.6467
14 | 2684631.6513 | 1251724.872
15 | 2684648.1857 | 1251725.4573
16 | 2684554.5952 | 1251678.651
17 | 2684717.9748 | 1251715.1896
18 | 2684716.8813 | 1251727.7834
19 | 2684719.8882 | 1251683.5849
20 | 2684714.8445 | 1251760.2739
21 | 2684681.4562 | 1251726.5839
22 | 2684705.6287 | 1251918.1546
23 | 2684710.7313 | 1251841.1029
24 | 2684705.5574 | 1251919.8034
25 | 2684671.8776 | 1251863.0308
26 | 2684672.1604 | 1251858.7186
27 | 2684657.3612 | 1251862.612
28 | 2684713.3139 | 1251808.8378
29 | 2684678.8575 | 1251838.7052
30 | 2684532.819 | 1251889.0763
31 | 2684562.4012 | 1251841.9073
32 | 2684597.9634 | 1251914.1998
33 | 2684572.3869 | 1251802.8205
34 | 2684616.9305 | 1251804.2351
35 | 2684571.9126 | 1251826.285
36 | 2684561.9166 | 1251850.4735
37 | 2684571.5895 | 1251842.2721
38 | 2684614.9922 | 1251724.2544
39 | 2684564.1539 | 1251749.9506
40 | 2684565.2829 | 1251798.0316
41 | 2684664.801 | 1251726.0199
42 | 2684657.5961 | 1251857.8006
43 | 2684673.4992 | 1251838.3021
44 | 2684659.7736 | 1251806.3264
45 | 2684645.0878 | 1251805.6095
46 | 2684658.3081 | 1251837.5623
47 | 2684658.2572 | 1251839.0096
48 | 2684617.7125 | 1251852.8287
49 | 2684615.2029 | 1251831.7485
50 | 2684659.7736 | 1251806.3264

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97473 | -0.48618 | 0.021182 | 0.0053087
1 | 0.97412 | -0.4981 | 0 | 0
2 | 0.97598 | -0.4616 | 0 | 0
3 | 0.97341 | -0.51209 | 0 | 0
4 | 0.97664 | -0.44846 | 0 | 0
5 | 0.97565 | -0.4681 | 0 | 0
6 | 0.97281 | -0.52408 | 0.021153 | 0.0053014
7 | 0.97534 | -0.47403 | 0.010278 | 0.0025759
8 | 0.97303 | -0.51964 | 0 | 0
9 | 0.97219 | -0.53604 | 0 | 0
10 | 0.97484 | -0.48383 | 0.032501 | 0.0081456
11 | 0.97258 | -0.52841 | 0.017337 | 0.004345
12 | 0.97174 | -0.54498 | 0 | 0
13 | 0.97092 | -0.56118 | 0.017947 | 0.0044978
14 | 0.97634 | -0.45443 | 0.022944 | 0.0057504
15 | 0.97712 | -0.43921 | 0.0088476 | 0.0022174
16 | 0.97161 | -0.54758 | 0.0097502 | 0.0024436
17 | 0.9813 | -0.35751 | 0 | 0
18 | 0.98154 | -0.35288 | 0 | 0
19 | 0.98071 | -0.36909 | 0.020195 | 0.0050613
20 | 0.98394 | -0.30638 | 0.023398 | 0.005864
21 | 0.97915 | -0.39943 | 0.0088246 | 0.0022117
22 | 0.98943 | -0.20093 | 0 | 0
23 | 0.9905 | -0.18011 | 0 | 0
24 | 0.98941 | -0.20137 | 0.015153 | 0.0037977
25 | 0.99393 | -0.11519 | 0 | 0
26 | 0.99384 | -0.1169 | 0.022515 | 0.0056428
27 | 0.99423 | -0.10942 | 0.013083 | 0.0032789
28 | 0.98788 | -0.23025 | 0 | 0
29 | 0.99324 | -0.12801 | 0.012901 | 0.0032333
30 | 0.99319 | -0.13083 | 0 | 0
31 | 0.99474 | -0.10108 | 0 | 0
32 | 0.9916 | -0.16179 | 0.021308 | 0.0053403
33 | 0.99646 | -0.067823 | 0 | 0
34 | 0.99819 | -0.034589 | 0 | 0
35 | 0.99555 | -0.085423 | 0.0073231 | 0.0018353
36 | 0.99463 | -0.1032 | 0.014044 | 0.0035198
37 | 0.99503 | -0.095371 | 0 | 0
38 | 0.97556 | -0.4698 | 0.0090022 | 0.0022562
39 | 0.97256 | -0.52892 | 0.0046517 | 0.0011658
40 | 0.97052 | -0.56919 | 0.0095062 | 0.0023825
41 | 0.97807 | -0.42051 | 0.023311 | 0.0058424
42 | 0.99439 | -0.1064 | 0 | 0
43 | 0.99372 | -0.11887 | 0 | 0
44 | 0.99842 | -0.029682 | 0 | 0
45 | 1 | 0 | -0.42554 | -0.10884
46 | 0.99507 | -0.093126 | 0 | 0
47 | 0.995 | -0.094604 | 0.022391 | 0.0056116
48 | 0.9972 | -0.053745 | 0.01382 | 0.0034637
49 | 0.9975 | -0.047901 | 0.013763 | 0.0034493
50 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.021191 | 0.0053247 | -0.021179 | -0.0053173 | 1.2043e-05 | 7.3254e-06 | 0.032355 | 0.032355 | 0.032355 | 0.97473 | -0.48618 | 0.97412 | -0.4981 | 8.8888
1 | -0.042373 | -0.010633 | 0.042423 | 0.010665 | 4.9729e-05 | 3.1431e-05 | 0.064692 | 0.064692 | 0.064692 | 0.97473 | -0.48618 | 0.97598 | -0.4616 | 17.7725
2 | 0.021179 | 0.0053173 | -0.021165 | -0.0053087 | 1.4134e-05 | 8.5979e-06 | 0.032355 | 0.032356 | 0.032356 | 0.97412 | -0.4981 | 0.97341 | -0.51209 | 8.8889
3 | -0.052707 | -0.013244 | 0.05274 | 0.013265 | 3.3079e-05 | 2.1e-05 | 0.080371 | 0.080371 | 0.080371 | 0.97598 | -0.4616 | 0.97664 | -0.44846 | 22.0801
4 | 0.010284 | 0.0025789 | -0.010281 | -0.0025773 | 3.1853e-06 | 1.607e-06 | 0.01568 | 0.01568 | 0.01568 | 0.97598 | -0.4616 | 0.97565 | -0.4681 | 4.3077
5 | 0.021165 | 0.0053087 | -0.021153 | -0.0053014 | 1.2082e-05 | 7.3503e-06 | 0.032356 | 0.032356 | 0.032356 | 0.97341 | -0.51209 | 0.97281 | -0.52408 | 8.8889
6 | 0.12399 | 0.031209 | -0.12396 | -0.031186 | 3.538e-05 | 2.2346e-05 | 0.18896 | 0.18896 | 0.18896 | 0.97664 | -0.44846 | 0.97634 | -0.45443 | 17.3043
7 | -0.17673 | -0.044474 | 0.17681 | 0.044523 | 7.8145e-05 | 4.9689e-05 | 0.26933 | 0.26933 | 0.26933 | 0.97664 | -0.44846 | 0.97712 | -0.43921 | 24.6643
8 | 0.010281 | 0.0025773 | -0.010278 | -0.0025759 | 2.9013e-06 | 1.464e-06 | 0.01568 | 0.01568 | 0.01568 | 0.97565 | -0.4681 | 0.97534 | -0.47403 | 4.3077
9 | 0.037274 | 0.0093672 | -0.037245 | -0.0093488 | 2.9149e-05 | 1.8358e-05 | 0.057011 | 0.057011 | 0.057011 | 0.97303 | -0.51964 | 0.97219 | -0.53604 | 15.6625
10 | -0.059272 | -0.014884 | 0.059373 | 0.014948 | 0.00010145 | 6.4519e-05 | 0.090653 | 0.090653 | 0.090653 | 0.97303 | -0.51964 | 0.97484 | -0.48383 | 24.9047
11 | 0.021998 | 0.0055164 | -0.021989 | -0.0055108 | 9.1869e-06 | 5.6109e-06 | 0.033642 | 0.033642 | 0.033642 | 0.97303 | -0.51964 | 0.97258 | -0.52841 | 9.2423
12 | 0.0097556 | 0.0024463 | -0.0097515 | -0.0024442 | 4.1542e-06 | 2.0429e-06 | 0.014932 | 0.014932 | 0.014932 | 0.97219 | -0.53604 | 0.97174 | -0.54498 | 4.1023
13 | 0.027489 | 0.0069025 | -0.027456 | -0.0068821 | 3.2932e-05 | 2.0463e-05 | 0.042079 | 0.042079 | 0.042079 | 0.97219 | -0.53604 | 0.97092 | -0.56118 | 11.5603
14 | -0.091875 | -0.023094 | 0.091936 | 0.023133 | 6.1633e-05 | 3.9028e-05 | 0.14026 | 0.14026 | 0.14026 | 0.97484 | -0.48383 | 0.97556 | -0.4698 | 19.267
15 | 0.0046518 | 0.0011658 | -0.0046517 | -0.0011658 | 1.1239e-07 | -1.4949e-09 | 0.0071171 | 0.0071171 | 0.0071171 | 0.97258 | -0.52841 | 0.97256 | -0.52892 | 1.9553
16 | 0.0097515 | 0.0024442 | -0.0097502 | -0.0024436 | 1.2096e-06 | 5.9495e-07 | 0.014932 | 0.014932 | 0.014932 | 0.97174 | -0.54498 | 0.97161 | -0.54758 | 4.1023
17 | 0.0095098 | 0.0023842 | -0.0095062 | -0.0023825 | 3.6268e-06 | 1.7583e-06 | 0.014575 | 0.014575 | 0.014575 | 0.97092 | -0.56118 | 0.97052 | -0.56919 | 4.0041
18 | 0.10101 | 0.025436 | -0.10094 | -0.025389 | 7.4124e-05 | 4.7023e-05 | 0.15399 | 0.15399 | 0.15399 | 0.97634 | -0.45443 | 0.97556 | -0.4698 | 21.1531
19 | -0.18566 | -0.046741 | 0.18582 | 0.046846 | 0.00016621 | 0.00010575 | 0.28281 | 0.28281 | 0.28281 | 0.97712 | -0.43921 | 0.97807 | -0.42051 | 25.8982
20 | -0.020206 | -0.005068 | 0.02021 | 0.0050707 | 4.455e-06 | 2.6913e-06 | 0.030641 | 0.030641 | 0.030641 | 0.9813 | -0.35751 | 0.98154 | -0.35288 | 8.4179
21 | 0.020206 | 0.005068 | -0.020195 | -0.0050613 | 1.1148e-05 | 6.7349e-06 | 0.030641 | 0.030641 | 0.030641 | 0.9813 | -0.35751 | 0.98071 | -0.36909 | 8.4179
22 | -0.23887 | -0.060416 | 0.2394 | 0.060757 | 0.00053421 | 0.00034066 | 0.36232 | 0.36232 | 0.36232 | 0.98154 | -0.35288 | 0.98394 | -0.30638 | 33.1799
23 | 0.21866 | 0.055345 | -0.21817 | -0.055035 | 0.00048744 | 0.00031062 | 0.33168 | 0.33168 | 0.33168 | 0.98154 | -0.35288 | 0.97915 | -0.39943 | 30.374
24 | -0.2628 | -0.066621 | 0.26377 | 0.067237 | 0.00096538 | 0.00061598 | 0.39771 | 0.39771 | 0.39771 | 0.98394 | -0.30638 | 0.98788 | -0.23025 | 36.4202
25 | 0.20935 | 0.052823 | -0.20914 | -0.052689 | 0.00021101 | 0.00013442 | 0.31827 | 0.31827 | 0.31827 | 0.97915 | -0.39943 | 0.97807 | -0.42051 | 29.1459
26 | -0.015153 | -0.0037979 | 0.015168 | 0.0038065 | 1.5045e-05 | 8.6354e-06 | 0.022789 | 0.022789 | 0.022789 | 0.98943 | -0.20093 | 0.9905 | -0.18011 | 6.2608
27 | 0.015153 | 0.0037979 | -0.015153 | -0.0037977 | 3.214e-07 | 1.845e-07 | 0.022789 | 0.022789 | 0.022789 | 0.98943 | -0.20093 | 0.98941 | -0.20137 | 6.2608
28 | 0.26441 | 0.067645 | -0.26377 | -0.067237 | 0.00064002 | 0.00040837 | 0.39771 | 0.39771 | 0.39771 | 0.9905 | -0.18011 | 0.98788 | -0.23025 | 36.4201
29 | -0.27957 | -0.071452 | 0.28028 | 0.071903 | 0.00070647 | 0.0004509 | 0.4205 | 0.4205 | 0.4205 | 0.9905 | -0.18011 | 0.99324 | -0.12801 | 38.5069
30 | 0.022517 | 0.0056439 | -0.022515 | -0.0056428 | 1.8416e-06 | 1.1226e-06 | 0.03371 | 0.03371 | 0.03371 | 0.99393 | -0.11519 | 0.99384 | -0.1169 | 9.2611
31 | -0.022517 | -0.0056439 | 0.022523 | 0.0056477 | 6.1886e-06 | 3.7724e-06 | 0.03371 | 0.03371 | 0.03371 | 0.99393 | -0.11519 | 0.99423 | -0.10942 | 9.2611
32 | -0.035606 | -0.0089266 | 0.035611 | 0.0089298 | 5.13e-06 | 3.2207e-06 | 0.053291 | 0.053291 | 0.053291 | 0.99423 | -0.10942 | 0.99439 | -0.1064 | 14.6403
33 | -0.29318 | -0.075136 | 0.29331 | 0.075219 | 0.00012993 | 8.2948e-05 | 0.43982 | 0.43982 | 0.43982 | 0.99324 | -0.12801 | 0.99372 | -0.11887 | 40.2768
34 | -0.02134 | -0.0053594 | 0.02137 | 0.0053778 | 3.0337e-05 | 1.839e-05 | 0.031975 | 0.031975 | 0.031975 | 0.99319 | -0.13083 | 0.99474 | -0.10108 | 8.7844
35 | 0.02134 | 0.0053594 | -0.021308 | -0.0053403 | 3.1472e-05 | 1.9081e-05 | 0.031975 | 0.031976 | 0.031976 | 0.99319 | -0.13083 | 0.9916 | -0.16179 | 8.7845
36 | 0.014045 | 0.0035206 | -0.014044 | -0.0035198 | 1.4205e-06 | 7.9776e-07 | 0.021011 | 0.021011 | 0.021011 | 0.99474 | -0.10108 | 0.99463 | -0.1032 | 5.7722
37 | -0.035415 | -0.0088984 | 0.035425 | 0.0089044 | 9.6521e-06 | 6.0583e-06 | 0.052986 | 0.052985 | 0.052986 | 0.99474 | -0.10108 | 0.99503 | -0.095371 | 14.5565
38 | -0.042801 | -0.010773 | 0.042869 | 0.010816 | 6.8103e-05 | 4.3006e-05 | 0.063931 | 0.063931 | 0.063931 | 0.99646 | -0.067823 | 0.99819 | -0.034589 | 17.5634
39 | 0.042801 | 0.010773 | -0.042765 | -0.01075 | 3.5971e-05 | 2.2716e-05 | 0.063931 | 0.063931 | 0.063931 | 0.99646 | -0.067823 | 0.99555 | -0.085423 | 17.5635
40 | -0.070474 | -0.017742 | 0.070591 | 0.017816 | 0.00011674 | 7.4343e-05 | 0.10508 | 0.10508 | 0.10508 | 0.99819 | -0.034589 | 1 | 0 | 28.8692
41 | 0.027605 | 0.006926 | -0.027587 | -0.0069152 | 1.7508e-05 | 1.0845e-05 | 0.041153 | 0.041153 | 0.041153 | 0.99819 | -0.034589 | 0.9975 | -0.047901 | 11.3059
42 | 0.035442 | 0.008915 | -0.035425 | -0.0089044 | 1.6835e-05 | 1.0566e-05 | 0.052985 | 0.052985 | 0.052985 | 0.99555 | -0.085423 | 0.99503 | -0.095371 | 14.5565
43 | -0.035611 | -0.0089298 | 0.035631 | 0.0089424 | 2.0024e-05 | 1.2571e-05 | 0.053291 | 0.053291 | 0.053291 | 0.99439 | -0.1064 | 0.995 | -0.094604 | 14.6403
44 | -0.29331 | -0.075219 | 0.29368 | 0.075453 | 0.00036667 | 0.00023408 | 0.43982 | 0.43982 | 0.43982 | 0.99372 | -0.11887 | 0.99507 | -0.093126 | 40.2768
45 | -0.35279 | -0.090702 | 0.3533 | 0.091028 | 0.00050966 | 0.00032561 | 0.5266 | 0.5266 | 0.5266 | 0.99842 | -0.029682 | 1 | 0 | 48.2231
46 | 0.35279 | 0.090702 | -0.3517 | -0.090009 | 0.001084 | 0.00069255 | 0.5266 | 0.5266 | 0.5266 | 0.99842 | -0.029682 | 0.99507 | -0.093126 | 48.2232
47 | 0.058026 | 0.014557 | -0.058022 | -0.014554 | 4.0893e-06 | 2.5984e-06 | 0.086776 | 0.086776 | 0.086776 | 0.99507 | -0.093126 | 0.995 | -0.094604 | 23.8395
48 | -0.01382 | -0.0034637 | 0.013824 | 0.0034659 | 3.8493e-06 | 2.1486e-06 | 0.020623 | 0.020623 | 0.020623 | 0.9972 | -0.053745 | 0.9975 | -0.047901 | 5.6656

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47989 | 0.12247

## res_load
| p_mw | q_mvar
0 | 0.021182 | 0.0053087
1 | 0.021153 | 0.0053014
2 | 0.010278 | 0.0025759
3 | 0.032501 | 0.0081456
4 | 0.017337 | 0.004345
5 | 0.017947 | 0.0044978
6 | 0.022944 | 0.0057504
7 | 0.0088476 | 0.0022174
8 | 0.0097502 | 0.0024436
9 | 0.020195 | 0.0050613
10 | 0.023398 | 0.005864
11 | 0.0088246 | 0.0022117
12 | 0.015153 | 0.0037977
13 | 0.022515 | 0.0056428
14 | 0.013083 | 0.0032789
15 | 0.012901 | 0.0032333
16 | 0.021308 | 0.0053403
17 | 0.0073231 | 0.0018353
18 | 0.014044 | 0.0035198
19 | 0.0090022 | 0.0022562
20 | 0.0046517 | 0.0011658
21 | 0.0095062 | 0.0023825
22 | 0.023311 | 0.0058424
23 | 0.054356 | 0.013623
24 | 0.022391 | 0.0056116
25 | 0.01382 | 0.0034637
26 | 0.013763 | 0.0034493

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1