## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-885_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-885_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-885_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-885_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-885_0_4_node_14 | 0.4 | n |  | TRUE
5 | bus_LV_261-885_0_4_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_261-885_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_261-885_0_4_node_96 | 0.4 | n |  | TRUE
8 | bus_LV_261-885_0_4_node_88 | 0.4 | n |  | TRUE
9 | bus_LV_261-885_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_261-885_0_4_node_151 | 0.4 | n |  | TRUE
11 | bus_LV_261-885_0_4_node_152 | 0.4 | n |  | TRUE
12 | bus_LV_261-885_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_261-885_0_4_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_261-885_0_4_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_261-885_0_4_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_261-885_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_261-885_0_4_node_140 | 0.4 | n |  | TRUE
18 | bus_LV_261-885_0_4_node_66 | 0.4 | n |  | TRUE
19 | bus_LV_261-885_0_4_node_87 | 0.4 | n |  | TRUE
20 | bus_LV_261-885_0_4_node_38 | 0.4 | n |  | TRUE
21 | bus_LV_261-885_0_4_node_39 | 0.4 | n |  | TRUE
22 | bus_LV_261-885_0_4_node_154 | 0.4 | n |  | TRUE
23 | bus_LV_261-885_0_4_node_150 | 0.4 | n |  | TRUE
24 | bus_LV_261-885_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_261-885_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_261-885_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_261-885_0_4_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_261-885_0_4_node_56 | 0.4 | n |  | TRUE
29 | bus_LV_261-885_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_261-885_0_4_node_57 | 0.4 | n |  | TRUE
31 | bus_LV_261-885_0_4_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_261-885_0_4_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_261-885_0_4_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_261-885_0_4_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_261-885_0_4_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_261-885_0_4_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_261-885_0_4_node_119 | 0.4 | n |  | TRUE
38 | bus_LV_261-885_0_4_node_109 | 0.4 | n |  | TRUE
39 | bus_LV_261-885_0_4_node_120 | 0.4 | n |  | TRUE
40 | bus_LV_261-885_0_4_node_107 | 0.4 | n |  | TRUE
41 | bus_LV_261-885_0_4_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_261-885_0_4_node_69 | 0.4 | n |  | TRUE
43 | bus_LV_261-885_0_4_node_129 | 0.4 | n |  | TRUE
44 | bus_LV_261-885_0_4_node_71 | 0.4 | n |  | TRUE
45 | bus_LV_261-885_0_4_node_67 | 0.4 | n |  | TRUE
46 | bus_LV_261-885_0_4_node_128 | 0.4 | n |  | TRUE
47 | bus_LV_261-885_0_4_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_261-885_0_4_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_261-885_0_4_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_261-885_0_4_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_261-885_0_4_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_261-885_0_4_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_261-885_0_4_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_261-885_0_4_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_261-885_0_4_node_139 | 0.4 | n |  | TRUE
56 | bus_LV_261-885_0_4_node_54 | 0.4 | n |  | TRUE
57 | bus_LV_261-885_0_4_node_122 | 0.4 | n |  | TRUE
58 | bus_LV_261-885_0_4_node_121 | 0.4 | n |  | TRUE
59 | bus_LV_261-885_0_4_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_261-885_0_4_node_113 | 0.4 | n |  | TRUE
61 | bus_LV_261-885_0_4_node_99 | 0.4 | n |  | TRUE
62 | bus_LV_261-885_0_4_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_261-885_0_4_node_158 | 0.4 | n |  | TRUE
64 | bus_LV_261-885_0_4_node_159 | 0.4 | n |  | TRUE
65 | bus_LV_261-885_0_4_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_261-885_0_4_node_42 | 0.4 | n |  | TRUE
67 | bus_LV_261-885_0_4_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_261-885_0_4_node_93 | 0.4 | n |  | TRUE
69 | bus_LV_261-885_0_4_node_141 | 0.4 | n |  | TRUE
70 | bus_LV_261-885_0_4_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_261-885_0_4_node_118 | 0.4 | n |  | TRUE
72 | bus_LV_261-885_0_4_node_44 | 0.4 | n |  | TRUE
73 | bus_LV_261-885_0_4_node_45 | 0.4 | n |  | TRUE
74 | bus_LV_261-885_0_4_node_85 | 0.4 | n |  | TRUE
75 | bus_LV_261-885_0_4_node_132 | 0.4 | n |  | TRUE
76 | bus_LV_261-885_0_4_node_148 | 0.4 | n |  | TRUE
77 | bus_LV_261-885_0_4_node_86 | 0.4 | n |  | TRUE
78 | bus_LV_261-885_0_4_node_41 | 0.4 | n |  | TRUE
79 | bus_LV_261-885_0_4_node_91 | 0.4 | n |  | TRUE
80 | bus_LV_261-885_0_4_node_50 | 0.4 | n |  | TRUE
81 | bus_LV_261-885_0_4_node_92 | 0.4 | n |  | TRUE
82 | bus_LV_261-885_0_4_node_33 | 0.4 | n |  | TRUE
83 | bus_LV_261-885_0_4_node_34 | 0.4 | n |  | TRUE
84 | bus_LV_261-885_0_4_node_36 | 0.4 | n |  | TRUE
85 | bus_LV_261-885_0_4_node_98 | 0.4 | n |  | TRUE
86 | bus_LV_261-885_0_4_node_61 | 0.4 | n |  | TRUE
87 | bus_LV_261-885_0_4_node_40 | 0.4 | n |  | TRUE
88 | bus_LV_261-885_0_4_node_104 | 0.4 | n |  | TRUE
89 | bus_LV_261-885_0_4_node_105 | 0.4 | n |  | TRUE
90 | bus_LV_261-885_0_4_node_77 | 0.4 | n |  | TRUE
91 | bus_LV_261-885_0_4_node_102 | 0.4 | n |  | TRUE
92 | bus_LV_261-885_0_4_node_100 | 0.4 | n |  | TRUE
93 | bus_LV_261-885_0_4_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_261-885_0_4_node_143 | 0.4 | n |  | TRUE
95 | bus_LV_261-885_0_4_node_97 | 0.4 | n |  | TRUE
96 | bus_LV_261-885_0_4_node_111 | 0.4 | n |  | TRUE
97 | bus_LV_261-885_0_4_node_136 | 0.4 | n |  | TRUE
98 | bus_LV_261-885_0_4_node_114 | 0.4 | n |  | TRUE
99 | bus_LV_261-885_0_4_node_64 | 0.4 | n |  | TRUE
100 | bus_LV_261-885_0_4_node_76 | 0.4 | n |  | TRUE
101 | bus_LV_261-885_0_4_node_131 | 0.4 | n |  | TRUE
102 | bus_LV_261-885_0_4_node_74 | 0.4 | n |  | TRUE
103 | bus_LV_261-885_0_4_node_94 | 0.4 | n |  | TRUE
104 | bus_LV_261-885_0_4_node_90 | 0.4 | n |  | TRUE
105 | bus_LV_261-885_0_4_node_142 | 0.4 | n |  | TRUE
106 | bus_LV_261-885_0_4_node_103 | 0.4 | n |  | TRUE
107 | bus_LV_261-885_0_4_node_58 | 0.4 | n |  | TRUE
108 | bus_LV_261-885_0_4_node_59 | 0.4 | n |  | TRUE
109 | bus_LV_261-885_0_4_node_60 | 0.4 | n |  | TRUE
110 | bus_LV_261-885_0_4_node_62 | 0.4 | n |  | TRUE
111 | bus_LV_261-885_0_4_node_117 | 0.4 | n |  | TRUE
112 | bus_LV_261-885_0_4_node_63 | 0.4 | n |  | TRUE
113 | bus_LV_261-885_0_4_node_65 | 0.4 | n |  | TRUE
114 | bus_LV_261-885_0_4_node_138 | 0.4 | n |  | TRUE
115 | bus_LV_261-885_0_4_node_134 | 0.4 | n |  | TRUE
116 | bus_LV_261-885_0_4_node_149 | 0.4 | n |  | TRUE
117 | bus_LV_261-885_0_4_node_133 | 0.4 | n |  | TRUE
118 | bus_LV_261-885_0_4_node_115 | 0.4 | n |  | TRUE
119 | bus_LV_261-885_0_4_node_68 | 0.4 | n |  | TRUE
120 | bus_LV_261-885_0_4_node_70 | 0.4 | n |  | TRUE
121 | bus_LV_261-885_0_4_node_82 | 0.4 | n |  | TRUE
122 | bus_LV_261-885_0_4_node_108 | 0.4 | n |  | TRUE
123 | bus_LV_261-885_0_4_node_84 | 0.4 | n |  | TRUE
124 | bus_LV_261-885_0_4_node_80 | 0.4 | n |  | TRUE
125 | bus_LV_261-885_0_4_node_72 | 0.4 | n |  | TRUE
126 | bus_LV_261-885_0_4_node_73 | 0.4 | n |  | TRUE
127 | bus_LV_261-885_0_4_node_75 | 0.4 | n |  | TRUE
128 | bus_LV_261-885_0_4_node_79 | 0.4 | n |  | TRUE
129 | bus_LV_261-885_0_4_node_126 | 0.4 | n |  | TRUE
130 | bus_LV_261-885_0_4_node_78 | 0.4 | n |  | TRUE
131 | bus_LV_261-885_0_4_node_146 | 0.4 | n |  | TRUE
132 | bus_LV_261-885_0_4_node_144 | 0.4 | n |  | TRUE
133 | bus_LV_261-885_0_4_node_145 | 0.4 | n |  | TRUE
134 | bus_LV_261-885_0_4_node_160 | 0.4 | n |  | TRUE
135 | bus_LV_261-885_0_4_node_124 | 0.4 | n |  | TRUE
136 | bus_LV_261-885_0_4_node_125 | 0.4 | n |  | TRUE
137 | bus_LV_261-885_0_4_node_147 | 0.4 | n |  | TRUE
138 | bus_LV_261-885_0_4_node_157 | 0.4 | n |  | TRUE
139 | bus_LV_261-885_0_4_node_137 | 0.4 | n |  | TRUE
140 | bus_LV_261-885_0_4_node_156 | 0.4 | n |  | TRUE
141 | bus_LV_261-885_0_4_node_81 | 0.4 | n |  | TRUE
142 | bus_LV_261-885_0_4_node_83 | 0.4 | n |  | TRUE
143 | bus_LV_261-885_0_4_node_101 | 0.4 | n |  | TRUE
144 | bus_LV_261-885_0_4_node_89 | 0.4 | n |  | TRUE
145 | bus_LV_261-885_0_4_node_106 | 0.4 | n |  | TRUE
146 | bus_LV_261-885_0_4_node_110 | 0.4 | n |  | TRUE
147 | bus_LV_261-885_0_4_node_135 | 0.4 | n |  | TRUE
148 | bus_LV_261-885_0_4_node_112 | 0.4 | n |  | TRUE
149 | bus_LV_261-885_0_4_node_116 | 0.4 | n |  | TRUE
150 | bus_LV_261-885_0_4_node_123 | 0.4 | n |  | TRUE
151 | bus_LV_261-885_0_4_node_127 | 0.4 | n |  | TRUE
152 | bus_LV_261-885_0_4_node_130 | 0.4 | n |  | TRUE
153 | bus_LV_261-885_0_4_node_155 | 0.4 | n |  | TRUE
154 | bus_LV_261-885_0_4_node_153 | 0.4 | n |  | TRUE
155 | bus_MV_543_0_node_183 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-885_0_4_load_0 | 0 | 0.016721 | 0.0041906 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-885_0_4_load_3 | 3 | 0.014389 | 0.0036062 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-885_0_4_load_14 | 4 | 0.0025556 | 0.00064049 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-885_0_4_load_10 | 5 | 0.0058575 | 0.001468 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-885_0_4_load_88 | 8 | 0.0038396 | 0.0009623 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-885_0_4_load_151 | 10 | 0.0012443 | 0.00031186 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-885_0_4_load_26 | 13 | 0.001637 | 0.00041027 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-885_0_4_load_25 | 14 | 0.0054217 | 0.0013588 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-885_0_4_load_27 | 15 | 0.006968 | 0.0017463 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-885_0_4_load_140 | 17 | 0.033508 | 0.0083978 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-885_0_4_load_87 | 19 | 0.0017972 | 0.00045043 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-885_0_4_load_38 | 20 | 0.0022124 | 0.00055449 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-885_0_4_load_39 | 21 | 0.0017471 | 0.00043786 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-885_0_4_load_154 | 22 | 0.0012812 | 0.0003211 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-885_0_4_load_21 | 24 | 0.0023269 | 0.00058317 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-885_0_4_load_13 | 25 | 0.01173 | 0.0029399 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-885_0_4_load_12 | 26 | 0.0084206 | 0.0021104 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-885_0_4_load_22 | 27 | 0.0016289 | 0.00040825 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-885_0_4_load_23 | 29 | 0.0016198 | 0.00040596 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-885_0_4_load_57 | 30 | 0.0093136 | 0.0023342 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-885_0_4_load_15 | 31 | 0.0059934 | 0.0015021 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-885_0_4_load_18 | 34 | 0.0015925 | 0.00039912 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-885_0_4_load_19 | 35 | 0.0054097 | 0.0013558 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-885_0_4_load_20 | 36 | 0.0017493 | 0.00043842 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-885_0_4_load_119 | 37 | 0.0015945 | 0.00039961 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-885_0_4_load_109 | 38 | 0.0018033 | 0.00045196 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-885_0_4_load_120 | 39 | 0.0018237 | 0.00045706 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-885_0_4_load_107 | 40 | 0.0041966 | 0.0010518 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-885_0_4_load_129 | 43 | 0.0016438 | 0.00041199 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-885_0_4_load_67 | 45 | 0.0016167 | 0.00040519 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-885_0_4_load_128 | 46 | 0.0081829 | 0.0020508 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-885_0_4_load_28 | 47 | 0.0020215 | 0.00050663 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-885_0_4_load_29 | 48 | 0.0056844 | 0.0014246 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-885_0_4_load_30 | 49 | 0.0058963 | 0.0014778 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-885_0_4_load_31 | 50 | 0.0078427 | 0.0019656 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-885_0_4_load_37 | 52 | 0.0058595 | 0.0014685 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-885_0_4_load_35 | 53 | 0.0020727 | 0.00051947 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-885_0_4_load_139 | 55 | 0.0061723 | 0.0015469 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-885_0_4_load_122 | 57 | 0.0050451 | 0.0012644 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-885_0_4_load_121 | 58 | 0.0050514 | 0.001266 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-885_0_4_load_113 | 60 | 0.0081793 | 0.0020499 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-885_0_4_load_99 | 61 | 0.004852 | 0.001216 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-885_0_4_load_158 | 63 | 0.0015018 | 0.0003764 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-885_0_4_load_159 | 64 | 0.0010769 | 0.00026991 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-885_0_4_load_141 | 69 | 0.014685 | 0.0036804 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-885_0_4_load_118 | 71 | 0.010383 | 0.0026022 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-885_0_4_load_132 | 75 | 0.011304 | 0.002833 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-885_0_4_load_148 | 76 | 0.0014665 | 0.00036753 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-885_0_4_load_41 | 78 | 0.0014712 | 0.00036872 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-885_0_4_load_91 | 79 | 0.0061382 | 0.0015384 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-885_0_4_load_33 | 82 | 0.0050563 | 0.0012672 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-885_0_4_load_34 | 83 | 0.0022111 | 0.00055416 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-885_0_4_load_36 | 84 | 0.0019232 | 0.00048199 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-885_0_4_load_61 | 86 | 0.0039076 | 0.00097933 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-885_0_4_load_104 | 88 | 0.00083776 | 0.00020996 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-885_0_4_load_77 | 90 | 0.0076777 | 0.0019242 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-885_0_4_load_102 | 91 | 0.0011977 | 0.00030018 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-885_0_4_load_100 | 92 | 0.0022835 | 0.00057231 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-885_0_4_load_143 | 94 | 0.0078686 | 0.0019721 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-885_0_4_load_111 | 96 | 0.00099616 | 0.00024966 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-885_0_4_load_114 | 98 | 0.0024275 | 0.0006084 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-885_0_4_load_131 | 101 | 0.011312 | 0.0028351 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-885_0_4_load_94 | 103 | 0.0016247 | 0.00040719 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-885_0_4_load_90 | 104 | 0.0011506 | 0.00028837 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-885_0_4_load_142 | 105 | 0.0024924 | 0.00062465 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-885_0_4_load_58 | 107 | 0.010651 | 0.0026694 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-885_0_4_load_59 | 108 | 0.011146 | 0.0027936 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-885_0_4_load_60 | 109 | 0.0022356 | 0.0005603 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-885_0_4_load_62 | 110 | 0.0018717 | 0.00046908 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-885_0_4_load_117 | 111 | 0.0011096 | 0.00027809 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-885_0_4_load_63 | 112 | 0.0021703 | 0.00054393 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-885_0_4_load_134 | 115 | 0.0011693 | 0.00029306 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-885_0_4_load_149 | 116 | 0.0021241 | 0.00053236 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-885_0_4_load_133 | 117 | 0.0011836 | 0.00029663 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-885_0_4_load_115 | 118 | 0.00097913 | 0.00024539 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-885_0_4_load_68 | 119 | 0.0024135 | 0.00060489 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-885_0_4_load_70 | 120 | 0.0032829 | 0.00082276 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-885_0_4_load_108 | 122 | 0.0061382 | 0.0015384 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-885_0_4_load_84 | 123 | 0.0013986 | 0.00035052 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-885_0_4_load_80 | 124 | 0.0013913 | 0.0003487 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-885_0_4_load_72 | 125 | 0.0022744 | 0.00057002 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-885_0_4_load_73 | 126 | 0.0033033 | 0.00082788 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-885_0_4_load_146 | 131 | 0.0043859 | 0.0010992 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-885_0_4_load_144 | 132 | 0.0031289 | 0.00078418 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-885_0_4_load_160 | 134 | 0.002118 | 0.00053083 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-885_0_4_load_125 | 136 | 0.0041795 | 0.0010475 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-885_0_4_load_157 | 138 | 0.0037114 | 0.00093017 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-885_0_4_load_156 | 140 | 0.0031943 | 0.00080056 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-885_0_4_load_81 | 141 | 0.0022477 | 0.00056333 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-885_0_4_load_83 | 142 | 0.0034763 | 0.00087125 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-885_0_4_load_89 | 144 | 0.030023 | 0.0075245 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-885_0_4_load_106 | 145 | 0.0017352 | 0.00043489 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-885_0_4_load_110 | 146 | 0.0011697 | 0.00029316 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-885_0_4_load_135 | 147 | 0.0022232 | 0.00055718 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-885_0_4_load_112 | 148 | 0.00091043 | 0.00022818 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-885_0_4_load_116 | 149 | 0.0013396 | 0.00033573 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-885_0_4_load_123 | 150 | 0.0022194 | 0.00055622 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-885_0_4_load_127 | 151 | 0.0028914 | 0.00072466 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-885_0_4_load_130 | 152 | 0.0074338 | 0.0018631 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-885_0_4_load_155 | 153 | 0.0011479 | 0.00028768 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-885_0_4_load_153 | 154 | 0.0015083 | 0.00037802 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 151 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-885_0_4_line_0 |  | 0 | 1 | 0.025039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-885_0_4_line_1 |  | 1 | 2 | 0.00343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-885_0_4_line_2 |  | 1 | 3 | 0.035529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-885_0_4_line_3 |  | 2 | 4 | 0.0050942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-885_0_4_line_4 |  | 2 | 5 | 0.023938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-885_0_4_line_5 |  | 4 | 15 | 0.018091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-885_0_4_line_6 |  | 5 | 16 | 0.021681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-885_0_4_line_7 |  | 6 | 7 | 0.05122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-885_0_4_line_8 |  | 6 | 8 | 0.01474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-885_0_4_line_9 |  | 7 | 18 | 0.041433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-885_0_4_line_10 |  | 7 | 17 | 0.029805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-885_0_4_line_11 |  | 8 | 19 | 0.020868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-885_0_4_line_12 |  | 9 | 10 | 0.037384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-885_0_4_line_13 |  | 9 | 11 | 0.003637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-885_0_4_line_14 |  | 11 | 22 | 0.010559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-885_0_4_line_15 |  | 11 | 23 | 0.012045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-885_0_4_line_16 |  | 12 | 13 | 0.035207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-885_0_4_line_17 |  | 12 | 14 | 0.0050575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-885_0_4_line_18 |  | 14 | 24 | 0.0078052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-885_0_4_line_19 |  | 16 | 25 | 0.026781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-885_0_4_line_20 |  | 18 | 98 | 0.014572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-885_0_4_line_21 |  | 18 | 99 | 0.01758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-885_0_4_line_22 |  | 18 | 95 | 0.02658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-885_0_4_line_23 |  | 19 | 144 | 0.012109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-885_0_4_line_24 |  | 20 | 21 | 0.026125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-885_0_4_line_25 |  | 21 | 87 | 0.0066271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-885_0_4_line_26 |  | 23 | 154 | 0.013481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-885_0_4_line_27 |  | 23 | 114 | 0.0071839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-885_0_4_line_28 |  | 24 | 33 | 0.01355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-885_0_4_line_29 |  | 25 | 28 | 0.016968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-885_0_4_line_30 |  | 26 | 27 | 0.0055631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-885_0_4_line_31 |  | 27 | 29 | 0.0086723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-885_0_4_line_32 |  | 28 | 30 | 0.0035998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-885_0_4_line_33 |  | 29 | 41 | 0.0053725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-885_0_4_line_34 |  | 30 | 51 | 0.018712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-885_0_4_line_35 |  | 31 | 32 | 0.016815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-885_0_4_line_36 |  | 31 | 33 | 0.0022656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-885_0_4_line_37 |  | 32 | 34 | 0.013234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-885_0_4_line_38 |  | 32 | 35 | 0.0022228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-885_0_4_line_39 |  | 33 | 36 | 0.032694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-885_0_4_line_40 |  | 34 | 37 | 0.0098491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-885_0_4_line_41 |  | 35 | 38 | 0.018929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-885_0_4_line_42 |  | 37 | 39 | 0.009657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-885_0_4_line_43 |  | 38 | 40 | 0.0066682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-885_0_4_line_44 |  | 40 | 122 | 0.0085816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-885_0_4_line_45 |  | 41 | 42 | 0.026285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-885_0_4_line_46 |  | 41 | 43 | 0.011143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-885_0_4_line_47 |  | 42 | 44 | 0.005186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-885_0_4_line_48 |  | 42 | 45 | 0.011377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-885_0_4_line_49 |  | 43 | 46 | 0.000365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-885_0_4_line_50 |  | 44 | 121 | 0.024395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-885_0_4_line_51 |  | 44 | 122 | 0.022864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-885_0_4_line_52 |  | 45 | 119 | 0.0003361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-885_0_4_line_53 |  | 46 | 152 | 0.012726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-885_0_4_line_54 |  | 47 | 48 | 0.0010349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-885_0_4_line_55 |  | 47 | 49 | 0.0071071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-885_0_4_line_56 |  | 48 | 50 | 0.018758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-885_0_4_line_57 |  | 49 | 51 | 0.030155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-885_0_4_line_58 |  | 50 | 52 | 0.0029168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-885_0_4_line_59 |  | 52 | 53 | 0.017961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-885_0_4_line_60 |  | 53 | 82 | 0.0048374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-885_0_4_line_61 |  | 54 | 55 | 0.009777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-885_0_4_line_62 |  | 54 | 56 | 0.059867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-885_0_4_line_63 |  | 55 | 106 | 0.001377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-885_0_4_line_64 |  | 56 | 57 | 0.033688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-885_0_4_line_65 |  | 56 | 58 | 0.036926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-885_0_4_line_66 |  | 57 | 105 | 0.012494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-885_0_4_line_67 |  | 59 | 60 | 0.029815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-885_0_4_line_68 |  | 59 | 61 | 0.056352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-885_0_4_line_69 |  | 61 | 85 | 0.023035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-885_0_4_line_70 |  | 62 | 63 | 0.020377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-885_0_4_line_71 |  | 62 | 64 | 0.010426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-885_0_4_line_72 |  | 62 | 65 | 0.022987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-885_0_4_line_73 |  | 62 | 66 | 0.003425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-885_0_4_line_74 |  | 65 | 76 | 0.008404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-885_0_4_line_75 |  | 65 | 77 | 0.012866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-885_0_4_line_76 |  | 66 | 78 | 0.010197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-885_0_4_line_77 |  | 67 | 68 | 0.022338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-885_0_4_line_78 |  | 67 | 69 | 0.036528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-885_0_4_line_79 |  | 68 | 103 | 0.010665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-885_0_4_line_80 |  | 68 | 104 | 0.033991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-885_0_4_line_81 |  | 70 | 71 | 0.020712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-885_0_4_line_82 |  | 70 | 72 | 0.029335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-885_0_4_line_83 |  | 72 | 79 | 0.02204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-885_0_4_line_84 |  | 73 | 74 | 0.032247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_261-885_0_4_line_85 |  | 73 | 75 | 0.019949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_261-885_0_4_line_86 |  | 74 | 77 | 0.005543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_261-885_0_4_line_87 |  | 74 | 90 | 0.015633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-885_0_4_line_88 |  | 75 | 81 | 0.013046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_261-885_0_4_line_89 |  | 77 | 91 | 0.019736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_261-885_0_4_line_90 |  | 77 | 92 | 0.013333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-885_0_4_line_91 |  | 79 | 80 | 0.014138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-885_0_4_line_92 |  | 80 | 81 | 0.028009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-885_0_4_line_93 |  | 81 | 101 | 0.010551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_261-885_0_4_line_94 |  | 82 | 83 | 0.013566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-885_0_4_line_95 |  | 83 | 84 | 0.0083918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-885_0_4_line_96 |  | 84 | 85 | 0.0059598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-885_0_4_line_97 |  | 85 | 86 | 0.0068825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-885_0_4_line_98 |  | 86 | 108 | 0.030075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_261-885_0_4_line_99 |  | 87 | 88 | 0.018613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-885_0_4_line_100 |  | 88 | 89 | 0.014314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-885_0_4_line_101 |  | 89 | 93 | 0.0094926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-885_0_4_line_102 |  | 89 | 145 | 0.0041365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-885_0_4_line_103 |  | 91 | 111 | 0.0070749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_261-885_0_4_line_104 |  | 92 | 143 | 0.034025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-885_0_4_line_105 |  | 93 | 94 | 0.025359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-885_0_4_line_106 |  | 95 | 96 | 0.01293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-885_0_4_line_107 |  | 95 | 97 | 0.000856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-885_0_4_line_108 |  | 96 | 146 | 0.0080768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-885_0_4_line_109 |  | 97 | 139 | 0.013069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-885_0_4_line_110 |  | 97 | 147 | 0.017995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-885_0_4_line_111 |  | 98 | 118 | 0.019528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-885_0_4_line_112 |  | 99 | 113 | 0.008651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-885_0_4_line_113 |  | 99 | 112 | 0.017662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-885_0_4_line_114 |  | 100 | 101 | 0.026033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_261-885_0_4_line_115 |  | 100 | 102 | 0.026253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_261-885_0_4_line_116 |  | 102 | 128 | 0.010821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-885_0_4_line_117 |  | 102 | 125 | 0.014675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_261-885_0_4_line_118 |  | 103 | 145 | 0.026906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-885_0_4_line_119 |  | 104 | 144 | 0.0040413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-885_0_4_line_120 |  | 106 | 143 | 0.003805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-885_0_4_line_121 |  | 107 | 108 | 0.0017386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_261-885_0_4_line_122 |  | 107 | 109 | 0.026347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_261-885_0_4_line_123 |  | 109 | 110 | 0.0016536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_261-885_0_4_line_124 |  | 110 | 111 | 0.0067022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_261-885_0_4_line_125 |  | 113 | 114 | 0.003659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-885_0_4_line_126 |  | 113 | 115 | 0.014312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-885_0_4_line_127 |  | 114 | 116 | 0.009875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-885_0_4_line_128 |  | 115 | 117 | 0.022626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-885_0_4_line_129 |  | 118 | 149 | 0.0026991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-885_0_4_line_130 |  | 119 | 120 | 0.013018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-885_0_4_line_131 |  | 121 | 123 | 0.016924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-885_0_4_line_132 |  | 121 | 124 | 0.010727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_261-885_0_4_line_133 |  | 123 | 136 | 0.020936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-885_0_4_line_134 |  | 124 | 141 | 0.00072805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_261-885_0_4_line_135 |  | 125 | 126 | 0.0083879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
136 | LV_261-885_0_4_line_136 |  | 126 | 127 | 0.012725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
137 | LV_261-885_0_4_line_137 |  | 127 | 129 | 0.003324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
138 | LV_261-885_0_4_line_138 |  | 128 | 132 | 0.011429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_261-885_0_4_line_139 |  | 128 | 133 | 0.020921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_261-885_0_4_line_140 |  | 128 | 130 | 0.0040057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_261-885_0_4_line_141 |  | 129 | 134 | 0.022274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_261-885_0_4_line_142 |  | 129 | 135 | 0.004184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
143 | LV_261-885_0_4_line_143 |  | 130 | 131 | 0.006724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_261-885_0_4_line_144 |  | 133 | 140 | 0.011063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_261-885_0_4_line_145 |  | 133 | 137 | 0.01303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_261-885_0_4_line_146 |  | 135 | 151 | 0.010553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
147 | LV_261-885_0_4_line_147 |  | 135 | 136 | 0.003314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_261-885_0_4_line_148 |  | 135 | 150 | 0.047117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_261-885_0_4_line_149 |  | 137 | 138 | 0.007723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_261-885_0_4_line_150 |  | 137 | 139 | 0.012118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_261-885_0_4_line_151 |  | 139 | 153 | 0.011283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_261-885_0_4_line_152 |  | 141 | 142 | 0.012768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_261-885_0_4_line_153 |  | 146 | 148 | 0.0074636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-885_0_4_trafo_127 | 0.63 MVA 20/0.4 kV | 155 | 151 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2684374.1917 | 1251330.1072 | 2684350.5568 | 1251338.3757
1 | 2684377.4386 | 1251328.9748 | 2684374.1917 | 1251330.1072
2 | 2684374.1917 | 1251330.1072 | 2684372.0224 | 1251319.1793 | 2684369.6113 | 1251311.9729 | 2684363.8621 | 1251296.1994
3 | 2684377.4386 | 1251328.9748 | 2684378.3762 | 1251333.982
4 | 2684377.4386 | 1251328.9748 | 2684376.2461 | 1251322.6086 | 2684371.8961 | 1251308.9698 | 2684370.8537 | 1251306.0019
5 | 2684379.159 | 1251352.0341 | 2684379.3278 | 1251346.8485 | 2684378.3927 | 1251334.07 | 2684378.3762 | 1251333.982
6 | 2684363.6695 | 1251285.5462 | 2684370.8537 | 1251306.0019
7 | 2684626.2284 | 1251340.0192 | 2684614.9354 | 1251339.502 | 2684609.1682 | 1251337.3959 | 2684579.9375 | 1251335.9665 | 2684575.2832 | 1251335.7443
8 | 2684626.2284 | 1251340.0192 | 2684626.4061 | 1251336.5636 | 2684624.2204 | 1251329.4604 | 2684624.2753 | 1251328.2603 | 2684624.3925 | 1251325.6164
9 | 2684541.2452 | 1251340.5734 | 2684541.5097 | 1251333.1494 | 2684544.9534 | 1251333.0429 | 2684550.4878 | 1251334.5452 | 2684572.1978 | 1251335.6002 | 2684575.2832 | 1251335.7443
10 | 2684575.2832 | 1251335.7443 | 2684574.186 | 1251365.5288
11 | 2684626.6497 | 1251306.311 | 2684626.6497 | 1251306.311 | 2684625.2552 | 1251306.1688 | 2684624.3925 | 1251325.6164
12 | 2684539.8131 | 1251393.3037 | 2684526.4365 | 1251392.8125 | 2684514.1545 | 1251392.3148 | 2684506.6021 | 1251392.0513 | 2684505.5535 | 1251390.9466 | 2684505.698 | 1251388.2244
13 | 2684539.8131 | 1251393.3037 | 2684539.9329 | 1251389.6693
14 | 2684550.5196 | 1251389.9539 | 2684539.9329 | 1251389.6693
15 | 2684540.3388 | 1251377.6327 | 2684539.9329 | 1251389.6693
16 | 2684452.6334 | 1251363.7386 | 2684487.8229 | 1251364.8534
17 | 2684452.6334 | 1251363.7386 | 2684452.7738 | 1251358.683
18 | 2684452.7738 | 1251358.683 | 2684452.9591 | 1251352.0122 | 2684453.0061 | 1251350.8814
19 | 2684363.6695 | 1251285.5462 | 2684354.4205 | 1251260.4131
20 | 2684541.2452 | 1251340.5734 | 2684526.6837 | 1251340.0177
21 | 2684541.2452 | 1251340.5734 | 2684540.8811 | 1251358.1481
22 | 2684541.2452 | 1251340.5734 | 2684541.5097 | 1251333.1494 | 2684541.7533 | 1251324.5464 | 2684542.2057 | 1251314.0116
23 | 2684626.6497 | 1251306.311 | 2684627.0432 | 1251294.2085
24 | 2684665.9661 | 1251327.613 | 2684666.2915 | 1251318.731 | 2684666.4188 | 1251315.1078 | 2684666.4673 | 1251313.8298 | 2684666.6406 | 1251308.5728 | 2684666.8741 | 1251301.5036
25 | 2684667.093 | 1251294.8801 | 2684666.8741 | 1251301.5036
26 | 2684540.3388 | 1251377.6327 | 2684526.8564 | 1251376.6175
27 | 2684540.3388 | 1251377.6327 | 2684540.4423 | 1251374.6097 | 2684540.5847 | 1251370.4531
28 | 2684453.5684 | 1251337.3432 | 2684453.0061 | 1251350.8814
29 | 2684348.5605 | 1251244.4893 | 2684354.4205 | 1251260.4131
30 | 2684399.3189 | 1251272.4703 | 2684394.0732 | 1251274.3224
31 | 2684399.3189 | 1251272.4703 | 2684403.4774 | 1251271.0021 | 2684407.5303 | 1251269.6825
32 | 2684348.5605 | 1251244.4893 | 2684347.2748 | 1251241.127
33 | 2684412.6388 | 1251268.0192 | 2684407.5303 | 1251269.6825
34 | 2684340.5914 | 1251223.6492 | 2684347.2748 | 1251241.127
35 | 2684453.1988 | 1251318.2681 | 2684453.5339 | 1251328.6473 | 2684453.5594 | 1251335.0776
36 | 2684453.5684 | 1251337.3432 | 2684453.5594 | 1251335.0776
37 | 2684453.1988 | 1251318.2681 | 2684466.3976 | 1251317.3055
38 | 2684453.1988 | 1251318.2681 | 2684452.9448 | 1251316.0598
39 | 2684453.5684 | 1251337.3432 | 2684486.3459 | 1251338.3111
40 | 2684466.3976 | 1251317.3055 | 2684476.2207 | 1251316.5891
41 | 2684452.9448 | 1251316.0598 | 2684451.2041 | 1251300.9266 | 2684450.5766 | 1251297.2838
42 | 2684485.3797 | 1251313.9679 | 2684479.9792 | 1251316.3149 | 2684476.2207 | 1251316.5891
43 | 2684449.4448 | 1251290.7124 | 2684450.5766 | 1251297.2838
44 | 2684449.4448 | 1251290.7124 | 2684448.785 | 1251286.8816 | 2684447.8179 | 1251282.2879
45 | 2684438.041 | 1251261.087 | 2684424.083 | 1251264.2906 | 2684412.6388 | 1251268.0192
46 | 2684412.6388 | 1251268.0192 | 2684409.3961 | 1251257.3588
47 | 2684443.1079 | 1251259.9139 | 2684438.041 | 1251261.087
48 | 2684438.041 | 1251261.087 | 2684435.2221 | 1251250.0643
49 | 2684409.3961 | 1251257.3588 | 2684409.2899 | 1251257.0096
50 | 2684443.1079 | 1251259.9139 | 2684453.4317 | 1251257.4702 | 2684466.9991 | 1251254.6615
51 | 2684443.1079 | 1251259.9139 | 2684447.8179 | 1251282.2879
52 | 2684435.2221 | 1251250.0643 | 2684435.1388 | 1251249.7387
53 | 2684405.5865 | 1251244.8348 | 2684409.2899 | 1251257.0096
54 | 2684373.2506 | 1251205.7088 | 2684374.1576 | 1251205.2106
55 | 2684367.0214 | 1251209.1306 | 2684373.2506 | 1251205.7088
56 | 2684390.5985 | 1251196.1793 | 2684374.1576 | 1251205.2106
57 | 2684340.5914 | 1251223.6492 | 2684367.0214 | 1251209.1306
58 | 2684390.5985 | 1251196.1793 | 2684393.1549 | 1251194.775
59 | 2684408.8968 | 1251186.1277 | 2684393.1549 | 1251194.775
60 | 2684408.8968 | 1251186.1277 | 2684413.1366 | 1251183.7987
61 | 2684528.0113 | 1251117.9844 | 2684528.5117 | 1251121.5386 | 2684529.27 | 1251127.6797
62 | 2684478.5665 | 1251107.3492 | 2684479.8089 | 1251106.5108 | 2684483.7138 | 1251107.4227 | 2684488.8554 | 1251108.43 | 2684494.6676 | 1251108.9911 | 2684500.1507 | 1251109.3473 | 2684505.8791 | 1251109.429 | 2684512.5076 | 1251108.8676 | 2684519.9078 | 1251107.65 | 2684526.4351 | 1251106.7757 | 2684528.0113 | 1251117.9844
63 | 2684529.4387 | 1251129.0464 | 2684529.27 | 1251127.6797
64 | 2684478.5665 | 1251107.3492 | 2684467.9244 | 1251107.7423 | 2684462.5799 | 1251108.7891 | 2684459.3179 | 1251110.9665 | 2684453.0314 | 1251123.1063
65 | 2684478.5665 | 1251107.3492 | 2684493.3696 | 1251116.9007 | 2684494.2498 | 1251130.3456 | 2684492.7431 | 1251135.9833
66 | 2684447.2858 | 1251134.2014 | 2684453.0314 | 1251123.1063
67 | 2684370.1469 | 1251128.6542 | 2684395.4891 | 1251112.9465
68 | 2684370.1469 | 1251128.6542 | 2684396.1723 | 1251144.7813 | 2684402.6904 | 1251148.7771 | 2684417.7514 | 1251158.7971
69 | 2684437.6059 | 1251170.3572 | 2684428.204 | 1251165.8421 | 2684423.6811 | 1251162.742 | 2684417.7514 | 1251158.7971
70 | 2684560.3625 | 1251167.4051 | 2684557.0347 | 1251167.8469 | 2684557.7756 | 1251174.1177 | 2684568.4453 | 1251172.8357
71 | 2684567.3553 | 1251162.4679 | 2684568.4453 | 1251172.8357
72 | 2684549.0429 | 1251178.2518 | 2684568.7708 | 1251175.9426 | 2684568.4453 | 1251172.8357
73 | 2684571.8557 | 1251172.4285 | 2684568.4453 | 1251172.8357
74 | 2684549.0429 | 1251178.2518 | 2684547.8784 | 1251169.9289
75 | 2684536.2262 | 1251179.7479 | 2684549.0429 | 1251178.2518
76 | 2684571.8557 | 1251172.4285 | 2684570.666 | 1251162.3007
77 | 2684628.2792 | 1251256.1967 | 2684628.4123 | 1251252.1622 | 2684643.0852 | 1251252.8278 | 2684643.1897 | 1251249.2155
78 | 2684643.1897 | 1251249.2155 | 2684606.6887 | 1251247.8199
79 | 2684628.2792 | 1251256.1967 | 2684638.9396 | 1251256.5237
80 | 2684628.2792 | 1251256.1967 | 2684627.1745 | 1251290.1693
81 | 2684627.6019 | 1251173.6362 | 2684629.846 | 1251193.0383 | 2684629.9121 | 1251194.2167
82 | 2684627.6019 | 1251173.6362 | 2684603.164 | 1251176.4338 | 2684598.3772 | 1251177.0215
83 | 2684598.3772 | 1251177.0215 | 2684599.326 | 1251184.5852 | 2684597.4967 | 1251184.7592 | 2684598.6719 | 1251197.2832
84 | 2684536.9706 | 1251185.2404 | 2684547.3637 | 1251183.2427 | 2684568.9609 | 1251180.6044
85 | 2684568.9609 | 1251180.6044 | 2684570.7859 | 1251200.4695
86 | 2684536.2262 | 1251179.7479 | 2684536.9706 | 1251185.2404
87 | 2684536.9706 | 1251185.2404 | 2684539.0764 | 1251200.7308
88 | 2684571.9793 | 1251213.461 | 2684570.7859 | 1251200.4695
89 | 2684536.2262 | 1251179.7479 | 2684516.5599 | 1251181.4073
90 | 2684536.2262 | 1251179.7479 | 2684534.9381 | 1251172.6798 | 2684534.1631 | 1251166.58
91 | 2684599.9928 | 1251211.3592 | 2684598.6719 | 1251197.2832
92 | 2684571.9793 | 1251213.461 | 2684599.9928 | 1251211.3592
93 | 2684571.9793 | 1251213.461 | 2684571.6567 | 1251224.0073
94 | 2684413.1366 | 1251183.7987 | 2684425.0271 | 1251177.267
95 | 2684425.0271 | 1251177.267 | 2684432.3823 | 1251173.2266
96 | 2684437.6059 | 1251170.3572 | 2684432.3823 | 1251173.2266
97 | 2684437.6059 | 1251170.3572 | 2684441.2328 | 1251169.5861 | 2684444.3698 | 1251170.0728
98 | 2684444.3698 | 1251170.0728 | 2684444.8633 | 1251170.1494 | 2684457.6224 | 1251174.2787 | 2684466.3429 | 1251176.816 | 2684473.2887 | 1251178.2036
99 | 2684667.093 | 1251294.8801 | 2684667.7115 | 1251276.2773
100 | 2684668.1825 | 1251261.9709 | 2684667.7552 | 1251274.9635 | 2684667.7115 | 1251276.2773
101 | 2684666.8623 | 1251253.9905 | 2684668.4464 | 1251254.0688 | 2684668.1825 | 1251261.9709
102 | 2684668.1825 | 1251261.9709 | 2684665.9344 | 1251261.8721 | 2684664.6914 | 1251260.4534
103 | 2684509.4982 | 1251181.6874 | 2684512.8948 | 1251181.7166 | 2684516.5599 | 1251181.4073
104 | 2684529.9057 | 1251132.8225 | 2684531.1648 | 1251142.9814 | 2684534.1631 | 1251166.58
105 | 2684666.8623 | 1251253.9905 | 2684667.8133 | 1251228.6518
106 | 2684542.2057 | 1251314.0116 | 2684536.014 | 1251314.1345 | 2684529.2803 | 1251313.9174
107 | 2684542.2057 | 1251314.0116 | 2684542.233 | 1251313.1558
108 | 2684529.2803 | 1251313.9174 | 2684521.2078 | 1251313.657
109 | 2684542.233 | 1251313.1558 | 2684542.7062 | 1251300.0972
110 | 2684542.233 | 1251313.1558 | 2684560.2089 | 1251313.9815
111 | 2684526.6837 | 1251340.0177 | 2684507.1702 | 1251339.2731
112 | 2684540.7048 | 1251366.7965 | 2684540.8811 | 1251358.1481
113 | 2684540.8811 | 1251358.1481 | 2684551.7796 | 1251358.2703 | 2684558.5412 | 1251358.4107
114 | 2684570.8608 | 1251250.028 | 2684571.6567 | 1251224.0073
115 | 2684544.5425 | 1251249.1964 | 2684570.8608 | 1251250.028
116 | 2684544.1542 | 1251260.01 | 2684544.1815 | 1251259.1542 | 2684544.5425 | 1251249.1964
117 | 2684544.5425 | 1251249.1964 | 2684529.8686 | 1251249.3767
118 | 2684638.9396 | 1251256.5237 | 2684660.1814 | 1251257.1753 | 2684663.3496 | 1251258.9218 | 2684664.6914 | 1251260.4534
119 | 2684627.1745 | 1251290.1693 | 2684627.0432 | 1251294.2085
120 | 2684529.9057 | 1251132.8225 | 2684529.4387 | 1251129.0464
121 | 2684474.9936 | 1251178.5443 | 2684473.2887 | 1251178.2036
122 | 2684474.9936 | 1251178.5443 | 2684477.491 | 1251179.0432 | 2684489.4252 | 1251180.6701 | 2684501.1426 | 1251181.6156
123 | 2684502.7962 | 1251181.6298 | 2684501.1426 | 1251181.6156 | 2684501.1426 | 1251181.6156
124 | 2684502.7962 | 1251181.6298 | 2684509.4982 | 1251181.6874
125 | 2684540.7048 | 1251366.7965 | 2684540.5847 | 1251370.4531
126 | 2684540.7048 | 1251366.7965 | 2684526.3965 | 1251366.4851
127 | 2684540.5847 | 1251370.4531 | 2684550.4842 | 1251370.7501
128 | 2684512.7838 | 1251357.4716 | 2684512.4893 | 1251366.1825 | 2684526.3965 | 1251366.4851
129 | 2684504.4731 | 1251339.1702 | 2684507.1702 | 1251339.2731
130 | 2684431.9133 | 1251237.1262 | 2684435.1388 | 1251249.7387
131 | 2684466.9991 | 1251254.6615 | 2684478.7054 | 1251252.6713 | 2684483.7287 | 1251252.1508
132 | 2684466.9991 | 1251254.6615 | 2684465.2446 | 1251244.0792
133 | 2684504.5788 | 1251250.2939 | 2684495.6851 | 1251250.912 | 2684483.7287 | 1251252.1508
134 | 2684465.2446 | 1251244.0792 | 2684465.1255 | 1251243.361
135 | 2684521.4814 | 1251249.4798 | 2684529.8686 | 1251249.3767
136 | 2684508.7724 | 1251250.009 | 2684515.2406 | 1251249.5565 | 2684521.4814 | 1251249.4798
137 | 2684508.7724 | 1251250.009 | 2684508.9893 | 1251253.3257
138 | 2684544.1542 | 1251260.01 | 2684555.6059 | 1251260.5182
139 | 2684543.3953 | 1251280.9149 | 2684543.5821 | 1251275.7581 | 2684543.9563 | 1251265.4113 | 2684544.0686 | 1251262.2994 | 2684544.1542 | 1251260.01
140 | 2684544.1542 | 1251260.01 | 2684544.1815 | 1251259.1542 | 2684541.0383 | 1251259.354
141 | 2684510.4234 | 1251275.5517 | 2684508.9893 | 1251253.3257
142 | 2684508.9893 | 1251253.3257 | 2684506.4586 | 1251253.4564 | 2684504.8034 | 1251253.5996
143 | 2684534.3066 | 1251259.7583 | 2684541.0383 | 1251259.354
144 | 2684543.3953 | 1251280.9149 | 2684554.4882 | 1251281.1733
145 | 2684540.0611 | 1251290.797 | 2684543.0329 | 1251290.9617 | 2684543.3953 | 1251280.9149
146 | 2684499.119 | 1251261.013 | 2684502.8732 | 1251259.7878 | 2684504.9021 | 1251255.1466 | 2684504.8034 | 1251253.5996
147 | 2684504.5788 | 1251250.2939 | 2684504.8034 | 1251253.5996
148 | 2684504.8034 | 1251253.5996 | 2684497.5019 | 1251254.2515 | 2684483.1766 | 1251255.6817 | 2684467.1602 | 1251258.1886 | 2684458.1436 | 1251259.9065
149 | 2684532.3401 | 1251290.1753 | 2684540.0611 | 1251290.797
150 | 2684540.0611 | 1251290.797 | 2684543.0329 | 1251290.9617 | 2684542.7062 | 1251300.0972
151 | 2684542.7062 | 1251300.0972 | 2684554.016 | 1251300.5033
152 | 2684463.0371 | 1251230.7649 | 2684465.1255 | 1251243.361
153 | 2684513.748 | 1251313.4164 | 2684521.2078 | 1251313.657

## bus_geodata
| x | y | coords
0 | 2684350.5568 | 1251338.3757
1 | 2684374.1917 | 1251330.1072
2 | 2684377.4386 | 1251328.9748
3 | 2684363.8621 | 1251296.1994
4 | 2684378.3762 | 1251333.982
5 | 2684370.8537 | 1251306.0019
6 | 2684626.2284 | 1251340.0192
7 | 2684575.2832 | 1251335.7443
8 | 2684624.3925 | 1251325.6164
9 | 2684539.8131 | 1251393.3037
10 | 2684505.698 | 1251388.2244
11 | 2684539.9329 | 1251389.6693
12 | 2684452.6334 | 1251363.7386
13 | 2684487.8229 | 1251364.8534
14 | 2684452.7738 | 1251358.683
15 | 2684379.159 | 1251352.0341
16 | 2684363.6695 | 1251285.5462
17 | 2684574.186 | 1251365.5288
18 | 2684541.2452 | 1251340.5734
19 | 2684626.6497 | 1251306.311
20 | 2684665.9661 | 1251327.613
21 | 2684666.8741 | 1251301.5036
22 | 2684550.5196 | 1251389.9539
23 | 2684540.3388 | 1251377.6327
24 | 2684453.0061 | 1251350.8814
25 | 2684354.4205 | 1251260.4131
26 | 2684394.0732 | 1251274.3224
27 | 2684399.3189 | 1251272.4703
28 | 2684348.5605 | 1251244.4893
29 | 2684407.5303 | 1251269.6825
30 | 2684347.2748 | 1251241.127
31 | 2684453.5594 | 1251335.0776
32 | 2684453.1988 | 1251318.2681
33 | 2684453.5684 | 1251337.3432
34 | 2684466.3976 | 1251317.3055
35 | 2684452.9448 | 1251316.0598
36 | 2684486.3459 | 1251338.3111
37 | 2684476.2207 | 1251316.5891
38 | 2684450.5766 | 1251297.2838
39 | 2684485.3797 | 1251313.9679
40 | 2684449.4448 | 1251290.7124
41 | 2684412.6388 | 1251268.0192
42 | 2684438.041 | 1251261.087
43 | 2684409.3961 | 1251257.3588
44 | 2684443.1079 | 1251259.9139
45 | 2684435.2221 | 1251250.0643
46 | 2684409.2899 | 1251257.0096
47 | 2684373.2506 | 1251205.7088
48 | 2684374.1576 | 1251205.2106
49 | 2684367.0214 | 1251209.1306
50 | 2684390.5985 | 1251196.1793
51 | 2684340.5914 | 1251223.6492
52 | 2684393.1549 | 1251194.775
53 | 2684408.8968 | 1251186.1277
54 | 2684528.0113 | 1251117.9844
55 | 2684529.27 | 1251127.6797
56 | 2684478.5665 | 1251107.3492
57 | 2684453.0314 | 1251123.1063
58 | 2684492.7431 | 1251135.9833
59 | 2684370.1469 | 1251128.6542
60 | 2684395.4891 | 1251112.9465
61 | 2684417.7514 | 1251158.7971
62 | 2684568.4453 | 1251172.8357
63 | 2684560.3625 | 1251167.4051
64 | 2684567.3553 | 1251162.4679
65 | 2684549.0429 | 1251178.2518
66 | 2684571.8557 | 1251172.4285
67 | 2684643.1897 | 1251249.2155
68 | 2684628.2792 | 1251256.1967
69 | 2684606.6887 | 1251247.8199
70 | 2684627.6019 | 1251173.6362
71 | 2684629.9121 | 1251194.2167
72 | 2684598.3772 | 1251177.0215
73 | 2684568.9609 | 1251180.6044
74 | 2684536.9706 | 1251185.2404
75 | 2684570.7859 | 1251200.4695
76 | 2684547.8784 | 1251169.9289
77 | 2684536.2262 | 1251179.7479
78 | 2684570.666 | 1251162.3007
79 | 2684598.6719 | 1251197.2832
80 | 2684599.9928 | 1251211.3592
81 | 2684571.9793 | 1251213.461
82 | 2684413.1366 | 1251183.7987
83 | 2684425.0271 | 1251177.267
84 | 2684432.3823 | 1251173.2266
85 | 2684437.6059 | 1251170.3572
86 | 2684444.3698 | 1251170.0728
87 | 2684667.093 | 1251294.8801
88 | 2684667.7115 | 1251276.2773
89 | 2684668.1825 | 1251261.9709
90 | 2684539.0764 | 1251200.7308
91 | 2684516.5599 | 1251181.4073
92 | 2684534.1631 | 1251166.58
93 | 2684666.8623 | 1251253.9905
94 | 2684667.8133 | 1251228.6518
95 | 2684542.2057 | 1251314.0116
96 | 2684529.2803 | 1251313.9174
97 | 2684542.233 | 1251313.1558
98 | 2684526.6837 | 1251340.0177
99 | 2684540.8811 | 1251358.1481
100 | 2684570.8608 | 1251250.028
101 | 2684571.6567 | 1251224.0073
102 | 2684544.5425 | 1251249.1964
103 | 2684638.9396 | 1251256.5237
104 | 2684627.1745 | 1251290.1693
105 | 2684447.2858 | 1251134.2014
106 | 2684529.4387 | 1251129.0464
107 | 2684474.9936 | 1251178.5443
108 | 2684473.2887 | 1251178.2036
109 | 2684501.1426 | 1251181.6156
110 | 2684502.7962 | 1251181.6298
111 | 2684509.4982 | 1251181.6874
112 | 2684558.5412 | 1251358.4107
113 | 2684540.7048 | 1251366.7965
114 | 2684540.5847 | 1251370.4531
115 | 2684526.3965 | 1251366.4851
116 | 2684550.4842 | 1251370.7501
117 | 2684512.7838 | 1251357.4716
118 | 2684507.1702 | 1251339.2731
119 | 2684435.1388 | 1251249.7387
120 | 2684431.9133 | 1251237.1262
121 | 2684466.9991 | 1251254.6615
122 | 2684447.8179 | 1251282.2879
123 | 2684483.7287 | 1251252.1508
124 | 2684465.2446 | 1251244.0792
125 | 2684529.8686 | 1251249.3767
126 | 2684521.4814 | 1251249.4798
127 | 2684508.7724 | 1251250.009
128 | 2684544.1542 | 1251260.01
129 | 2684508.9893 | 1251253.3257
130 | 2684541.0383 | 1251259.354
131 | 2684534.3066 | 1251259.7583
132 | 2684555.6059 | 1251260.5182
133 | 2684543.3953 | 1251280.9149
134 | 2684510.4234 | 1251275.5517
135 | 2684504.8034 | 1251253.5996
136 | 2684504.5788 | 1251250.2939
137 | 2684540.0611 | 1251290.797
138 | 2684532.3401 | 1251290.1753
139 | 2684542.7062 | 1251300.0972
140 | 2684554.4882 | 1251281.1733
141 | 2684465.1255 | 1251243.361
142 | 2684463.0371 | 1251230.7649
143 | 2684529.9057 | 1251132.8225
144 | 2684627.0432 | 1251294.2085
145 | 2684664.6914 | 1251260.4534
146 | 2684521.2078 | 1251313.657
147 | 2684560.2089 | 1251313.9815
148 | 2684513.748 | 1251313.4164
149 | 2684504.4731 | 1251339.1702
150 | 2684458.1436 | 1251259.9065
151 | 2684499.119 | 1251261.013
152 | 2684405.5865 | 1251244.8348
153 | 2684554.016 | 1251300.5033
154 | 2684526.8564 | 1251376.6175
155 | 2684504.8034 | 1251253.5996

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9702 | -0.57592 | 0.016721 | 0.0041906
1 | 0.97059 | -0.56817 | 0 | 0
2 | 0.97069 | -0.5662 | 0 | 0
3 | 0.97011 | -0.57763 | 0.014389 | 0.0036062
4 | 0.97065 | -0.56709 | 0.0025556 | 0.00064049
5 | 0.9716 | -0.54822 | 0.0058575 | 0.001468
6 | 0.97683 | -0.4451 | 0 | 0
7 | 0.98005 | -0.38213 | 0 | 0
8 | 0.9759 | -0.4633 | 0.0038396 | 0.0009623
9 | 0.98363 | -0.31273 | 0 | 0
10 | 0.98358 | -0.31357 | 0.0012443 | 0.00031186
11 | 0.98363 | -0.31265 | 0 | 0
12 | 0.99177 | -0.15819 | 0 | 0
13 | 0.99171 | -0.15921 | 0.001637 | 0.00041027
14 | 0.99177 | -0.15804 | 0.0054217 | 0.0013588
15 | 0.97053 | -0.56943 | 0.006968 | 0.0017463
16 | 0.97254 | -0.52963 | 0 | 0
17 | 0.97913 | -0.40027 | 0.033508 | 0.0083978
18 | 0.98395 | -0.30646 | 0 | 0
19 | 0.97467 | -0.48766 | 0.0017972 | 0.00045043
20 | 0.97209 | -0.53842 | 0.0022124 | 0.00055449
21 | 0.97215 | -0.53736 | 0.0017471 | 0.00043786
22 | 0.98362 | -0.31289 | 0.0012812 | 0.0003211
23 | 0.98366 | -0.3121 | 0 | 0
24 | 0.99182 | -0.15707 | 0.0023269 | 0.00058317
25 | 0.97371 | -0.50671 | 0.01173 | 0.0029399
26 | 0.99297 | -0.13481 | 0.0084206 | 0.0021104
27 | 0.99302 | -0.13399 | 0.0016289 | 0.00040825
28 | 0.97463 | -0.48856 | 0 | 0
29 | 0.9931 | -0.13245 | 0.0016198 | 0.00040596
30 | 0.97482 | -0.48472 | 0.0093136 | 0.0023342
31 | 0.99196 | -0.15437 | 0.0059934 | 0.0015021
32 | 0.99223 | -0.14927 | 0 | 0
33 | 0.99194 | -0.15481 | 0 | 0
34 | 0.99217 | -0.15044 | 0.0015925 | 0.00039912
35 | 0.99227 | -0.14839 | 0.0054097 | 0.0013558
36 | 0.99189 | -0.15583 | 0.0017493 | 0.00043842
37 | 0.99214 | -0.15104 | 0.0015945 | 0.00039961
38 | 0.99275 | -0.13917 | 0.0018033 | 0.00045196
39 | 0.99212 | -0.15135 | 0.0018237 | 0.00045706
40 | 0.99293 | -0.1357 | 0.0041966 | 0.0010518
41 | 0.99315 | -0.13134 | 0 | 0
42 | 0.99385 | -0.11791 | 0 | 0
43 | 0.99298 | -0.13474 | 0.0016438 | 0.00041199
44 | 0.99402 | -0.11459 | 0 | 0
45 | 0.99377 | -0.11938 | 0.0016167 | 0.00040519
46 | 0.99297 | -0.13484 | 0.0081829 | 0.0020508
47 | 0.97839 | -0.41486 | 0.0020215 | 0.00050663
48 | 0.97847 | -0.41344 | 0.0056844 | 0.0014246
49 | 0.97791 | -0.42437 | 0.0058963 | 0.0014778
50 | 0.97988 | -0.38577 | 0.0078427 | 0.0019656
51 | 0.976 | -0.46156 | 0 | 0
52 | 0.98013 | -0.38106 | 0.0058595 | 0.0014685
53 | 0.98171 | -0.3502 | 0.0020727 | 0.00051947
54 | 0.98787 | -0.23145 | 0 | 0
55 | 0.98799 | -0.22925 | 0.0061723 | 0.0015469
56 | 0.98718 | -0.24492 | 0 | 0
57 | 0.98695 | -0.24946 | 0.0050451 | 0.0012644
58 | 0.98701 | -0.24826 | 0.0050514 | 0.001266
59 | 0.98414 | -0.30334 | 0 | 0
60 | 0.98392 | -0.30773 | 0.0081793 | 0.0020499
61 | 0.98457 | -0.29505 | 0.004852 | 0.001216
62 | 0.98877 | -0.21404 | 0 | 0
63 | 0.98874 | -0.21459 | 0.0015018 | 0.0003764
64 | 0.98876 | -0.21424 | 0.0010769 | 0.00026991
65 | 0.98885 | -0.21238 | 0 | 0
66 | 0.98876 | -0.21413 | 0 | 0
67 | 0.97257 | -0.52903 | 0 | 0
68 | 0.97287 | -0.52299 | 0 | 0
69 | 0.97207 | -0.53892 | 0.014685 | 0.0036804
70 | 0.99086 | -0.17412 | 0 | 0
71 | 0.99066 | -0.17794 | 0.010383 | 0.0026022
72 | 0.99114 | -0.16872 | 0 | 0
73 | 0.99053 | -0.18012 | 0 | 0
74 | 0.98915 | -0.20672 | 0 | 0
75 | 0.99139 | -0.16369 | 0.011304 | 0.002833
76 | 0.98884 | -0.2126 | 0.0014665 | 0.00036753
77 | 0.98892 | -0.21111 | 0 | 0
78 | 0.98875 | -0.2144 | 0.0014712 | 0.00036872
79 | 0.99135 | -0.16466 | 0.0061382 | 0.0015384
80 | 0.99156 | -0.16052 | 0 | 0
81 | 0.99198 | -0.15231 | 0 | 0
82 | 0.98215 | -0.34173 | 0.0050563 | 0.0012672
83 | 0.98344 | -0.31676 | 0.0022111 | 0.00055416
84 | 0.98425 | -0.30102 | 0.0019232 | 0.00048199
85 | 0.98484 | -0.28965 | 0 | 0
86 | 0.9856 | -0.27492 | 0.0039076 | 0.00097933
87 | 0.97217 | -0.53687 | 0 | 0
88 | 0.97224 | -0.53552 | 0.00083776 | 0.00020996
89 | 0.9723 | -0.53425 | 0 | 0
90 | 0.98904 | -0.20886 | 0.0076777 | 0.0019242
91 | 0.98823 | -0.22443 | 0.0011977 | 0.00030018
92 | 0.98866 | -0.21612 | 0.0022835 | 0.00057231
93 | 0.97223 | -0.53563 | 0 | 0
94 | 0.97205 | -0.53931 | 0.0078686 | 0.0019721
95 | 0.98683 | -0.25089 | 0 | 0
96 | 0.98679 | -0.2516 | 0.00099616 | 0.00024966
97 | 0.98692 | -0.24906 | 0 | 0
98 | 0.98388 | -0.30771 | 0.0024275 | 0.0006084
99 | 0.98378 | -0.30984 | 0 | 0
100 | 0.99385 | -0.11651 | 0 | 0
101 | 0.9925 | -0.14235 | 0.011312 | 0.0028351
102 | 0.99522 | -0.090527 | 0 | 0
103 | 0.97271 | -0.52614 | 0.0016247 | 0.00040719
104 | 0.97385 | -0.50378 | 0.0011506 | 0.00028837
105 | 0.98692 | -0.25002 | 0.0024924 | 0.00062465
106 | 0.98801 | -0.22878 | 0 | 0
107 | 0.98681 | -0.25177 | 0.010651 | 0.0026694
108 | 0.98675 | -0.25281 | 0.011146 | 0.0027936
109 | 0.98769 | -0.23471 | 0.0022356 | 0.0005603
110 | 0.98775 | -0.23362 | 0.0018717 | 0.00046908
111 | 0.98798 | -0.22916 | 0.0011096 | 0.00027809
112 | 0.98374 | -0.31054 | 0.0021703 | 0.00054393
113 | 0.98371 | -0.31117 | 0 | 0
114 | 0.98369 | -0.31158 | 0 | 0
115 | 0.98368 | -0.31178 | 0.0011693 | 0.00029306
116 | 0.98367 | -0.31196 | 0.0021241 | 0.00053236
117 | 0.98365 | -0.31226 | 0.0011836 | 0.00029663
118 | 0.98384 | -0.30852 | 0.00097913 | 0.00024539
119 | 0.99377 | -0.11941 | 0.0024135 | 0.00060489
120 | 0.99373 | -0.12017 | 0.0032829 | 0.00082276
121 | 0.99571 | -0.08197 | 0 | 0
122 | 0.99319 | -0.13062 | 0.0061382 | 0.0015384
123 | 0.997 | -0.05729 | 0.0013986 | 0.00035052
124 | 0.99564 | -0.083312 | 0.0013913 | 0.0003487
125 | 0.99645 | -0.067183 | 0.0022744 | 0.00057002
126 | 0.99715 | -0.053782 | 0.0033033 | 0.00082788
127 | 0.99824 | -0.033304 | 0 | 0
128 | 0.99384 | -0.11672 | 0 | 0
129 | 0.99852 | -0.027962 | 0 | 0
130 | 0.99382 | -0.11703 | 0 | 0
131 | 0.9938 | -0.11755 | 0.0043859 | 0.0010992
132 | 0.99381 | -0.11735 | 0.0031289 | 0.00078418
133 | 0.99132 | -0.16477 | 0 | 0
134 | 0.99848 | -0.028787 | 0.002118 | 0.00053083
135 | 0.99888 | -0.021203 | 0 | 0
136 | 0.99861 | -0.026336 | 0.0041795 | 0.0010475
137 | 0.98978 | -0.19408 | 0 | 0
138 | 0.98976 | -0.19459 | 0.0037114 | 0.00093017
139 | 0.9884 | -0.22062 | 0 | 0
140 | 0.99128 | -0.1654 | 0.0031943 | 0.00080056
141 | 0.99564 | -0.083385 | 0.0022477 | 0.00056333
142 | 0.9956 | -0.084166 | 0.0034763 | 0.00087125
143 | 0.98807 | -0.22751 | 0 | 0
144 | 0.97397 | -0.50142 | 0.030023 | 0.0075245
145 | 0.97235 | -0.53328 | 0.0017352 | 0.00043489
146 | 0.98677 | -0.2519 | 0.0011697 | 0.00029316
147 | 0.98688 | -0.24977 | 0.0022232 | 0.00055718
148 | 0.98677 | -0.25202 | 0.00091043 | 0.00022818
149 | 0.98384 | -0.30859 | 0.0013396 | 0.00033573
150 | 0.99878 | -0.023031 | 0.0022194 | 0.00055622
151 | 1 | 0 | -0.46927 | -0.11993
152 | 0.99289 | -0.13651 | 0.0074338 | 0.0018631
153 | 0.98839 | -0.22085 | 0.0011479 | 0.00028768
154 | 0.98364 | -0.31247 | 0.0015083 | 0.00037802
155 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.016721 | -0.0041906 | 0.016727 | 0.0041942 | 6.1752e-06 | 3.6428e-06 | 0.025645 | 0.025645 | 0.025645 | 0.9702 | -0.57592 | 0.97059 | -0.56817 | 7.0453
1 | -0.031122 | -0.0078042 | 0.031125 | 0.007806 | 2.9284e-06 | 1.8318e-06 | 0.047715 | 0.047715 | 0.047715 | 0.97059 | -0.56817 | 0.97069 | -0.5662 | 13.1085
2 | 0.014395 | 0.0036099 | -0.014389 | -0.0036062 | 6.4899e-06 | 3.7147e-06 | 0.02207 | 0.022071 | 0.022071 | 0.97059 | -0.56817 | 0.97011 | -0.57763 | 6.0634
3 | 0.0095248 | 0.0023873 | -0.0095244 | -0.0023871 | 4.0726e-07 | 1.9768e-07 | 0.014601 | 0.014601 | 0.014601 | 0.97069 | -0.5662 | 0.97065 | -0.56709 | 4.0113
4 | -0.04065 | -0.010193 | 0.040685 | 0.010215 | 3.486e-05 | 2.2014e-05 | 0.062316 | 0.062316 | 0.062316 | 0.97069 | -0.5662 | 0.9716 | -0.54822 | 17.1198
5 | 0.0069688 | 0.0017466 | -0.006968 | -0.0017463 | 7.7427e-07 | 2.7195e-07 | 0.010683 | 0.010683 | 0.010683 | 0.97065 | -0.56709 | 0.97053 | -0.56943 | 2.935
6 | -0.046542 | -0.011683 | 0.046584 | 0.01171 | 4.1316e-05 | 2.6174e-05 | 0.071287 | 0.071287 | 0.071287 | 0.9716 | -0.54822 | 0.97254 | -0.52963 | 19.5843
7 | -0.067749 | -0.017064 | 0.067953 | 0.017195 | 0.00020469 | 0.00013036 | 0.10323 | 0.10323 | 0.10323 | 0.97683 | -0.4451 | 0.98005 | -0.38213 | 28.3607
8 | 0.067749 | 0.017064 | -0.06769 | -0.017027 | 5.8906e-05 | 3.7516e-05 | 0.10323 | 0.10323 | 0.10323 | 0.97683 | -0.4451 | 0.9759 | -0.4633 | 28.3607
9 | -0.10149 | -0.025611 | 0.10186 | 0.025846 | 0.00036923 | 0.00023578 | 0.15416 | 0.15416 | 0.15416 | 0.98005 | -0.38213 | 0.98395 | -0.30646 | 42.3503
10 | 0.033537 | 0.008416 | -0.033508 | -0.0083978 | 2.8983e-05 | 1.8174e-05 | 0.050923 | 0.050923 | 0.050923 | 0.98005 | -0.38213 | 0.97913 | -0.40027 | 13.9898
11 | 0.06385 | 0.016065 | -0.063776 | -0.016017 | 7.4207e-05 | 4.7232e-05 | 0.097378 | 0.097378 | 0.097378 | 0.9759 | -0.4633 | 0.97467 | -0.48766 | 26.7523
12 | 0.0012444 | 0.00031142 | -0.0012443 | -0.00031186 | 4.9677e-08 | -4.4271e-07 | 0.0018823 | 0.0018825 | 0.0018825 | 0.98363 | -0.31273 | 0.98358 | -0.31357 | 0.51717
13 | -0.0012444 | -0.00031142 | 0.0012444 | 0.00031138 | 4.8324e-09 | -4.3073e-08 | 0.0018823 | 0.0018823 | 0.0018823 | 0.98363 | -0.31273 | 0.98363 | -0.31265 | 0.51713
14 | 0.0012812 | 0.00032097 | -0.0012812 | -0.0003211 | 1.4874e-08 | -1.2451e-07 | 0.0019381 | 0.0019382 | 0.0019382 | 0.98363 | -0.31265 | 0.98362 | -0.31289 | 0.53247
15 | -0.0025256 | -0.00063235 | 0.0025257 | 0.00063224 | 6.5927e-08 | -1.107e-07 | 0.0038205 | 0.0038204 | 0.0038205 | 0.98363 | -0.31265 | 0.98366 | -0.3121 | 1.0496
16 | 0.0016371 | 0.00040987 | -0.001637 | -0.00041027 | 7.9648e-08 | -4.0332e-07 | 0.0024561 | 0.0024562 | 0.0024562 | 0.99177 | -0.15819 | 0.99171 | -0.15921 | 0.67479
17 | -0.0016371 | -0.00040987 | 0.0016371 | 0.00040981 | 1.1441e-08 | -5.7941e-08 | 0.0024561 | 0.0024561 | 0.0024561 | 0.99177 | -0.15819 | 0.99177 | -0.15804 | 0.67475
18 | -0.0070588 | -0.0017686 | 0.0070592 | 0.0017687 | 3.2829e-07 | 1.0938e-07 | 0.010591 | 0.010591 | 0.010591 | 0.99177 | -0.15804 | 0.99182 | -0.15707 | 2.9095
19 | -0.046584 | -0.01171 | 0.046635 | 0.011742 | 5.1036e-05 | 3.233e-05 | 0.071287 | 0.071287 | 0.071287 | 0.97254 | -0.52963 | 0.97371 | -0.50671 | 19.5843
20 | 0.0047466 | 0.0011893 | -0.0047463 | -0.0011893 | 2.8157e-07 | -4.8732e-09 | 0.0071781 | 0.0071782 | 0.0071782 | 0.98395 | -0.30646 | 0.98388 | -0.30771 | 1.972
21 | 0.010684 | 0.0026765 | -0.010682 | -0.0026756 | 1.721e-06 | 8.7817e-07 | 0.016157 | 0.016157 | 0.016157 | 0.98395 | -0.30646 | 0.98378 | -0.30984 | 4.4388
22 | -0.11729 | -0.029712 | 0.1176 | 0.029913 | 0.000314 | 0.00020062 | 0.17749 | 0.17749 | 0.17749 | 0.98395 | -0.30646 | 0.98683 | -0.25089 | 48.761
23 | 0.061979 | 0.015567 | -0.061938 | -0.015541 | 4.0667e-05 | 2.5876e-05 | 0.094635 | 0.094635 | 0.094635 | 0.97467 | -0.48766 | 0.97397 | -0.50142 | 25.9985
24 | -0.0022124 | -0.00055449 | 0.0022125 | 0.00055424 | 1.1236e-07 | -2.5199e-07 | 0.0033866 | 0.0033865 | 0.0033866 | 0.97209 | -0.53842 | 0.97215 | -0.53736 | 0.9304
25 | -0.0039596 | -0.00099209 | 0.0039597 | 0.00099207 | 9.1285e-08 | -2.3747e-08 | 0.0060607 | 0.0060607 | 0.0060607 | 0.97215 | -0.53736 | 0.97217 | -0.53687 | 1.665
26 | 0.0015084 | 0.00037787 | -0.0015083 | -0.00037802 | 2.6319e-08 | -1.5428e-07 | 0.0022817 | 0.0022817 | 0.0022817 | 0.98366 | -0.3121 | 0.98364 | -0.31247 | 0.62685
27 | -0.004034 | -0.0010101 | 0.0040341 | 0.0010101 | 1.0031e-07 | -2.6996e-08 | 0.0061021 | 0.0061021 | 0.0061021 | 0.98366 | -0.3121 | 0.98369 | -0.31158 | 1.6764
28 | -0.009386 | -0.0023519 | 0.0093871 | 0.0023524 | 1.0075e-06 | 4.6994e-07 | 0.014082 | 0.014081 | 0.014082 | 0.99182 | -0.15707 | 0.99194 | -0.15481 | 3.8686
29 | -0.058365 | -0.014682 | 0.058416 | 0.014714 | 5.0642e-05 | 3.22e-05 | 0.089213 | 0.089213 | 0.089213 | 0.97371 | -0.50671 | 0.97463 | -0.48856 | 24.5091
30 | -0.0084206 | -0.0021104 | 0.0084209 | 0.0021105 | 3.3218e-07 | 1.4063e-07 | 0.012619 | 0.012619 | 0.012619 | 0.99297 | -0.13481 | 0.99302 | -0.13399 | 3.4667
31 | -0.01005 | -0.0025188 | 0.010051 | 0.0025191 | 7.3754e-07 | 3.5983e-07 | 0.01506 | 0.015059 | 0.01506 | 0.99302 | -0.13399 | 0.9931 | -0.13245 | 4.1372
32 | -0.058416 | -0.014714 | 0.058427 | 0.014721 | 1.0744e-05 | 6.8312e-06 | 0.089213 | 0.089213 | 0.089213 | 0.97463 | -0.48856 | 0.97482 | -0.48472 | 24.5091
33 | -0.01167 | -0.0029251 | 0.011671 | 0.0029254 | 6.1604e-07 | 3.2475e-07 | 0.017487 | 0.017486 | 0.017487 | 0.9931 | -0.13245 | 0.99315 | -0.13134 | 4.804
34 | -0.06774 | -0.017055 | 0.067815 | 0.017103 | 7.5066e-05 | 4.7809e-05 | 0.10343 | 0.10343 | 0.10343 | 0.97482 | -0.48472 | 0.976 | -0.46156 | 28.4147
35 | -0.01713 | -0.0042926 | 0.017134 | 0.0042951 | 4.1636e-06 | 2.4476e-06 | 0.025696 | 0.025696 | 0.025696 | 0.99196 | -0.15437 | 0.99223 | -0.14927 | 7.0594
36 | 0.011137 | 0.0027906 | -0.011136 | -0.0027904 | 2.371e-07 | 1.225e-07 | 0.016706 | 0.016706 | 0.016706 | 0.99196 | -0.15437 | 0.99194 | -0.15481 | 4.5895
37 | 0.0050111 | 0.0012556 | -0.0050108 | -0.0012556 | 2.8027e-07 | 8.449e-09 | 0.0075149 | 0.007515 | 0.007515 | 0.99223 | -0.14927 | 0.99217 | -0.15044 | 2.0645
38 | -0.022145 | -0.0055507 | 0.022146 | 0.0055513 | 9.1938e-07 | 5.5969e-07 | 0.033211 | 0.033211 | 0.033211 | 0.99223 | -0.14927 | 0.99227 | -0.14839 | 9.1239
39 | 0.0017494 | 0.00043806 | -0.0017493 | -0.00043842 | 8.4432e-08 | -3.6798e-07 | 0.0026242 | 0.0026243 | 0.0026243 | 0.99194 | -0.15481 | 0.99189 | -0.15583 | 0.72097
40 | 0.0034183 | 0.0008565 | -0.0034182 | -0.00085657 | 9.707e-08 | -6.5068e-08 | 0.0051266 | 0.0051266 | 0.0051266 | 0.99217 | -0.15044 | 0.99214 | -0.15104 | 1.4084
41 | -0.027556 | -0.0069071 | 0.027568 | 0.0069146 | 1.2122e-05 | 7.5132e-06 | 0.041323 | 0.041323 | 0.041323 | 0.99227 | -0.14839 | 0.99275 | -0.13917 | 11.3526
42 | 0.0018237 | 0.00045695 | -0.0018237 | -0.00045706 | 2.7093e-08 | -1.0737e-07 | 0.0027352 | 0.0027352 | 0.0027352 | 0.99214 | -0.15104 | 0.99212 | -0.15135 | 0.75144
43 | -0.029371 | -0.0073666 | 0.029376 | 0.0073696 | 4.8469e-06 | 3.0158e-06 | 0.044026 | 0.044026 | 0.044026 | 0.99275 | -0.13917 | 0.99293 | -0.1357 | 12.0951
44 | -0.033573 | -0.0084213 | 0.033581 | 0.0084264 | 8.1471e-06 | 5.1031e-06 | 0.050315 | 0.050315 | 0.050315 | 0.99293 | -0.1357 | 0.99319 | -0.13062 | 13.8229
45 | -0.028935 | -0.0072532 | 0.028953 | 0.0072647 | 1.8526e-05 | 1.1516e-05 | 0.043353 | 0.043353 | 0.043353 | 0.99315 | -0.13134 | 0.99385 | -0.11791 | 11.9102
46 | 0.017264 | 0.0043278 | -0.017261 | -0.0043262 | 2.7958e-06 | 1.6451e-06 | 0.025867 | 0.025867 | 0.025867 | 0.99315 | -0.13134 | 0.99298 | -0.13474 | 7.1062
47 | -0.036267 | -0.0090977 | 0.036273 | 0.0091013 | 5.7348e-06 | 3.603e-06 | 0.054303 | 0.054303 | 0.054303 | 0.99385 | -0.11791 | 0.99402 | -0.11459 | 14.9185
48 | 0.0073137 | 0.0018329 | -0.0073132 | -0.0018327 | 5.116e-07 | 1.8e-07 | 0.01095 | 0.01095 | 0.01095 | 0.99385 | -0.11791 | 0.99377 | -0.11938 | 3.0083
49 | 0.015617 | 0.0039142 | -0.015617 | -0.0039141 | 7.4967e-08 | 4.3258e-08 | 0.023403 | 0.023403 | 0.023403 | 0.99298 | -0.13474 | 0.99297 | -0.13484 | 6.4295
50 | -0.076023 | -0.019085 | 0.076141 | 0.019161 | 0.0001185 | 7.5525e-05 | 0.11381 | 0.11381 | 0.11381 | 0.99402 | -0.11459 | 0.99571 | -0.08197 | 31.2678
51 | 0.03975 | 0.009984 | -0.039719 | -0.0099648 | 3.0367e-05 | 1.9138e-05 | 0.059512 | 0.059512 | 0.059512 | 0.99402 | -0.11459 | 0.99319 | -0.13062 | 16.3494
52 | 0.0056965 | 0.0014276 | -0.0056965 | -0.0014276 | 9.1697e-09 | 1.5142e-09 | 0.0085296 | 0.0085296 | 0.0085296 | 0.99377 | -0.11938 | 0.99377 | -0.11941 | 2.3433
53 | 0.0074344 | 0.0018633 | -0.0074338 | -0.0018631 | 5.923e-07 | 2.1448e-07 | 0.011141 | 0.011141 | 0.011141 | 0.99297 | -0.13484 | 0.99289 | -0.13651 | 3.0607
54 | -0.075888 | -0.019186 | 0.075893 | 0.019189 | 5.1748e-06 | 3.2989e-06 | 0.11548 | 0.11548 | 0.11548 | 0.97839 | -0.41486 | 0.97847 | -0.41344 | 31.7241
55 | 0.073866 | 0.018679 | -0.073833 | -0.018658 | 3.3672e-05 | 2.1461e-05 | 0.1124 | 0.1124 | 0.1124 | 0.97839 | -0.41486 | 0.97791 | -0.42437 | 30.8795
56 | -0.081577 | -0.020614 | 0.081686 | 0.020683 | 0.00010837 | 6.9121e-05 | 0.12412 | 0.12412 | 0.12412 | 0.97847 | -0.41344 | 0.97988 | -0.38577 | 34.099
57 | 0.067936 | 0.01718 | -0.067815 | -0.017103 | 0.00012097 | 7.7044e-05 | 0.10343 | 0.10343 | 0.10343 | 0.97791 | -0.42437 | 0.976 | -0.46156 | 28.4147
58 | -0.089528 | -0.022648 | 0.089548 | 0.022661 | 2.0239e-05 | 1.2917e-05 | 0.13603 | 0.13603 | 0.13603 | 0.97988 | -0.38577 | 0.98013 | -0.38106 | 37.3709
59 | -0.095408 | -0.02413 | 0.095549 | 0.02422 | 0.00014146 | 9.0309e-05 | 0.14493 | 0.14493 | 0.14493 | 0.98013 | -0.38106 | 0.98171 | -0.3502 | 39.8148
60 | -0.097622 | -0.02474 | 0.097662 | 0.024765 | 3.9771e-05 | 2.5392e-05 | 0.14807 | 0.14807 | 0.14807 | 0.98171 | -0.3502 | 0.98215 | -0.34173 | 40.6778
61 | -0.012599 | -0.00316 | 0.012601 | 0.0031607 | 1.3207e-06 | 7.2003e-07 | 0.018979 | 0.018979 | 0.018979 | 0.98787 | -0.23145 | 0.98799 | -0.22925 | 5.2141
62 | 0.012599 | 0.00316 | -0.012591 | -0.0031556 | 8.0869e-06 | 4.4097e-06 | 0.018979 | 0.018979 | 0.018979 | 0.98787 | -0.23145 | 0.98718 | -0.24492 | 5.2141
63 | -0.018773 | -0.0047077 | 0.018773 | 0.0047079 | 4.1284e-07 | 2.4659e-07 | 0.028275 | 0.028275 | 0.028275 | 0.98799 | -0.22925 | 0.98801 | -0.22878 | 7.7679
64 | 0.0075391 | 0.0018896 | -0.0075375 | -0.0018889 | 1.6315e-06 | 6.1355e-07 | 0.011364 | 0.011364 | 0.011364 | 0.98718 | -0.24492 | 0.98695 | -0.24946 | 3.122
65 | 0.0050522 | 0.001266 | -0.0050514 | -0.001266 | 8.0308e-07 | 4.1944e-08 | 0.0076153 | 0.0076155 | 0.0076155 | 0.98718 | -0.24492 | 0.98701 | -0.24826 | 2.0922
66 | 0.0024924 | 0.00062453 | -0.0024924 | -0.00062465 | 6.6164e-08 | -1.1732e-07 | 0.0037578 | 0.0037578 | 0.0037578 | 0.98695 | -0.24946 | 0.98692 | -0.25002 | 1.0324
67 | 0.008181 | 0.0020506 | -0.0081793 | -0.0020499 | 1.7108e-06 | 7.1614e-07 | 0.01237 | 0.01237 | 0.01237 | 0.98414 | -0.30334 | 0.98392 | -0.30773 | 3.3983
68 | -0.008181 | -0.0020506 | 0.0081842 | 0.002052 | 3.2333e-06 | 1.353e-06 | 0.01237 | 0.012369 | 0.01237 | 0.98414 | -0.30334 | 0.98457 | -0.29505 | 3.3983
69 | -0.013036 | -0.003268 | 0.01304 | 0.0032699 | 3.3532e-06 | 1.853e-06 | 0.019703 | 0.019702 | 0.019703 | 0.98457 | -0.29505 | 0.98484 | -0.28965 | 5.4128
70 | 0.0015019 | 0.00037616 | -0.0015018 | -0.0003764 | 3.9035e-08 | -2.3637e-07 | 0.0022601 | 0.0022602 | 0.0022602 | 0.98877 | -0.21404 | 0.98874 | -0.21459 | 0.62094
71 | 0.001077 | 0.00026978 | -0.0010769 | -0.00026991 | 1.027e-08 | -1.2715e-07 | 0.0016207 | 0.0016207 | 0.0016207 | 0.98877 | -0.21404 | 0.98876 | -0.21424 | 0.44526
72 | -0.0040501 | -0.0010145 | 0.0040504 | 0.0010144 | 3.202e-07 | -8.9927e-08 | 0.0060949 | 0.0060948 | 0.0060949 | 0.98877 | -0.21404 | 0.98885 | -0.21238 | 1.6744
73 | 0.0014713 | 0.00036857 | -0.0014712 | -0.00036861 | 6.2961e-09 | -3.99e-08 | 0.0022141 | 0.0022141 | 0.0022141 | 0.98877 | -0.21404 | 0.98876 | -0.21413 | 0.60826
74 | 0.0014665 | 0.00036743 | -0.0014665 | -0.00036753 | 1.5346e-08 | -9.7987e-08 | 0.0022067 | 0.0022067 | 0.0022067 | 0.98885 | -0.21238 | 0.98884 | -0.2126 | 0.60624
75 | -0.0055169 | -0.0013818 | 0.0055172 | 0.0013819 | 3.3249e-07 | 4.7733e-08 | 0.0083015 | 0.0083014 | 0.0083015 | 0.98885 | -0.21238 | 0.98892 | -0.21111 | 2.2806
76 | 0.0014712 | 0.00036861 | -0.0014712 | -0.00036872 | 1.8746e-08 | -1.1879e-07 | 0.0022141 | 0.0022141 | 0.0022141 | 0.98876 | -0.21413 | 0.98875 | -0.2144 | 0.60827
77 | -0.014692 | -0.0036844 | 0.014696 | 0.0036868 | 4.2331e-06 | 2.4319e-06 | 0.022479 | 0.022479 | 0.022479 | 0.97257 | -0.52903 | 0.97287 | -0.52299 | 6.1757
78 | 0.014692 | 0.0036844 | -0.014685 | -0.0036804 | 6.9219e-06 | 3.977e-06 | 0.022479 | 0.02248 | 0.02248 | 0.97257 | -0.52903 | 0.97207 | -0.53892 | 6.1757
79 | 0.016036 | 0.0040214 | -0.016034 | -0.00402 | 2.4063e-06 | 1.4076e-06 | 0.024529 | 0.024529 | 0.024529 | 0.97287 | -0.52299 | 0.97271 | -0.52614 | 6.7386
80 | -0.030733 | -0.0077083 | 0.030761 | 0.0077259 | 2.8166e-05 | 1.7604e-05 | 0.047008 | 0.047008 | 0.047008 | 0.97287 | -0.52299 | 0.97385 | -0.50378 | 12.9143
81 | 0.010385 | 0.0026031 | -0.010383 | -0.0026022 | 1.889e-06 | 9.4223e-07 | 0.015595 | 0.015595 | 0.015595 | 0.99086 | -0.17412 | 0.99066 | -0.17794 | 4.2844
82 | -0.010385 | -0.0026031 | 0.010387 | 0.0026044 | 2.6754e-06 | 1.3343e-06 | 0.015595 | 0.015595 | 0.015595 | 0.99086 | -0.17412 | 0.99114 | -0.16872 | 4.2844
83 | -0.010387 | -0.0026044 | 0.010389 | 0.0026054 | 2.01e-06 | 1.0023e-06 | 0.015595 | 0.015595 | 0.015595 | 0.99114 | -0.16872 | 0.99135 | -0.16466 | 4.2844
84 | 0.18734 | 0.047654 | -0.1871 | -0.047502 | 0.00023986 | 0.00015185 | 0.28168 | 0.28168 | 0.28168 | 0.99053 | -0.18012 | 0.98915 | -0.20672 | 19.3459
85 | -0.18734 | -0.047654 | 0.18749 | 0.047748 | 0.00014838 | 9.3938e-05 | 0.28168 | 0.28168 | 0.28168 | 0.99053 | -0.18012 | 0.99139 | -0.16369 | 19.3459
86 | 0.17942 | 0.045578 | -0.17938 | -0.045554 | 3.7918e-05 | 2.3983e-05 | 0.27013 | 0.27013 | 0.27013 | 0.98915 | -0.20672 | 0.98892 | -0.21111 | 18.5526
87 | 0.0076785 | 0.0019245 | -0.0076777 | -0.0019242 | 7.822e-07 | 2.9997e-07 | 0.011551 | 0.011551 | 0.011551 | 0.98915 | -0.20672 | 0.98904 | -0.20886 | 3.1734
88 | -0.19879 | -0.050581 | 0.1989 | 0.05065 | 0.00010908 | 6.914e-05 | 0.29864 | 0.29864 | 0.29864 | 0.99139 | -0.16369 | 0.99198 | -0.15231 | 20.5111
89 | 0.15279 | 0.038882 | -0.15269 | -0.03882 | 9.7975e-05 | 6.1692e-05 | 0.23011 | 0.23011 | 0.23011 | 0.98892 | -0.21111 | 0.98823 | -0.22443 | 15.8045
90 | 0.021073 | 0.00529 | -0.021068 | -0.005287 | 5.0282e-06 | 3.047e-06 | 0.031712 | 0.031712 | 0.031712 | 0.98892 | -0.21111 | 0.98866 | -0.21612 | 8.7121
91 | -0.016528 | -0.0041438 | 0.016531 | 0.0041457 | 3.263e-06 | 1.906e-06 | 0.024808 | 0.024808 | 0.024808 | 0.99135 | -0.16466 | 0.99156 | -0.16052 | 6.8155
92 | -0.016531 | -0.0041457 | 0.016537 | 0.0041495 | 6.4643e-06 | 3.7757e-06 | 0.024808 | 0.024808 | 0.024808 | 0.99156 | -0.16052 | 0.99198 | -0.15231 | 6.8155
93 | -0.21544 | -0.054799 | 0.21554 | 0.054865 | 0.00010349 | 6.5687e-05 | 0.32345 | 0.32345 | 0.32345 | 0.99198 | -0.15231 | 0.9925 | -0.14235 | 22.215
94 | -0.10272 | -0.026032 | 0.10284 | 0.026111 | 0.00012338 | 7.8789e-05 | 0.15573 | 0.15573 | 0.15573 | 0.98215 | -0.34173 | 0.98344 | -0.31676 | 42.7824
95 | -0.10505 | -0.026665 | 0.10513 | 0.026716 | 7.9631e-05 | 5.0857e-05 | 0.15907 | 0.15907 | 0.15907 | 0.98344 | -0.31676 | 0.98425 | -0.30102 | 43.7015
96 | -0.10706 | -0.027198 | 0.10711 | 0.027235 | 5.864e-05 | 3.7454e-05 | 0.16198 | 0.16198 | 0.16198 | 0.98425 | -0.30102 | 0.98484 | -0.28965 | 44.5002
97 | -0.12015 | -0.030505 | 0.12024 | 0.03056 | 8.5194e-05 | 5.4437e-05 | 0.18168 | 0.18168 | 0.18168 | 0.98484 | -0.28965 | 0.9856 | -0.27492 | 49.9129
98 | -0.12415 | -0.031539 | 0.12428 | 0.031623 | 0.00013228 | 8.3509e-05 | 0.18758 | 0.18758 | 0.18758 | 0.9856 | -0.27492 | 0.98675 | -0.25281 | 17.1779
99 | -0.0039597 | -0.00099207 | 0.00396 | 0.000992 | 2.5638e-07 | -6.6722e-08 | 0.0060607 | 0.0060606 | 0.0060607 | 0.97217 | -0.53687 | 0.97224 | -0.53552 | 1.665
100 | -0.0047977 | -0.001202 | 0.004798 | 0.001202 | 2.8941e-07 | 7.7006e-09 | 0.0073428 | 0.0073427 | 0.0073428 | 0.97224 | -0.53552 | 0.9723 | -0.53425 | 2.0172
101 | 0.0078705 | 0.0019728 | -0.00787 | -0.0019726 | 5.1647e-07 | 2.1282e-07 | 0.012045 | 0.012045 | 0.012045 | 0.9723 | -0.53425 | 0.97223 | -0.53563 | 3.3091
102 | -0.012669 | -0.0031748 | 0.012669 | 0.0031751 | 5.8307e-07 | 3.2186e-07 | 0.019388 | 0.019388 | 0.019388 | 0.9723 | -0.53425 | 0.97235 | -0.53328 | 5.3263
103 | 0.15149 | 0.03852 | -0.15146 | -0.038498 | 3.4573e-05 | 2.1764e-05 | 0.22831 | 0.22831 | 0.22831 | 0.98823 | -0.22443 | 0.98798 | -0.22916 | 15.6806
104 | 0.018785 | 0.0047147 | -0.018775 | -0.0047086 | 1.0201e-05 | 6.0925e-06 | 0.028275 | 0.028275 | 0.028275 | 0.98866 | -0.21612 | 0.98807 | -0.22751 | 7.7679
105 | 0.00787 | 0.0019726 | -0.0078686 | -0.0019721 | 1.3797e-06 | 5.6862e-07 | 0.012045 | 0.012045 | 0.012045 | 0.97223 | -0.53563 | 0.97205 | -0.53931 | 3.3092
106 | 0.0030765 | 0.00077072 | -0.0030764 | -0.00077082 | 1.0434e-07 | -9.8409e-08 | 0.0046388 | 0.0046389 | 0.0046389 | 0.98683 | -0.25089 | 0.98679 | -0.2516 | 1.2744
107 | -0.12068 | -0.030684 | 0.12069 | 0.03069 | 1.0648e-05 | 6.8037e-06 | 0.18213 | 0.18213 | 0.18213 | 0.98683 | -0.25089 | 0.98692 | -0.24906 | 50.0354
108 | 0.0020802 | 0.00052116 | -0.0020802 | -0.00052125 | 2.9801e-08 | -8.4106e-08 | 0.0031367 | 0.0031368 | 0.0031368 | 0.98679 | -0.2516 | 0.98677 | -0.2519 | 0.86175
109 | -0.12291 | -0.031247 | 0.12308 | 0.031355 | 0.00016861 | 0.00010774 | 0.18548 | 0.18548 | 0.18548 | 0.98692 | -0.24906 | 0.9884 | -0.22062 | 50.9563
110 | 0.0022233 | 0.000557 | -0.0022232 | -0.00055718 | 7.5823e-08 | -1.8141e-07 | 0.003352 | 0.0033521 | 0.0033521 | 0.98692 | -0.24906 | 0.98688 | -0.24977 | 0.92091
111 | 0.0023188 | 0.0005809 | -0.0023187 | -0.00058109 | 9.0058e-08 | -1.9035e-07 | 0.0035068 | 0.0035069 | 0.0035069 | 0.98388 | -0.30771 | 0.98384 | -0.30852 | 0.96344
112 | 0.008512 | 0.0021319 | -0.0085114 | -0.0021317 | 5.3771e-07 | 2.343e-07 | 0.012874 | 0.012874 | 0.012874 | 0.98378 | -0.30984 | 0.98371 | -0.31117 | 3.5369
113 | 0.0021704 | 0.00054375 | -0.0021703 | -0.00054393 | 7.1376e-08 | -1.7857e-07 | 0.0032827 | 0.0032828 | 0.0032828 | 0.98378 | -0.30984 | 0.98374 | -0.31054 | 0.90187
114 | 0.22713 | 0.05788 | -0.22685 | -0.0577 | 0.00028281 | 0.00017965 | 0.34041 | 0.34041 | 0.34041 | 0.99385 | -0.11651 | 0.9925 | -0.14235 | 23.3798
115 | -0.22713 | -0.05788 | 0.22742 | 0.058061 | 0.0002852 | 0.00018117 | 0.34041 | 0.34041 | 0.34041 | 0.99385 | -0.11651 | 0.99522 | -0.090527 | 23.3797
116 | 0.13948 | 0.035783 | -0.1393 | -0.03567 | 0.00017697 | 0.00011312 | 0.20883 | 0.20883 | 0.20883 | 0.99522 | -0.090527 | 0.99384 | -0.11672 | 57.3722
117 | -0.3669 | -0.093844 | 0.36731 | 0.094109 | 0.00041503 | 0.00026486 | 0.54924 | 0.54924 | 0.54924 | 0.99522 | -0.090527 | 0.99645 | -0.067183 | 37.7227
118 | 0.014409 | 0.0036128 | -0.014404 | -0.00361 | 4.9026e-06 | 2.8038e-06 | 0.022043 | 0.022043 | 0.022043 | 0.97271 | -0.52614 | 0.97235 | -0.53328 | 6.0559
119 | -0.031911 | -0.0080142 | 0.031915 | 0.0080165 | 3.604e-06 | 2.2563e-06 | 0.048766 | 0.048766 | 0.048766 | 0.97385 | -0.50378 | 0.97397 | -0.50142 | 13.3972
120 | -0.018773 | -0.0047079 | 0.018775 | 0.0047086 | 1.1408e-06 | 6.8136e-07 | 0.028275 | 0.028275 | 0.028275 | 0.98801 | -0.22878 | 0.98807 | -0.22751 | 7.7679
121 | 0.13543 | 0.03442 | -0.13543 | -0.034416 | 6.8093e-06 | 4.2691e-06 | 0.20439 | 0.20439 | 0.20439 | 0.98681 | -0.25177 | 0.98675 | -0.25281 | 14.0378
122 | -0.14608 | -0.03709 | 0.1462 | 0.037165 | 0.00012004 | 7.5478e-05 | 0.22045 | 0.22045 | 0.22045 | 0.98681 | -0.25177 | 0.98769 | -0.23471 | 15.1409
123 | -0.14844 | -0.037726 | 0.14845 | 0.03773 | 7.7661e-06 | 4.8856e-06 | 0.22382 | 0.22382 | 0.22382 | 0.98769 | -0.23471 | 0.98775 | -0.23362 | 15.3722
124 | -0.15032 | -0.0382 | 0.15035 | 0.03822 | 3.2274e-05 | 2.0312e-05 | 0.22664 | 0.22664 | 0.22664 | 0.98775 | -0.23362 | 0.98798 | -0.22916 | 15.5658
125 | 0.0061584 | 0.0015424 | -0.0061583 | -0.0015423 | 1.1906e-07 | 2.975e-08 | 0.0093152 | 0.0093152 | 0.0093152 | 0.98371 | -0.31117 | 0.98369 | -0.31158 | 2.5591
126 | 0.002353 | 0.00058929 | -0.002353 | -0.00058943 | 6.7987e-08 | -1.3817e-07 | 0.0035592 | 0.0035592 | 0.0035592 | 0.98371 | -0.31117 | 0.98368 | -0.31178 | 0.97781
127 | 0.0021242 | 0.00053226 | -0.0021241 | -0.00053236 | 3.8234e-08 | -1.0089e-07 | 0.0032132 | 0.0032132 | 0.0032132 | 0.98369 | -0.31158 | 0.98367 | -0.31196 | 0.88275
128 | 0.0011836 | 0.00029636 | -0.0011836 | -0.00029663 | 2.7199e-08 | -2.6982e-07 | 0.0017904 | 0.0017905 | 0.0017905 | 0.98368 | -0.31178 | 0.98365 | -0.31226 | 0.49189
129 | 0.0013396 | 0.0003357 | -0.0013396 | -0.00033573 | 4.1548e-09 | -3.1616e-08 | 0.002026 | 0.002026 | 0.002026 | 0.98384 | -0.30852 | 0.98384 | -0.30859 | 0.55661
130 | 0.003283 | 0.00082267 | -0.0032829 | -0.00082276 | 1.1797e-07 | -9.3165e-08 | 0.0049157 | 0.0049158 | 0.0049158 | 0.99377 | -0.11941 | 0.99373 | -0.12017 | 1.3505
131 | -0.083257 | -0.020944 | 0.083355 | 0.021007 | 9.8294e-05 | 6.2688e-05 | 0.12445 | 0.12445 | 0.12445 | 0.99571 | -0.08197 | 0.997 | -0.05729 | 34.1893
132 | 0.007116 | 0.0017834 | -0.0071155 | -0.0017832 | 4.549e-07 | 1.5162e-07 | 0.010634 | 0.010634 | 0.010634 | 0.99571 | -0.08197 | 0.99564 | -0.083312 | 2.9215
133 | -0.084754 | -0.021357 | 0.08488 | 0.021437 | 0.0001257 | 8.0177e-05 | 0.12654 | 0.12654 | 0.12654 | 0.997 | -0.05729 | 0.99861 | -0.026336 | 34.7627
134 | 0.0057242 | 0.0014345 | -0.0057242 | -0.0014345 | 1.9981e-08 | 3.3197e-09 | 0.0085549 | 0.0085549 | 0.0085549 | 0.99564 | -0.083312 | 0.99564 | -0.083385 | 2.3502
135 | -0.36958 | -0.094679 | 0.36982 | 0.094832 | 0.00024016 | 0.00015327 | 0.55264 | 0.55264 | 0.55264 | 0.99645 | -0.067183 | 0.99715 | -0.053782 | 37.956
136 | -0.37313 | -0.09566 | 0.3735 | 0.095897 | 0.00037088 | 0.0002367 | 0.55757 | 0.55757 | 0.55757 | 0.99715 | -0.053782 | 0.99824 | -0.033304 | 38.2945
137 | -0.3735 | -0.095897 | 0.3736 | 0.095959 | 9.6879e-05 | 6.1828e-05 | 0.55757 | 0.55757 | 0.55757 | 0.99824 | -0.033304 | 0.99852 | -0.027962 | 38.2945
138 | 0.003129 | 0.00078409 | -0.0031289 | -0.00078418 | 9.4067e-08 | -8.7891e-08 | 0.0046849 | 0.0046849 | 0.0046849 | 0.99384 | -0.11672 | 0.99381 | -0.11735 | 1.2871
139 | 0.13178 | 0.033787 | -0.13148 | -0.033591 | 0.00030628 | 0.00019575 | 0.19758 | 0.19758 | 0.19758 | 0.99384 | -0.11672 | 0.99132 | -0.16477 | 54.2811
140 | 0.0043861 | 0.0010992 | -0.0043861 | -0.0010992 | 6.4782e-08 | -1.0445e-08 | 0.0065671 | 0.0065671 | 0.0065671 | 0.99384 | -0.11672 | 0.99382 | -0.11703 | 1.8041
141 | 0.0021181 | 0.00053059 | -0.002118 | -0.00053083 | 8.3219e-08 | -2.3808e-07 | 0.0031564 | 0.0031565 | 0.0031565 | 0.99852 | -0.027962 | 0.99848 | -0.028787 | 0.86717
142 | -0.37571 | -0.096489 | 0.37584 | 0.096568 | 0.00012333 | 7.8711e-05 | 0.56072 | 0.56072 | 0.56072 | 0.99852 | -0.027962 | 0.99888 | -0.021203 | 38.5113
143 | 0.0043861 | 0.0010992 | -0.0043859 | -0.0010992 | 1.0874e-07 | -1.7529e-08 | 0.0065671 | 0.0065671 | 0.0065671 | 0.99382 | -0.11703 | 0.9938 | -0.11755 | 1.8041
144 | 0.0031944 | 0.00080048 | -0.0031943 | -0.00080056 | 9.5382e-08 | -8.158e-08 | 0.0047949 | 0.0047949 | 0.0047949 | 0.99132 | -0.16477 | 0.99128 | -0.1654 | 1.3173
145 | 0.12828 | 0.032791 | -0.1281 | -0.032675 | 0.00018161 | 0.00011606 | 0.19279 | 0.19279 | 0.19279 | 0.99132 | -0.16477 | 0.98978 | -0.19408 | 52.9639
146 | -0.46714 | -0.11962 | 0.46762 | 0.11993 | 0.00048035 | 0.00030687 | 0.69679 | 0.69679 | 0.69679 | 0.99888 | -0.021203 | 1 | 0 | 47.8567
147 | 0.089081 | 0.022499 | -0.089059 | -0.022485 | 2.1905e-05 | 1.3976e-05 | 0.13276 | 0.13276 | 0.13276 | 0.99888 | -0.021203 | 0.99861 | -0.026336 | 36.4736
148 | 0.0022196 | 0.00055573 | -0.0022194 | -0.00055622 | 1.9316e-07 | -4.9308e-07 | 0.0033063 | 0.0033065 | 0.0033065 | 0.99888 | -0.021203 | 0.99878 | -0.023031 | 0.90837
149 | 0.0037115 | 0.00093013 | -0.0037114 | -0.00093017 | 9.0169e-08 | -4.155e-08 | 0.0055798 | 0.0055798 | 0.0055798 | 0.98978 | -0.19408 | 0.98976 | -0.19459 | 1.5329
150 | 0.12439 | 0.031744 | -0.12423 | -0.031643 | 0.00015926 | 0.00010177 | 0.18721 | 0.18721 | 0.18721 | 0.98978 | -0.19408 | 0.9884 | -0.22062 | 51.431
151 | 0.0011479 | 0.00028755 | -0.0011479 | -0.00028768 | 1.2635e-08 | -1.3652e-07 | 0.0017281 | 0.0017281 | 0.0017281 | 0.9884 | -0.22062 | 0.98839 | -0.22085 | 0.47475
152 | 0.0034764 | 0.00087116 | -0.0034763 | -0.00087125 | 1.2925e-07 | -8.3321e-08 | 0.0051956 | 0.0051957 | 0.0051957 | 0.99564 | -0.083385 | 0.9956 | -0.084166 | 1.4274
153 | 0.00091044 | 0.00022808 | -0.00091043 | -0.00022818 | 5.2754e-09 | -9.1967e-08 | 0.0013729 | 0.0013729 | 0.0013729 | 0.98677 | -0.2519 | 0.98677 | -0.25202 | 0.37717

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47216 | 0.12065

## res_load
| p_mw | q_mvar
0 | 0.016721 | 0.0041906
1 | 0.014389 | 0.0036062
2 | 0.0025556 | 0.00064049
3 | 0.0058575 | 0.001468
4 | 0.0038396 | 0.0009623
5 | 0.0012443 | 0.00031186
6 | 0.001637 | 0.00041027
7 | 0.0054217 | 0.0013588
8 | 0.006968 | 0.0017463
9 | 0.033508 | 0.0083978
10 | 0.0017972 | 0.00045043
11 | 0.0022124 | 0.00055449
12 | 0.0017471 | 0.00043786
13 | 0.0012812 | 0.0003211
14 | 0.0023269 | 0.00058317
15 | 0.01173 | 0.0029399
16 | 0.0084206 | 0.0021104
17 | 0.0016289 | 0.00040825
18 | 0.0016198 | 0.00040596
19 | 0.0093136 | 0.0023342
20 | 0.0059934 | 0.0015021
21 | 0.0015925 | 0.00039912
22 | 0.0054097 | 0.0013558
23 | 0.0017493 | 0.00043842
24 | 0.0015945 | 0.00039961
25 | 0.0018033 | 0.00045196
26 | 0.0018237 | 0.00045706
27 | 0.0041966 | 0.0010518
28 | 0.0016438 | 0.00041199
29 | 0.0016167 | 0.00040519
30 | 0.0081829 | 0.0020508
31 | 0.0020215 | 0.00050663
32 | 0.0056844 | 0.0014246
33 | 0.0058963 | 0.0014778
34 | 0.0078427 | 0.0019656
35 | 0.0058595 | 0.0014685
36 | 0.0020727 | 0.00051947
37 | 0.0061723 | 0.0015469
38 | 0.0050451 | 0.0012644
39 | 0.0050514 | 0.001266
40 | 0.0081793 | 0.0020499
41 | 0.004852 | 0.001216
42 | 0.0015018 | 0.0003764
43 | 0.0010769 | 0.00026991
44 | 0.014685 | 0.0036804
45 | 0.010383 | 0.0026022
46 | 0.011304 | 0.002833
47 | 0.0014665 | 0.00036753
48 | 0.0014712 | 0.00036872
49 | 0.0061382 | 0.0015384
50 | 0.0050563 | 0.0012672
51 | 0.0022111 | 0.00055416
52 | 0.0019232 | 0.00048199
53 | 0.0039076 | 0.00097933
54 | 0.00083776 | 0.00020996
55 | 0.0076777 | 0.0019242
56 | 0.0011977 | 0.00030018
57 | 0.0022835 | 0.00057231
58 | 0.0078686 | 0.0019721
59 | 0.00099616 | 0.00024966
60 | 0.0024275 | 0.0006084
61 | 0.011312 | 0.0028351
62 | 0.0016247 | 0.00040719
63 | 0.0011506 | 0.00028837
64 | 0.0024924 | 0.00062465
65 | 0.010651 | 0.0026694
66 | 0.011146 | 0.0027936
67 | 0.0022356 | 0.0005603
68 | 0.0018717 | 0.00046908
69 | 0.0011096 | 0.00027809
70 | 0.0021703 | 0.00054393
71 | 0.0011693 | 0.00029306
72 | 0.0021241 | 0.00053236
73 | 0.0011836 | 0.00029663
74 | 0.00097913 | 0.00024539
75 | 0.0024135 | 0.00060489
76 | 0.0032829 | 0.00082276
77 | 0.0061382 | 0.0015384
78 | 0.0013986 | 0.00035052
79 | 0.0013913 | 0.0003487
80 | 0.0022744 | 0.00057002
81 | 0.0033033 | 0.00082788
82 | 0.0043859 | 0.0010992
83 | 0.0031289 | 0.00078418
84 | 0.002118 | 0.00053083
85 | 0.0041795 | 0.0010475
86 | 0.0037114 | 0.00093017
87 | 0.0031943 | 0.00080056
88 | 0.0022477 | 0.00056333
89 | 0.0034763 | 0.00087125
90 | 0.030023 | 0.0075245
91 | 0.0017352 | 0.00043489
92 | 0.0011697 | 0.00029316
93 | 0.0022232 | 0.00055718
94 | 0.00091043 | 0.00022818
95 | 0.0013396 | 0.00033573
96 | 0.0022194 | 0.00055622
97 | 0.0028914 | 0.00072466
98 | 0.0074338 | 0.0018631
99 | 0.0011479 | 0.00028768
100 | 0.0015083 | 0.00037802

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1