## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-899_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-899_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-899_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-899_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-899_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-899_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-899_0_3_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_261-899_0_3_node_38 | 0.4 | n |  | TRUE
8 | bus_LV_261-899_0_3_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_261-899_0_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_261-899_0_3_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_261-899_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_261-899_0_3_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_261-899_0_3_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_261-899_0_3_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_261-899_0_3_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_261-899_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_261-899_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_261-899_0_3_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_261-899_0_3_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_261-899_0_3_node_41 | 0.4 | n |  | TRUE
21 | bus_LV_261-899_0_3_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_261-899_0_3_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_261-899_0_3_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_261-899_0_3_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_261-899_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_261-899_0_3_node_45 | 0.4 | n |  | TRUE
27 | bus_LV_261-899_0_3_node_44 | 0.4 | n |  | TRUE
28 | bus_LV_261-899_0_3_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_261-899_0_3_node_46 | 0.4 | n |  | TRUE
30 | bus_LV_261-899_0_3_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_261-899_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_261-899_0_3_node_14 | 0.4 | n |  | TRUE
33 | bus_LV_261-899_0_3_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_261-899_0_3_node_13 | 0.4 | n |  | TRUE
35 | bus_LV_261-899_0_3_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_261-899_0_3_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_261-899_0_3_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_261-899_0_3_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_261-899_0_3_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_261-899_0_3_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_261-899_0_3_node_43 | 0.4 | n |  | TRUE
42 | bus_LV_261-899_0_3_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_261-899_0_3_node_42 | 0.4 | n |  | TRUE
44 | bus_MV_548_0_node_113 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-899_0_3_load_0 | 0 | 0.010783 | 0.0027024 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-899_0_3_load_1 | 1 | 0.021192 | 0.0053111 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-899_0_3_load_4 | 4 | 0.010883 | 0.0027276 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-899_0_3_load_5 | 5 | 0.0025755 | 0.00064547 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-899_0_3_load_38 | 7 | 0.023468 | 0.0058817 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-899_0_3_load_27 | 8 | 0.0044794 | 0.0011226 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-899_0_3_load_12 | 10 | 0.0038965 | 0.00097655 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-899_0_3_load_6 | 11 | 0.013395 | 0.0033571 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-899_0_3_load_39 | 12 | 0.066245 | 0.016603 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-899_0_3_load_20 | 14 | 0.010256 | 0.0025703 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-899_0_3_load_9 | 16 | 0.0084885 | 0.0021274 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-899_0_3_load_41 | 20 | 0.011573 | 0.0029004 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-899_0_3_load_40 | 21 | 0.0091604 | 0.0022958 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-899_0_3_load_28 | 22 | 0.0036395 | 0.00091214 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-899_0_3_load_32 | 23 | 0.039328 | 0.0098564 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-899_0_3_load_45 | 26 | 0.0038286 | 0.00095954 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-899_0_3_load_44 | 27 | 0.0037195 | 0.00093219 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-899_0_3_load_46 | 29 | 0.0030438 | 0.00076285 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-899_0_3_load_26 | 30 | 0.012014 | 0.0030111 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-899_0_3_load_24 | 31 | 0.010874 | 0.0027253 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-899_0_3_load_29 | 33 | 0.0067001 | 0.0016792 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-899_0_3_load_13 | 34 | 0.044879 | 0.011248 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-899_0_3_load_22 | 35 | 0.00719 | 0.001802 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-899_0_3_load_25 | 36 | 0.022887 | 0.0057361 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-899_0_3_load_21 | 37 | 0.0057549 | 0.0014423 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-899_0_3_load_30 | 38 | 0.0066725 | 0.0016723 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-899_0_3_load_43 | 41 | 0.0033581 | 0.00084163 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-899_0_3_load_36 | 42 | 0.016994 | 0.0042591 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-899_0_3_load_42 | 43 | 0.0032467 | 0.00081369 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-899_0_3_line_0 |  | 0 | 1 | 0.0075014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_261-899_0_3_line_1 |  | 0 | 2 | 0.025928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_261-899_0_3_line_2 |  | 1 | 3 | 0.024707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_261-899_0_3_line_3 |  | 2 | 4 | 0.013517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-899_0_3_line_4 |  | 2 | 5 | 0.0026681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-899_0_3_line_5 |  | 3 | 6 | 0.01604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-899_0_3_line_6 |  | 3 | 7 | 0.0027928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_261-899_0_3_line_7 |  | 4 | 8 | 0.00048245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-899_0_3_line_8 |  | 5 | 9 | 0.01728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-899_0_3_line_9 |  | 6 | 10 | 0.032014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-899_0_3_line_10 |  | 6 | 11 | 0.0086861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-899_0_3_line_11 |  | 7 | 12 | 0.012017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-899_0_3_line_12 |  | 9 | 13 | 0.072142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-899_0_3_line_13 |  | 9 | 14 | 0.013311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-899_0_3_line_14 |  | 10 | 19 | 0.029997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-899_0_3_line_15 |  | 11 | 15 | 0.031304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-899_0_3_line_16 |  | 13 | 29 | 0.023319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-899_0_3_line_17 |  | 14 | 37 | 0.029674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-899_0_3_line_18 |  | 15 | 16 | 0.0046462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-899_0_3_line_19 |  | 15 | 17 | 0.040261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-899_0_3_line_20 |  | 16 | 18 | 0.024503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-899_0_3_line_21 |  | 17 | 22 | 0.013571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-899_0_3_line_22 |  | 18 | 23 | 0.022348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-899_0_3_line_23 |  | 18 | 24 | 0.086312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-899_0_3_line_24 |  | 19 | 20 | 0.003743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-899_0_3_line_25 |  | 19 | 21 | 0.018955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-899_0_3_line_26 |  | 22 | 33 | 0.0026624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-899_0_3_line_27 |  | 24 | 42 | 0.014022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-899_0_3_line_28 |  | 25 | 26 | 0.025312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-899_0_3_line_29 |  | 25 | 27 | 0.014831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-899_0_3_line_30 |  | 25 | 28 | 0.010048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-899_0_3_line_31 |  | 28 | 30 | 0.02343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-899_0_3_line_32 |  | 28 | 31 | 0.01129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-899_0_3_line_33 |  | 28 | 32 | 0.050444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-899_0_3_line_34 |  | 30 | 35 | 0.014958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-899_0_3_line_35 |  | 31 | 36 | 0.0070633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-899_0_3_line_36 |  | 32 | 34 | 0.059662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-899_0_3_line_37 |  | 33 | 38 | 0.0071438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-899_0_3_line_38 |  | 35 | 37 | 0.0014341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-899_0_3_line_39 |  | 39 | 40 | 0.022221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-899_0_3_line_40 |  | 39 | 41 | 0.0071395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-899_0_3_line_41 |  | 40 | 42 | 0.0030106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-899_0_3_line_42 |  | 41 | 43 | 0.0018463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-899_0_3_trafo_39 | 0.63 MVA 20/0.4 kV | 44 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2684124.1881 | 1246836.6817 | 2684121.5218 | 1246838.2562 | 2684117.1893 | 1246837.4608
1 | 2684140.1246 | 1246857.134 | 2684124.1881 | 1246836.6817
2 | 2684098.8227 | 1246821.0883 | 2684105.5013 | 1246825.8421 | 2684106.8106 | 1246826.7391 | 2684117.1893 | 1246837.4608
3 | 2684140.1246 | 1246857.134 | 2684150.4046 | 1246848.3569
4 | 2684140.1246 | 1246857.134 | 2684141.7598 | 1246859.2423
5 | 2684109.4414 | 1246809.0411 | 2684098.8227 | 1246821.0883
6 | 2684098.8227 | 1246821.0883 | 2684096.9964 | 1246823.2011
7 | 2684150.7715 | 1246848.0436 | 2684150.4046 | 1246848.3569
8 | 2684152.3504 | 1246872.8968 | 2684141.7598 | 1246859.2423
9 | 2684109.4414 | 1246809.0411 | 2684118.93 | 1246810.0876 | 2684130.3531 | 1246808.4373 | 2684137.7885 | 1246805.6407 | 2684140.2126 | 1246803.9034
10 | 2684109.4414 | 1246809.0411 | 2684102.3769 | 1246803.9873
11 | 2684089.1376 | 1246832.2926 | 2684096.9964 | 1246823.2011
12 | 2684168.0852 | 1246827.7424 | 2684176.845 | 1246830.1018 | 2684179.3164 | 1246832.1495 | 2684187.5563 | 1246838.6712 | 2684182.9856 | 1246844.544 | 2684174.2161 | 1246854.0376 | 2684172.224 | 1246854.9434 | 2684165.5962 | 1246861.5097 | 2684152.3504 | 1246872.8968
13 | 2684152.3504 | 1246872.8968 | 2684142.2047 | 1246881.5133
14 | 2684145.8882 | 1246780.0034 | 2684144.2221 | 1246789.3422 | 2684149.1374 | 1246797.5068 | 2684140.2126 | 1246803.9034
15 | 2684076.9173 | 1246785.774 | 2684102.3769 | 1246803.9873
16 | 2684156.9288 | 1246817.5321 | 2684155.6898 | 1246817.003 | 2684153.7911 | 1246820.3786 | 2684153.5059 | 1246821.8423 | 2684154.1067 | 1246823.6855 | 2684155.8569 | 1246824.9223 | 2684159.461 | 1246825.4072 | 2684168.0852 | 1246827.7424
17 | 2684119.6085 | 1246900.7475 | 2684130.1755 | 1246891.7295 | 2684142.2047 | 1246881.5133
18 | 2684076.9173 | 1246785.774 | 2684072.9795 | 1246788.2399
19 | 2684111.0344 | 1246764.3975 | 2684100.6757 | 1246770.8887 | 2684076.9173 | 1246785.774
20 | 2684052.2139 | 1246801.2464 | 2684058.0524 | 1246797.5931 | 2684060.301 | 1246796.1795 | 2684072.9795 | 1246788.2399
21 | 2684111.0344 | 1246764.3975 | 2684104.1748 | 1246752.6875
22 | 2684052.2139 | 1246801.2464 | 2684033.2781 | 1246813.1145
23 | 2683997.9466 | 1246755.6774 | 2684008.8842 | 1246749.9058 | 2684008.048 | 1246753.4744 | 2684009.8432 | 1246763.2626 | 2684015.4884 | 1246775.3737 | 2684030.8134 | 1246779.8496 | 2684045.2808 | 1246789.9287 | 2684049.051 | 1246794.6856 | 2684050.1513 | 1246796.4692 | 2684052.2139 | 1246801.2464
24 | 2684145.8882 | 1246780.0034 | 2684146.7332 | 1246776.3571
25 | 2684145.8882 | 1246780.0034 | 2684161.3151 | 1246791.0173
26 | 2684104.1748 | 1246752.6875 | 2684102.8291 | 1246750.3903
27 | 2683997.9466 | 1246755.6774 | 2683994.6176 | 1246757.0979 | 2683992.1434 | 1246756.8405 | 2683989.3234 | 1246757.5233 | 2683987.331 | 1246759.5188 | 2683986.5691 | 1246761.5761
28 | 2684093.5335 | 1246934.041 | 2684112.8711 | 1246917.7088
29 | 2684093.5335 | 1246934.041 | 2684103.0752 | 1246945.3953
30 | 2684089.318 | 1246926.598 | 2684091.6302 | 1246929.2216 | 2684090.3762 | 1246930.2823 | 2684093.5335 | 1246934.041
31 | 2684089.318 | 1246926.598 | 2684107.14 | 1246911.3884
32 | 2684089.318 | 1246926.598 | 2684081.8543 | 1246918.1267
33 | 2684052.5728 | 1246936.2731 | 2684063.0193 | 1246948.5969 | 2684086.5371 | 1246928.7935 | 2684089.318 | 1246926.598
34 | 2684107.14 | 1246911.3884 | 2684118.5177 | 1246901.6784
35 | 2684077.1848 | 1246912.8269 | 2684081.8543 | 1246918.1267
36 | 2684052.5728 | 1246936.2731 | 2684069.4203 | 1246920.7227 | 2684044.1674 | 1246894.0437
37 | 2684099.2183 | 1246744.2262 | 2684102.8291 | 1246750.3903
38 | 2684119.6085 | 1246900.7475 | 2684118.5177 | 1246901.6784
39 | 2683968.4581 | 1246777.2424 | 2683968.7452 | 1246774.0441 | 2683973.9411 | 1246768.2912 | 2683983.8904 | 1246762.9503
40 | 2683968.4581 | 1246777.2424 | 2683961.6575 | 1246775.0688
41 | 2683983.8904 | 1246762.9503 | 2683986.5691 | 1246761.5761
42 | 2683960.343 | 1246773.9288 | 2683960.9227 | 1246774.8339 | 2683961.6575 | 1246775.0688

## bus_geodata
| x | y | coords
0 | 2684124.1881 | 1246836.6817
1 | 2684117.1893 | 1246837.4608
2 | 2684140.1246 | 1246857.134
3 | 2684098.8227 | 1246821.0883
4 | 2684150.4046 | 1246848.3569
5 | 2684141.7598 | 1246859.2423
6 | 2684109.4414 | 1246809.0411
7 | 2684096.9964 | 1246823.2011
8 | 2684150.7715 | 1246848.0437
9 | 2684152.3504 | 1246872.8968
10 | 2684140.2126 | 1246803.9034
11 | 2684102.3769 | 1246803.9873
12 | 2684089.1376 | 1246832.2926
13 | 2684168.0852 | 1246827.7424
14 | 2684142.2047 | 1246881.5133
15 | 2684076.9173 | 1246785.774
16 | 2684072.9795 | 1246788.2399
17 | 2684111.0344 | 1246764.3975
18 | 2684052.2139 | 1246801.2464
19 | 2684145.8882 | 1246780.0034
20 | 2684146.7332 | 1246776.3571
21 | 2684161.3151 | 1246791.0173
22 | 2684104.1748 | 1246752.6875
23 | 2684033.2781 | 1246813.1145
24 | 2683997.9466 | 1246755.6774
25 | 2684093.5335 | 1246934.041
26 | 2684112.8711 | 1246917.7088
27 | 2684103.0752 | 1246945.3953
28 | 2684089.318 | 1246926.598
29 | 2684156.9288 | 1246817.5321
30 | 2684107.14 | 1246911.3884
31 | 2684081.8543 | 1246918.1267
32 | 2684052.5728 | 1246936.2731
33 | 2684102.8291 | 1246750.3903
34 | 2684044.1674 | 1246894.0437
35 | 2684118.5177 | 1246901.6784
36 | 2684077.1848 | 1246912.8269
37 | 2684119.6085 | 1246900.7475
38 | 2684099.2183 | 1246744.2262
39 | 2683968.4581 | 1246777.2424
40 | 2683983.8904 | 1246762.9503
41 | 2683961.6575 | 1246775.0688
42 | 2683986.5691 | 1246761.5761
43 | 2683960.343 | 1246773.9288
44 | 2684098.8227 | 1246821.0883

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99688 | -0.059416 | 0.010783 | 0.0027024
1 | 0.99723 | -0.0527 | 0.021192 | 0.0053111
2 | 0.99518 | -0.091848 | 0 | 0
3 | 0.99855 | -0.027564 | 0 | 0
4 | 0.99499 | -0.095504 | 0.010883 | 0.0027276
5 | 0.99487 | -0.097815 | 0.0025755 | 0.00064547
6 | 0.9967 | -0.063088 | 0 | 0
7 | 0.99881 | -0.02267 | 0.023468 | 0.0058817
8 | 0.99499 | -0.095542 | 0.0044794 | 0.0011226
9 | 0.99289 | -0.13576 | 0 | 0
10 | 0.99598 | -0.076933 | 0.0038965 | 0.00097655
11 | 0.99589 | -0.078619 | 0.013395 | 0.0033571
12 | 1 | 0 | -0.32881 | -0.083106
13 | 0.99269 | -0.13965 | 0 | 0
14 | 0.9914 | -0.16438 | 0.010256 | 0.0025703
15 | 0.99336 | -0.12739 | 0 | 0
16 | 0.99305 | -0.13326 | 0.0084885 | 0.0021274
17 | 0.99273 | -0.1395 | 0 | 0
18 | 0.99164 | -0.16055 | 0 | 0
19 | 0.99541 | -0.087867 | 0 | 0
20 | 0.99537 | -0.088629 | 0.011573 | 0.0029004
21 | 0.99526 | -0.090922 | 0.0091604 | 0.0022958
22 | 0.99252 | -0.14358 | 0.0036395 | 0.00091214
23 | 0.99084 | -0.17614 | 0.039328 | 0.0098564
24 | 0.98977 | -0.19672 | 0 | 0
25 | 0.98493 | -0.28958 | 0 | 0
26 | 0.98484 | -0.29132 | 0.0038286 | 0.00095954
27 | 0.98488 | -0.29057 | 0.0037195 | 0.00093219
28 | 0.985 | -0.28821 | 0 | 0
29 | 0.99262 | -0.1409 | 0.0030438 | 0.00076285
30 | 0.98686 | -0.252 | 0.012014 | 0.0030111
31 | 0.98465 | -0.29506 | 0.010874 | 0.0027253
32 | 0.9829 | -0.32897 | 0 | 0
33 | 0.99249 | -0.14421 | 0.0067001 | 0.0016792
34 | 0.98043 | -0.3774 | 0.044879 | 0.011248
35 | 0.98822 | -0.22575 | 0.00719 | 0.001802
36 | 0.9845 | -0.29797 | 0.022887 | 0.0057361
37 | 0.98836 | -0.22305 | 0.0057549 | 0.0014423
38 | 0.99244 | -0.14506 | 0.0066725 | 0.0016723
39 | 0.98932 | -0.20558 | 0 | 0
40 | 0.98945 | -0.20297 | 0 | 0
41 | 0.98928 | -0.20642 | 0.0033581 | 0.00084163
42 | 0.98947 | -0.20261 | 0.016994 | 0.0042591
43 | 0.98927 | -0.20653 | 0.0032467 | 0.00081369
44 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.15464 | -0.039323 | 0.15469 | 0.039355 | 5.0047e-05 | 3.1736e-05 | 0.23103 | 0.23103 | 0.23103 | 0.99688 | -0.059416 | 0.99723 | -0.0527 | 21.1563
1 | 0.14386 | 0.036621 | -0.14363 | -0.036478 | 0.00022458 | 0.00014306 | 0.21493 | 0.21493 | 0.21493 | 0.99688 | -0.059416 | 0.99518 | -0.091848 | 29.5236
2 | -0.17588 | -0.044666 | 0.17609 | 0.044802 | 0.00021305 | 0.00013538 | 0.26265 | 0.26265 | 0.26265 | 0.99723 | -0.0527 | 0.99855 | -0.027564 | 24.0519
3 | 0.015365 | 0.0038517 | -0.015362 | -0.0038502 | 2.6756e-06 | 1.5368e-06 | 0.022975 | 0.022975 | 0.022975 | 0.99518 | -0.091848 | 0.99499 | -0.095504 | 6.3117
4 | 0.12827 | 0.032626 | -0.12823 | -0.032603 | 3.6867e-05 | 2.356e-05 | 0.19196 | 0.19196 | 0.19196 | 0.99518 | -0.091848 | 0.99487 | -0.097815 | 52.7355
5 | 0.12717 | 0.032149 | -0.12696 | -0.032011 | 0.00021625 | 0.00013819 | 0.18961 | 0.18961 | 0.18961 | 0.99855 | -0.027564 | 0.9967 | -0.063088 | 52.09
6 | -0.30327 | -0.07695 | 0.30334 | 0.076996 | 7.1402e-05 | 4.5587e-05 | 0.45225 | 0.45225 | 0.45225 | 0.99855 | -0.027564 | 0.99881 | -0.02267 | 41.4152
7 | 0.0044794 | 0.0011226 | -0.0044794 | -0.0011226 | 8.1188e-09 | -1.0704e-09 | 0.0066989 | 0.0066989 | 0.0066989 | 0.99499 | -0.095504 | 0.99499 | -0.095542 | 1.8404
8 | 0.12565 | 0.031957 | -0.12543 | -0.031811 | 0.00022929 | 0.00014652 | 0.18811 | 0.18811 | 0.18811 | 0.99487 | -0.097815 | 0.99289 | -0.13576 | 51.6773
9 | 0.024658 | 0.0061901 | -0.024642 | -0.0061801 | 1.6273e-05 | 9.998e-06 | 0.036817 | 0.036817 | 0.036817 | 0.9967 | -0.063088 | 0.99598 | -0.076933 | 10.1146
10 | 0.1023 | 0.02582 | -0.10222 | -0.025772 | 7.6042e-05 | 4.8553e-05 | 0.15279 | 0.15279 | 0.15279 | 0.9967 | -0.063088 | 0.99589 | -0.078619 | 41.9754
11 | -0.32681 | -0.082878 | 0.32716 | 0.083105 | 0.00035658 | 0.00022774 | 0.48722 | 0.48722 | 0.48722 | 0.99881 | -0.02267 | 1 | 0 | 44.617
12 | 0.0030445 | 0.00076209 | -0.003044 | -0.00076266 | 5.6318e-07 | -5.7241e-07 | 0.0045624 | 0.0045628 | 0.0045628 | 0.99289 | -0.13576 | 0.99269 | -0.13965 | 1.2535
13 | 0.12238 | 0.031049 | -0.12221 | -0.030941 | 0.00016816 | 0.00010745 | 0.18354 | 0.18354 | 0.18354 | 0.99289 | -0.13576 | 0.9914 | -0.16438 | 50.4239
14 | 0.020746 | 0.0052035 | -0.020735 | -0.005197 | 1.0807e-05 | 6.5265e-06 | 0.030996 | 0.030996 | 0.030996 | 0.99598 | -0.076933 | 0.99541 | -0.087867 | 8.5154
15 | 0.088828 | 0.022415 | -0.088621 | -0.022283 | 0.00020695 | 0.00013204 | 0.13278 | 0.13278 | 0.13278 | 0.99589 | -0.078619 | 0.99336 | -0.12739 | 36.4771
16 | 0.003044 | 0.00076266 | -0.0030438 | -0.00076285 | 1.8206e-07 | -1.8493e-07 | 0.0045628 | 0.0045629 | 0.0045629 | 0.99269 | -0.13965 | 0.99262 | -0.1409 | 1.2535
17 | 0.11196 | 0.028371 | -0.11164 | -0.02817 | 0.00031463 | 0.00020098 | 0.16815 | 0.16815 | 0.16815 | 0.9914 | -0.16438 | 0.98836 | -0.22305 | 46.1952
18 | 0.071595 | 0.018011 | -0.071575 | -0.017998 | 2.0049e-05 | 1.2771e-05 | 0.10727 | 0.10727 | 0.10727 | 0.99336 | -0.12739 | 0.99305 | -0.13326 | 29.47
19 | 0.017026 | 0.0042716 | -0.017016 | -0.0042659 | 9.8219e-06 | 5.7652e-06 | 0.025506 | 0.025506 | 0.025506 | 0.99336 | -0.12739 | 0.99273 | -0.1395 | 7.0072
20 | 0.063086 | 0.015871 | -0.063004 | -0.015819 | 8.2145e-05 | 5.2256e-05 | 0.094552 | 0.094552 | 0.094552 | 0.99305 | -0.13326 | 0.99164 | -0.16055 | 25.9757
21 | 0.017016 | 0.0042659 | -0.017013 | -0.0042639 | 3.3108e-06 | 1.9435e-06 | 0.025506 | 0.025506 | 0.025506 | 0.99273 | -0.1395 | 0.99252 | -0.14358 | 7.0072
22 | 0.039357 | 0.0098749 | -0.039328 | -0.0098564 | 2.9233e-05 | 1.8421e-05 | 0.059061 | 0.059061 | 0.059061 | 0.99164 | -0.16055 | 0.99084 | -0.17614 | 16.2256
23 | 0.023647 | 0.0059438 | -0.023607 | -0.0059188 | 4.0769e-05 | 2.4981e-05 | 0.03549 | 0.035491 | 0.035491 | 0.99164 | -0.16055 | 0.98977 | -0.19672 | 9.7502
24 | 0.011573 | 0.0029006 | -0.011573 | -0.0029004 | 4.2011e-07 | 2.2022e-07 | 0.0173 | 0.0173 | 0.0173 | 0.99541 | -0.087867 | 0.99537 | -0.088629 | 4.7529
25 | 0.0091617 | 0.0022964 | -0.0091604 | -0.0022958 | 1.3333e-06 | 6.0694e-07 | 0.013696 | 0.013696 | 0.013696 | 0.99541 | -0.087867 | 0.99526 | -0.090922 | 3.7626
26 | 0.013373 | 0.0033518 | -0.013373 | -0.0033516 | 4.0134e-07 | 2.2245e-07 | 0.02005 | 0.02005 | 0.02005 | 0.99252 | -0.14358 | 0.99249 | -0.14421 | 5.5082
27 | 0.023607 | 0.0059188 | -0.0236 | -0.0059148 | 6.6234e-06 | 4.0588e-06 | 0.035491 | 0.035491 | 0.035491 | 0.98977 | -0.19672 | 0.98947 | -0.20261 | 9.7502
28 | 0.0038289 | 0.00095942 | -0.0038286 | -0.00095954 | 3.1762e-07 | -1.1883e-07 | 0.0057846 | 0.0057847 | 0.0057847 | 0.98493 | -0.28958 | 0.98484 | -0.29132 | 1.5892
29 | 0.0037197 | 0.00093212 | -0.0037195 | -0.00093219 | 1.7564e-07 | -7.6334e-08 | 0.0056196 | 0.0056197 | 0.0056197 | 0.98493 | -0.28958 | 0.98488 | -0.29057 | 1.5439
30 | -0.0075486 | -0.0018915 | 0.0075491 | 0.0018917 | 4.9006e-07 | 1.8575e-07 | 0.011404 | 0.011404 | 0.011404 | 0.98493 | -0.28958 | 0.985 | -0.28821 | 3.133
31 | -0.086396 | -0.021731 | 0.086545 | 0.021827 | 0.00014973 | 9.553e-05 | 0.13054 | 0.13054 | 0.13054 | 0.985 | -0.28821 | 0.98686 | -0.252 | 35.8638
32 | 0.033776 | 0.0084703 | -0.033765 | -0.0084633 | 1.1024e-05 | 6.9114e-06 | 0.051026 | 0.051026 | 0.051026 | 0.985 | -0.28821 | 0.98465 | -0.29506 | 14.0182
33 | 0.045071 | 0.011369 | -0.044983 | -0.011313 | 8.7763e-05 | 5.5528e-05 | 0.068114 | 0.068114 | 0.068114 | 0.985 | -0.28821 | 0.9829 | -0.32897 | 18.7127
34 | -0.09856 | -0.024838 | 0.098684 | 0.024917 | 0.00012396 | 7.9144e-05 | 0.14866 | 0.14866 | 0.14866 | 0.98686 | -0.252 | 0.98822 | -0.22575 | 40.8406
35 | 0.02289 | 0.005738 | -0.022887 | -0.0057361 | 3.1697e-06 | 1.9388e-06 | 0.034593 | 0.034593 | 0.034593 | 0.98465 | -0.29506 | 0.9845 | -0.29797 | 9.5035
36 | 0.044983 | 0.011313 | -0.044879 | -0.011248 | 0.0001038 | 6.5679e-05 | 0.068114 | 0.068114 | 0.068114 | 0.9829 | -0.32897 | 0.98043 | -0.3774 | 18.7128
37 | 0.0066728 | 0.0016724 | -0.0066725 | -0.0016723 | 2.6813e-07 | 7.9287e-08 | 0.010004 | 0.010004 | 0.010004 | 0.99249 | -0.14421 | 0.99244 | -0.14506 | 2.7485
38 | -0.10587 | -0.026719 | 0.10589 | 0.026728 | 1.3679e-05 | 8.7361e-06 | 0.15949 | 0.15949 | 0.15949 | 0.98822 | -0.22575 | 0.98836 | -0.22305 | 43.8149
39 | -0.0066051 | -0.0016554 | 0.0066059 | 0.0016556 | 8.2241e-07 | 2.4098e-07 | 0.0099346 | 0.0099345 | 0.0099346 | 0.98932 | -0.20558 | 0.98945 | -0.20297 | 2.7293
40 | 0.0066051 | 0.0016554 | -0.0066048 | -0.0016553 | 2.6424e-07 | 7.7443e-08 | 0.0099346 | 0.0099346 | 0.0099346 | 0.98932 | -0.20558 | 0.98928 | -0.20642 | 2.7293
41 | -0.0066059 | -0.0016556 | 0.006606 | 0.0016557 | 1.1142e-07 | 3.2641e-08 | 0.0099345 | 0.0099345 | 0.0099345 | 0.98945 | -0.20297 | 0.98947 | -0.20261 | 2.7293
42 | 0.0032467 | 0.00081368 | -0.0032467 | -0.00081369 | 1.6512e-08 | -1.3138e-08 | 0.0048835 | 0.0048835 | 0.0048835 | 0.98928 | -0.20642 | 0.98927 | -0.20653 | 1.3416

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39506 | 0.099708

## res_load
| p_mw | q_mvar
0 | 0.010783 | 0.0027024
1 | 0.021192 | 0.0053111
2 | 0.010883 | 0.0027276
3 | 0.0025755 | 0.00064547
4 | 0.023468 | 0.0058817
5 | 0.0044794 | 0.0011226
6 | 0.0038965 | 0.00097655
7 | 0.013395 | 0.0033571
8 | 0.066245 | 0.016603
9 | 0.010256 | 0.0025703
10 | 0.0084885 | 0.0021274
11 | 0.011573 | 0.0029004
12 | 0.0091604 | 0.0022958
13 | 0.0036395 | 0.00091214
14 | 0.039328 | 0.0098564
15 | 0.0038286 | 0.00095954
16 | 0.0037195 | 0.00093219
17 | 0.0030438 | 0.00076285
18 | 0.012014 | 0.0030111
19 | 0.010874 | 0.0027253
20 | 0.0067001 | 0.0016792
21 | 0.044879 | 0.011248
22 | 0.00719 | 0.001802
23 | 0.022887 | 0.0057361
24 | 0.0057549 | 0.0014423
25 | 0.0066725 | 0.0016723
26 | 0.0033581 | 0.00084163
27 | 0.016994 | 0.0042591
28 | 0.0032467 | 0.00081369

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1