## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-89_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-89_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-89_0_3_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_261-89_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-89_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-89_0_3_node_28 | 0.4 | n |  | TRUE
6 | bus_LV_261-89_0_3_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_261-89_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_261-89_0_3_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_261-89_0_3_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_261-89_0_3_node_31 | 0.4 | n |  | TRUE
11 | bus_LV_261-89_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_261-89_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_261-89_0_3_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_261-89_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_261-89_0_3_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_261-89_0_3_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_261-89_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_261-89_0_3_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_261-89_0_3_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_261-89_0_3_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_261-89_0_3_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_261-89_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_261-89_0_3_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_261-89_0_3_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_261-89_0_3_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_261-89_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_261-89_0_3_node_17 | 0.4 | n |  | TRUE
28 | bus_MV_548_0_node_60 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-89_0_3_load_0 | 0 | 0.012036 | 0.0030165 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-89_0_3_load_28 | 5 | 0.022541 | 0.0056493 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-89_0_3_load_16 | 6 | 0.039255 | 0.0098383 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-89_0_3_load_22 | 9 | 0.017578 | 0.0044053 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-89_0_3_load_31 | 10 | 0.052862 | 0.013249 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-89_0_3_load_23 | 13 | 0.011566 | 0.0028988 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-89_0_3_load_25 | 15 | 0.025154 | 0.0063042 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-89_0_3_load_27 | 16 | 0.030931 | 0.007752 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-89_0_3_load_24 | 18 | 0.0019075 | 0.00047807 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-89_0_3_load_26 | 19 | 0.017998 | 0.0045108 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-89_0_3_load_11 | 20 | 0.016613 | 0.0041636 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-89_0_3_load_15 | 22 | 0.015695 | 0.0039335 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-89_0_3_load_30 | 23 | 0.023232 | 0.0058225 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-89_0_3_load_20 | 24 | 0.012986 | 0.0032547 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-89_0_3_load_29 | 25 | 0.031865 | 0.007986 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-89_0_3_load_17 | 27 | 0.023624 | 0.0059206 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-89_0_3_line_0 |  | 0 | 1 | 0.052856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-89_0_3_line_1 |  | 1 | 2 | 0.081742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-89_0_3_line_2 |  | 2 | 10 | 0.036742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-89_0_3_line_3 |  | 2 | 4 | 0.021529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-89_0_3_line_4 |  | 3 | 4 | 0.002724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_261-89_0_3_line_5 |  | 3 | 5 | 0.026643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_261-89_0_3_line_6 |  | 4 | 6 | 0.044006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-89_0_3_line_7 |  | 5 | 7 | 0.029982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_261-89_0_3_line_8 |  | 6 | 14 | 0.016166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-89_0_3_line_9 |  | 7 | 8 | 0.024037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_261-89_0_3_line_10 |  | 7 | 9 | 0.02477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-89_0_3_line_11 |  | 8 | 16 | 0.026349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-89_0_3_line_12 |  | 8 | 17 | 0.008956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-89_0_3_line_13 |  | 11 | 12 | 0.020752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-89_0_3_line_14 |  | 11 | 13 | 0.028311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-89_0_3_line_15 |  | 12 | 14 | 0.00712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-89_0_3_line_16 |  | 12 | 15 | 0.013456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-89_0_3_line_17 |  | 13 | 18 | 0.0064319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-89_0_3_line_18 |  | 15 | 19 | 0.020017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-89_0_3_line_19 |  | 16 | 25 | 0.017847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_261-89_0_3_line_20 |  | 17 | 21 | 0.013552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-89_0_3_line_21 |  | 17 | 22 | 0.01601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-89_0_3_line_22 |  | 17 | 20 | 0.013487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-89_0_3_line_23 |  | 21 | 23 | 0.021674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-89_0_3_line_24 |  | 21 | 24 | 0.0092842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-89_0_3_line_25 |  | 24 | 26 | 0.0036091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-89_0_3_line_26 |  | 26 | 27 | 0.012113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-89_0_3_trafo_29 | 0.63 MVA 20/0.4 kV | 28 | 25 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2683815.274 | 1247277.9222 | 2683842.3862 | 1247323.2952
1 | 2683815.274 | 1247277.9222 | 2683816.15 | 1247277.412 | 2683816.2717 | 1247277.347 | 2683818.5719 | 1247276.0119 | 2683820.6218 | 1247274.7399 | 2683820.8047 | 1247274.6313 | 2683821.4754 | 1247274.2071 | 2683821.4891 | 1247272.1725 | 2683822.1559 | 1247270.4251 | 2683823.0133 | 1247269.0806 | 2683833.045 | 1247262.6622 | 2683871.4792 | 1247239.6886 | 2683876.1336 | 1247236.9302 | 2683879.9819 | 1247236.1618 | 2683882.8319 | 1247237.0695
2 | 2683882.8319 | 1247237.0695 | 2683884.5757 | 1247239.8184 | 2683885.2112 | 1247240.817 | 2683902.5118 | 1247268.0963
3 | 2683882.8319 | 1247237.0695 | 2683884.285 | 1247236.8788 | 2683884.8527 | 1247236.7978 | 2683885.3975 | 1247236.7277 | 2683886.2299 | 1247236.6283 | 2683896.4568 | 1247235.0941 | 2683901.3546 | 1247234.3628 | 2683902.1115 | 1247234.2512 | 2683904.1327 | 1247233.9463
4 | 2683904.1327 | 1247233.9463 | 2683904.4768 | 1247232.5834 | 2683904.5152 | 1247232.5395 | 2683905.352 | 1247231.5951
5 | 2683905.352 | 1247231.5951 | 2683907.4865 | 1247230.758 | 2683922.8378 | 1247224.7597 | 2683930.1291 | 1247221.8012
6 | 2683904.1327 | 1247233.9463 | 2683909.3699 | 1247241.7817 | 2683927.3354 | 1247271.3299
7 | 2683958.1226 | 1247212.45 | 2683954.7594 | 1247213.6366 | 2683953.0159 | 1247213.0003 | 2683950.6676 | 1247213.4675 | 2683930.1291 | 1247221.8012
8 | 2683933.8229 | 1247285.4377 | 2683934.4241 | 1247282.9888 | 2683927.3354 | 1247271.3299
9 | 2683966.8168 | 1247234.8674 | 2683958.1226 | 1247212.45
10 | 2683958.1226 | 1247212.45 | 2683962.5107 | 1247210.8999 | 2683962.2651 | 1247209.5732 | 2683962.4719 | 1247208.3085 | 2683963.3461 | 1247206.8532 | 2683965.4174 | 1247205.6816 | 2683978.2424 | 1247201.77
11 | 2683966.8168 | 1247234.8674 | 2683957.4863 | 1247237.1036 | 2683950.5211 | 1247239.807 | 2683945.7553 | 1247240.2955 | 2683944.0617 | 1247236.1351
12 | 2683973.1416 | 1247240.5723 | 2683970.1428 | 1247239.5068 | 2683968.1092 | 1247237.4876 | 2683966.8168 | 1247234.8674
13 | 2683944.5681 | 1247309.7076 | 2683940.6009 | 1247303.4135 | 2683933.4938 | 1247292.1379
14 | 2683944.5681 | 1247309.7076 | 2683968.9487 | 1247295.3158
15 | 2683933.4938 | 1247292.1379 | 2683932.5558 | 1247290.6347 | 2683933.8229 | 1247285.4377
16 | 2683933.4938 | 1247292.1379 | 2683945.019 | 1247285.1936
17 | 2683968.9487 | 1247295.3158 | 2683974.4876 | 1247292.0462
18 | 2683959.7745 | 1247284.0707 | 2683956.4646 | 1247278.2973 | 2683945.019 | 1247285.1936
19 | 2683928.4095 | 1247244.7088 | 2683944.0617 | 1247236.1351
20 | 2683973.1416 | 1247240.5723 | 2683977.9105 | 1247241.4738 | 2683986.6081 | 1247242.3198
21 | 2683973.1416 | 1247240.5723 | 2683964.0395 | 1247253.7426
22 | 2683973.1416 | 1247240.5723 | 2683974.2556 | 1247254.013
23 | 2683986.6081 | 1247242.3198 | 2683980.7322 | 1247221.4545
24 | 2683986.6081 | 1247242.3198 | 2683995.8651 | 1247241.6103
25 | 2683999.4636 | 1247241.3345 | 2683995.8651 | 1247241.6103
26 | 2683999.4636 | 1247241.3345 | 2683996.0881 | 1247229.7016

## bus_geodata
| x | y | coords
0 | 2683842.3862 | 1247323.2952
1 | 2683815.274 | 1247277.9222
2 | 2683882.8319 | 1247237.0695
3 | 2683905.352 | 1247231.5951
4 | 2683904.1327 | 1247233.9463
5 | 2683930.1291 | 1247221.8012
6 | 2683927.3354 | 1247271.3299
7 | 2683958.1226 | 1247212.45
8 | 2683966.8168 | 1247234.8674
9 | 2683978.2424 | 1247201.77
10 | 2683902.5118 | 1247268.0963
11 | 2683944.5681 | 1247309.7076
12 | 2683933.4938 | 1247292.1379
13 | 2683968.9487 | 1247295.3158
14 | 2683933.8229 | 1247285.4377
15 | 2683945.019 | 1247285.1936
16 | 2683944.0617 | 1247236.1351
17 | 2683973.1416 | 1247240.5723
18 | 2683974.4876 | 1247292.0462
19 | 2683959.7745 | 1247284.0707
20 | 2683974.2556 | 1247254.013
21 | 2683986.6081 | 1247242.3198
22 | 2683964.0395 | 1247253.7426
23 | 2683980.7322 | 1247221.4545
24 | 2683995.8651 | 1247241.6103
25 | 2683928.4095 | 1247244.7088
26 | 2683999.4636 | 1247241.3345
27 | 2683996.0881 | 1247229.7016
28 | 2683966.8168 | 1247234.8674

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98843 | -0.22232 | 0.012036 | 0.0030165
1 | 0.98902 | -0.21098 | 0 | 0
2 | 0.98992 | -0.19346 | 0 | 0
3 | 0.9914 | -0.16476 | 0 | 0
4 | 0.9912 | -0.16864 | 0 | 0
5 | 0.99272 | -0.13947 | 0.022541 | 0.0056493
6 | 0.98732 | -0.24379 | 0.039255 | 0.0098383
7 | 0.9944 | -0.10712 | 0 | 0
8 | 0.99588 | -0.078783 | 0 | 0
9 | 0.994 | -0.11479 | 0.017578 | 0.0044053
10 | 0.98814 | -0.22807 | 0.052862 | 0.013249
11 | 0.98585 | -0.27241 | 0 | 0
12 | 0.98611 | -0.2674 | 0 | 0
13 | 0.9855 | -0.27925 | 0.011566 | 0.0028988
14 | 0.98648 | -0.26017 | 0 | 0
15 | 0.98558 | -0.27781 | 0.025154 | 0.0063042
16 | 0.99824 | -0.033654 | 0.030931 | 0.007752
17 | 0.99512 | -0.093299 | 0 | 0
18 | 0.98549 | -0.27947 | 0.0019075 | 0.00047807
19 | 0.98524 | -0.28428 | 0.017998 | 0.0045108
20 | 0.99492 | -0.097243 | 0.016613 | 0.0041636
21 | 0.99438 | -0.10758 | 0 | 0
22 | 0.9949 | -0.097722 | 0.015695 | 0.0039335
23 | 0.99393 | -0.11646 | 0.023232 | 0.0058225
24 | 0.99407 | -0.11358 | 0.012986 | 0.0032547
25 | 1 | 0 | -0.32835 | -0.082929
26 | 0.994 | -0.11508 | 0 | 0
27 | 0.99374 | -0.12013 | 0.023624 | 0.0059206
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.012036 | -0.0030165 | 0.012043 | 0.00302 | 6.5075e-06 | 3.4869e-06 | 0.01812 | 0.018119 | 0.01812 | 0.98843 | -0.22232 | 0.98902 | -0.21098 | 4.9779
1 | -0.012043 | -0.00302 | 0.012053 | 0.0030254 | 1.0064e-05 | 5.3907e-06 | 0.018119 | 0.018119 | 0.018119 | 0.98902 | -0.21098 | 0.98992 | -0.19346 | 4.9778
2 | 0.05295 | 0.013304 | -0.052862 | -0.013249 | 8.731e-05 | 5.5407e-05 | 0.079604 | 0.079604 | 0.079604 | 0.98992 | -0.19346 | 0.98814 | -0.22807 | 21.8693
3 | -0.065002 | -0.016329 | 0.06508 | 0.016378 | 7.71e-05 | 4.9067e-05 | 0.097723 | 0.097723 | 0.097723 | 0.98992 | -0.19346 | 0.9912 | -0.16864 | 26.847
4 | 0.16143 | 0.04071 | -0.1614 | -0.040691 | 3.0008e-05 | 1.9135e-05 | 0.24239 | 0.24239 | 0.24239 | 0.9914 | -0.16476 | 0.9912 | -0.16864 | 33.2952
5 | -0.16143 | -0.04071 | 0.16163 | 0.040834 | 0.00019567 | 0.0001242 | 0.24239 | 0.24239 | 0.24239 | 0.9914 | -0.16476 | 0.99272 | -0.13947 | 22.1968
6 | 0.096325 | 0.024312 | -0.09598 | -0.024092 | 0.00034536 | 0.00022047 | 0.14467 | 0.14467 | 0.14467 | 0.9912 | -0.16864 | 0.98732 | -0.24379 | 39.7434
7 | -0.18417 | -0.046483 | 0.18446 | 0.046665 | 0.00028585 | 0.00018178 | 0.27618 | 0.27618 | 0.27618 | 0.99272 | -0.13947 | 0.9944 | -0.10712 | 25.2908
8 | 0.056724 | 0.014253 | -0.05668 | -0.014225 | 4.4321e-05 | 2.8159e-05 | 0.085504 | 0.085504 | 0.085504 | 0.98732 | -0.24379 | 0.98648 | -0.26017 | 23.49
9 | -0.20204 | -0.051074 | 0.20232 | 0.051249 | 0.00027492 | 0.00017501 | 0.30249 | 0.30249 | 0.30249 | 0.9944 | -0.10712 | 0.99588 | -0.078783 | 27.7004
10 | 0.017584 | 0.0044091 | -0.017578 | -0.0044053 | 6.4315e-06 | 3.795e-06 | 0.026313 | 0.026313 | 0.026313 | 0.9944 | -0.10712 | 0.994 | -0.11479 | 7.229
11 | -0.2946 | -0.074432 | 0.29524 | 0.074839 | 0.00063881 | 0.00040781 | 0.4404 | 0.4404 | 0.4404 | 0.99588 | -0.078783 | 0.99824 | -0.033654 | 40.3299
12 | 0.092289 | 0.023182 | -0.092225 | -0.023142 | 6.388e-05 | 4.0767e-05 | 0.13791 | 0.13791 | 0.13791 | 0.99588 | -0.078783 | 0.99512 | -0.093299 | 37.8885
13 | -0.013478 | -0.0033792 | 0.013481 | 0.003381 | 3.2208e-06 | 1.7967e-06 | 0.020344 | 0.020344 | 0.020344 | 0.98585 | -0.27241 | 0.98611 | -0.2674 | 5.589
14 | 0.013478 | 0.0033792 | -0.013474 | -0.0033768 | 4.3941e-06 | 2.4514e-06 | 0.020344 | 0.020344 | 0.020344 | 0.98585 | -0.27241 | 0.9855 | -0.27925 | 5.5891
15 | -0.056661 | -0.014213 | 0.05668 | 0.014225 | 1.952e-05 | 1.2402e-05 | 0.085504 | 0.085504 | 0.085504 | 0.98611 | -0.2674 | 0.98648 | -0.26017 | 23.49
16 | 0.043179 | 0.010832 | -0.043158 | -0.010818 | 2.1424e-05 | 1.354e-05 | 0.06516 | 0.06516 | 0.06516 | 0.98611 | -0.2674 | 0.98558 | -0.27781 | 17.9011
17 | 0.0019076 | 0.000478 | -0.0019075 | -0.00047807 | 2.0009e-08 | -6.9146e-08 | 0.0028802 | 0.0028802 | 0.0028802 | 0.9855 | -0.27925 | 0.98549 | -0.27947 | 0.79127
18 | 0.018004 | 0.0045141 | -0.017998 | -0.0045108 | 5.5466e-06 | 3.2948e-06 | 0.027183 | 0.027183 | 0.027183 | 0.98558 | -0.27781 | 0.98524 | -0.28428 | 7.4678
19 | -0.32617 | -0.082591 | 0.3267 | 0.082929 | 0.00052801 | 0.00033723 | 0.48651 | 0.48651 | 0.48651 | 0.99824 | -0.033654 | 1 | 0 | 44.5521
20 | 0.05991 | 0.015041 | -0.059869 | -0.015015 | 4.0793e-05 | 2.5931e-05 | 0.089593 | 0.089593 | 0.089593 | 0.99512 | -0.093299 | 0.99438 | -0.10758 | 24.6135
21 | 0.015698 | 0.0039355 | -0.015695 | -0.0039335 | 3.3082e-06 | 1.9093e-06 | 0.023474 | 0.023474 | 0.023474 | 0.99512 | -0.093299 | 0.9949 | -0.097722 | 6.449
22 | 0.016616 | 0.0041655 | -0.016613 | -0.0041636 | 3.1223e-06 | 1.8231e-06 | 0.024847 | 0.024847 | 0.024847 | 0.99512 | -0.093299 | 0.99492 | -0.097243 | 6.826
23 | 0.023242 | 0.0058285 | -0.023232 | -0.0058225 | 9.8321e-06 | 6.0115e-06 | 0.034781 | 0.034781 | 0.034781 | 0.99438 | -0.10758 | 0.99393 | -0.11646 | 9.5551
24 | 0.036628 | 0.0091864 | -0.036617 | -0.0091798 | 1.046e-05 | 6.5741e-06 | 0.054813 | 0.054813 | 0.054813 | 0.99438 | -0.10758 | 0.99407 | -0.11358 | 15.0584
25 | 0.023631 | 0.0059251 | -0.023629 | -0.0059241 | 1.6935e-06 | 1.0371e-06 | 0.035374 | 0.035374 | 0.035374 | 0.99407 | -0.11358 | 0.994 | -0.11508 | 9.718
26 | 0.023629 | 0.0059241 | -0.023624 | -0.0059206 | 5.6837e-06 | 3.4806e-06 | 0.035374 | 0.035374 | 0.035374 | 0.994 | -0.11508 | 0.99374 | -0.12013 | 9.7181

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36022 | 0.090915

## res_load
| p_mw | q_mvar
0 | 0.012036 | 0.0030165
1 | 0.022541 | 0.0056493
2 | 0.039255 | 0.0098383
3 | 0.017578 | 0.0044053
4 | 0.052862 | 0.013249
5 | 0.011566 | 0.0028988
6 | 0.025154 | 0.0063042
7 | 0.030931 | 0.007752
8 | 0.0019075 | 0.00047807
9 | 0.017998 | 0.0045108
10 | 0.016613 | 0.0041636
11 | 0.015695 | 0.0039335
12 | 0.023232 | 0.0058225
13 | 0.012986 | 0.0032547
14 | 0.031865 | 0.007986
15 | 0.023624 | 0.0059206

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1