## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-8_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-8_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-8_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-8_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-8_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-8_0_5_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_261-8_0_5_node_24 | 0.4 | n |  | TRUE
7 | bus_LV_261-8_0_5_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_261-8_0_5_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_261-8_0_5_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_261-8_0_5_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_261-8_0_5_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_261-8_0_5_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_261-8_0_5_node_51 | 0.4 | n |  | TRUE
14 | bus_LV_261-8_0_5_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_261-8_0_5_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_261-8_0_5_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_261-8_0_5_node_37 | 0.4 | n |  | TRUE
18 | bus_LV_261-8_0_5_node_53 | 0.4 | n |  | TRUE
19 | bus_LV_261-8_0_5_node_41 | 0.4 | n |  | TRUE
20 | bus_LV_261-8_0_5_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_261-8_0_5_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_261-8_0_5_node_50 | 0.4 | n |  | TRUE
23 | bus_LV_261-8_0_5_node_48 | 0.4 | n |  | TRUE
24 | bus_LV_261-8_0_5_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_261-8_0_5_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_261-8_0_5_node_47 | 0.4 | n |  | TRUE
27 | bus_LV_261-8_0_5_node_49 | 0.4 | n |  | TRUE
28 | bus_LV_261-8_0_5_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_261-8_0_5_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_261-8_0_5_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_261-8_0_5_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_261-8_0_5_node_42 | 0.4 | n |  | TRUE
33 | bus_LV_261-8_0_5_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_261-8_0_5_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_261-8_0_5_node_52 | 0.4 | n |  | TRUE
36 | bus_LV_261-8_0_5_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_261-8_0_5_node_56 | 0.4 | n |  | TRUE
38 | bus_LV_261-8_0_5_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_261-8_0_5_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_261-8_0_5_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_261-8_0_5_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_261-8_0_5_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_261-8_0_5_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_261-8_0_5_node_55 | 0.4 | n |  | TRUE
45 | bus_LV_261-8_0_5_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_261-8_0_5_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_261-8_0_5_node_40 | 0.4 | n |  | TRUE
48 | bus_MV_542_0_node_94 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-8_0_5_load_0 | 0 | 0.014143 | 0.0035447 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-8_0_5_load_1 | 1 | 0.020228 | 0.0050696 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-8_0_5_load_28 | 7 | 0.037023 | 0.0092788 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-8_0_5_load_27 | 9 | 0.0038274 | 0.00095925 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-8_0_5_load_51 | 13 | 0.0046731 | 0.0011712 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-8_0_5_load_38 | 16 | 0.021596 | 0.0054125 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-8_0_5_load_37 | 17 | 0.017586 | 0.0044076 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-8_0_5_load_53 | 18 | 0.010987 | 0.0027535 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-8_0_5_load_41 | 19 | 0.0053064 | 0.0013299 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-8_0_5_load_46 | 20 | 0.045003 | 0.011279 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-8_0_5_load_50 | 22 | 0.03446 | 0.0086366 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-8_0_5_load_48 | 23 | 0.0062443 | 0.001565 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-8_0_5_load_32 | 25 | 0.0045519 | 0.0011408 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-8_0_5_load_47 | 26 | 0.022573 | 0.0056574 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-8_0_5_load_49 | 27 | 0.0061907 | 0.0015515 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-8_0_5_load_29 | 29 | 0.0057991 | 0.0014534 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-8_0_5_load_54 | 30 | 0.0051193 | 0.001283 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-8_0_5_load_36 | 31 | 0.0021291 | 0.00053361 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-8_0_5_load_42 | 32 | 0.016281 | 0.0040804 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-8_0_5_load_45 | 33 | 0.0097443 | 0.0024422 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-8_0_5_load_26 | 34 | 0.0090696 | 0.0022731 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-8_0_5_load_52 | 35 | 0.011185 | 0.0028031 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-8_0_5_load_39 | 36 | 0.011754 | 0.0029457 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-8_0_5_load_56 | 37 | 0.0058948 | 0.0014774 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-8_0_5_load_30 | 38 | 0.0045533 | 0.0011412 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-8_0_5_load_33 | 39 | 0.0026442 | 0.0006627 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-8_0_5_load_31 | 40 | 0.033051 | 0.0082833 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-8_0_5_load_34 | 41 | 0.0021051 | 0.00052759 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-8_0_5_load_35 | 42 | 0.0021059 | 0.0005278 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-8_0_5_load_25 | 43 | 0.01105 | 0.0027693 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-8_0_5_load_55 | 44 | 0.0051684 | 0.0012953 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-8_0_5_load_44 | 45 | 0.018378 | 0.0046059 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-8_0_5_load_43 | 46 | 0.01456 | 0.003649 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-8_0_5_load_40 | 47 | 0.0073053 | 0.0018309 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-8_0_5_line_0 |  | 0 | 1 | 0.030473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-8_0_5_line_1 |  | 0 | 2 | 0.027072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-8_0_5_line_2 |  | 1 | 3 | 0.012558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-8_0_5_line_3 |  | 2 | 4 | 0.004171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_261-8_0_5_line_4 |  | 2 | 5 | 0.008757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-8_0_5_line_5 |  | 3 | 6 | 0.0079566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-8_0_5_line_6 |  | 3 | 7 | 0.044324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-8_0_5_line_7 |  | 4 | 8 | 0.011579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-8_0_5_line_8 |  | 4 | 9 | 0.028439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-8_0_5_line_9 |  | 5 | 18 | 0.031874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-8_0_5_line_10 |  | 5 | 19 | 0.011785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-8_0_5_line_11 |  | 6 | 32 | 0.019381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-8_0_5_line_12 |  | 6 | 33 | 0.02802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-8_0_5_line_13 |  | 8 | 20 | 0.011875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-8_0_5_line_14 |  | 8 | 15 | 0.008897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-8_0_5_line_15 |  | 9 | 34 | 0.02253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-8_0_5_line_16 |  | 10 | 11 | 0.008065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-8_0_5_line_17 |  | 10 | 12 | 0.013974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-8_0_5_line_18 |  | 10 | 13 | 0.026947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-8_0_5_line_19 |  | 11 | 30 | 0.0058082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-8_0_5_line_20 |  | 11 | 28 | 0.02316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-8_0_5_line_21 |  | 12 | 14 | 0.008508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-8_0_5_line_22 |  | 13 | 35 | 0.018847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-8_0_5_line_23 |  | 14 | 31 | 0.0019565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-8_0_5_line_24 |  | 15 | 16 | 0.027958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-8_0_5_line_25 |  | 15 | 17 | 0.03475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-8_0_5_line_26 |  | 16 | 36 | 0.033813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-8_0_5_line_27 |  | 18 | 35 | 0.017534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-8_0_5_line_28 |  | 20 | 26 | 0.034976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-8_0_5_line_29 |  | 21 | 22 | 0.017134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-8_0_5_line_30 |  | 21 | 23 | 0.017885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-8_0_5_line_31 |  | 22 | 37 | 0.03087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-8_0_5_line_32 |  | 23 | 27 | 0.013361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-8_0_5_line_33 |  | 24 | 25 | 0.033141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-8_0_5_line_34 |  | 24 | 26 | 0.023842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-8_0_5_line_35 |  | 24 | 27 | 0.011311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-8_0_5_line_36 |  | 25 | 38 | 0.012302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-8_0_5_line_37 |  | 28 | 29 | 0.012348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-8_0_5_line_38 |  | 30 | 44 | 0.01655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-8_0_5_line_39 |  | 31 | 42 | 0.008022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-8_0_5_line_40 |  | 32 | 47 | 0.0088202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-8_0_5_line_41 |  | 33 | 46 | 0.011357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-8_0_5_line_42 |  | 34 | 43 | 0.036171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-8_0_5_line_43 |  | 38 | 40 | 0.0080302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-8_0_5_line_44 |  | 39 | 40 | 0.012683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-8_0_5_line_45 |  | 41 | 42 | 0.0080257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-8_0_5_line_46 |  | 45 | 46 | 0.012619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-8_0_5_trafo_4 | 0.63 MVA 20/0.4 kV | 48 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2683815.3993 | 1251026.7442 | 2683785.4624 | 1251032.4364
1 | 2683841.9638 | 1251021.5345 | 2683836.7538 | 1251022.6838 | 2683815.3993 | 1251026.7442
2 | 2683773.1255 | 1251034.7821 | 2683785.4624 | 1251032.4364
3 | 2683841.9638 | 1251021.5345 | 2683840.9264 | 1251017.4945
4 | 2683841.9638 | 1251021.5345 | 2683842.8082 | 1251024.8155 | 2683844.4039 | 1251029.9419
5 | 2683773.1255 | 1251034.7821 | 2683773.7155 | 1251038.4376 | 2683774.3808 | 1251042.6391
6 | 2683773.1255 | 1251034.7821 | 2683771.1064 | 1251034.4978 | 2683769.5771 | 1251033.7423 | 2683767.9042 | 1251031.9284 | 2683767.0677 | 1251030.2264 | 2683766.6784 | 1251028.9311 | 2683765.2799 | 1251018.926 | 2683761.9524 | 1250994.3901
7 | 2683840.9264 | 1251017.4945 | 2683845.7292 | 1251016.3172 | 2683852.1756 | 1251014.7516
8 | 2683840.9264 | 1251017.4945 | 2683830.3338 | 1250991.1017
9 | 2683844.4039 | 1251029.9419 | 2683853.8683 | 1251060.3781
10 | 2683844.4039 | 1251029.9419 | 2683832.8081 | 1251032.0446
11 | 2683774.3808 | 1251042.6391 | 2683793.4512 | 1251039.1811
12 | 2683774.3808 | 1251042.6391 | 2683768.4234 | 1251043.789 | 2683768.8322 | 1251046.9083 | 2683770.007 | 1251065.6787
13 | 2683852.1756 | 1251014.7516 | 2683851.8179 | 1251013.3566 | 2683852.4911 | 1251010.5974 | 2683852.891 | 1251005.2769 | 2683852.594 | 1251003.0373
14 | 2683855.1671 | 1251023.1335 | 2683852.1756 | 1251014.7516
15 | 2683819.3114 | 1250971.4787 | 2683824.3029 | 1250979.6645 | 2683829.5802 | 1250989.224 | 2683830.3338 | 1250991.1017
16 | 2683864.9547 | 1251124.6702 | 2683866.7653 | 1251124.2177 | 2683872.0654 | 1251120.968
17 | 2683872.0654 | 1251120.968 | 2683877.6829 | 1251119.2907 | 2683885.4607 | 1251116.988
18 | 2683872.0654 | 1251120.968 | 2683871.8335 | 1251118.1515 | 2683864.6711 | 1251095.1181
19 | 2683864.9547 | 1251124.6702 | 2683859.3135 | 1251126.0525
20 | 2683864.9547 | 1251124.6702 | 2683866.6624 | 1251131.4883 | 2683868.3467 | 1251138.3506 | 2683872.9527 | 1251137.2039 | 2683876.8674 | 1251139.0273
21 | 2683885.4607 | 1251116.988 | 2683889.452 | 1251118.2009 | 2683893.81 | 1251118.0403
22 | 2683864.6711 | 1251095.1181 | 2683859.0748 | 1251077.1214
23 | 2683893.81 | 1251118.0403 | 2683895.7059 | 1251117.5572
24 | 2683855.1671 | 1251023.1335 | 2683863.3908 | 1251049.8548
25 | 2683855.1671 | 1251023.1335 | 2683881.6829 | 1251020.7514 | 2683889.7763 | 1251020.0103
26 | 2683863.3908 | 1251049.8548 | 2683873.3366 | 1251082.1715
27 | 2683859.0748 | 1251077.1214 | 2683853.8683 | 1251060.3781
28 | 2683852.594 | 1251003.0373 | 2683852.4817 | 1251002.191 | 2683847.4216 | 1250989.5544 | 2683840.5682 | 1250982.0074 | 2683838.3439 | 1250976.4829 | 2683836.8512 | 1250972.3857
29 | 2683793.9019 | 1250923.159 | 2683805.2518 | 1250910.3232
30 | 2683793.9019 | 1250923.159 | 2683801.0644 | 1250929.6763 | 2683806.812 | 1250935.5258
31 | 2683805.2518 | 1250910.3232 | 2683816.1199 | 1250898.0322 | 2683824.6585 | 1250892.66 | 2683828.6205 | 1250890.8048
32 | 2683806.812 | 1250935.5258 | 2683810.4711 | 1250939.2498 | 2683815.8439 | 1250945.2747 | 2683815.8859 | 1250945.3278
33 | 2683822.912 | 1250954.1924 | 2683833.954 | 1250947.4213 | 2683845.1117 | 1250944.2212 | 2683853.6534 | 1250943.4047
34 | 2683822.912 | 1250954.1924 | 2683824.3746 | 1250954.858 | 2683827.365 | 1250956.3904 | 2683830.8858 | 1250959.9206 | 2683834.3981 | 1250965.6523 | 2683836.8512 | 1250972.3857
35 | 2683822.912 | 1250954.1924 | 2683815.8859 | 1250945.3278
36 | 2683853.6534 | 1250943.4047 | 2683857.1689 | 1250943.0687 | 2683865.8897 | 1250942.1394
37 | 2683876.8674 | 1251139.0273 | 2683879.0144 | 1251140.4031 | 2683881.9684 | 1251149.7448
38 | 2683859.3135 | 1251126.0525 | 2683843.2393 | 1251129.9912
39 | 2683895.7059 | 1251117.5572 | 2683903.4795 | 1251115.5765
40 | 2683802.1299 | 1251037.6074 | 2683793.4512 | 1251039.1811
41 | 2683769.8281 | 1251077.0332 | 2683770.0268 | 1251065.995 | 2683770.007 | 1251065.6787
42 | 2683797.1794 | 1250943.0247 | 2683804.0653 | 1250950.2118 | 2683813.7156 | 1250962.3018 | 2683819.3114 | 1250971.4787
43 | 2683865.8897 | 1250942.1394 | 2683873.8747 | 1250941.2885
44 | 2683886.4858 | 1250939.9446 | 2683873.8747 | 1250941.2885
45 | 2683903.4795 | 1251115.5765 | 2683911.2568 | 1251113.5948
46 | 2683769.8281 | 1251077.0332 | 2683769.8151 | 1251077.7563 | 2683769.6475 | 1251089.6073 | 2683769.6462 | 1251089.6514

## bus_geodata
| x | y | coords
0 | 2683815.3993 | 1251026.7442
1 | 2683785.4624 | 1251032.4364
2 | 2683841.9638 | 1251021.5345
3 | 2683773.1255 | 1251034.7821
4 | 2683840.9264 | 1251017.4945
5 | 2683844.4039 | 1251029.9419
6 | 2683774.3808 | 1251042.6391
7 | 2683761.9524 | 1250994.3901
8 | 2683852.1756 | 1251014.7516
9 | 2683830.3338 | 1250991.1017
10 | 2683872.0654 | 1251120.968
11 | 2683864.9547 | 1251124.6702
12 | 2683885.4607 | 1251116.988
13 | 2683864.6711 | 1251095.1181
14 | 2683893.81 | 1251118.0403
15 | 2683855.1671 | 1251023.1335
16 | 2683863.3908 | 1251049.8548
17 | 2683889.7763 | 1251020.0103
18 | 2683853.8683 | 1251060.3781
19 | 2683832.8081 | 1251032.0446
20 | 2683852.594 | 1251003.0373
21 | 2683793.9019 | 1250923.159
22 | 2683805.2518 | 1250910.3232
23 | 2683806.812 | 1250935.5258
24 | 2683822.912 | 1250954.1924
25 | 2683853.6534 | 1250943.4047
26 | 2683836.8512 | 1250972.3857
27 | 2683815.8859 | 1250945.3278
28 | 2683876.8674 | 1251139.0273
29 | 2683881.9684 | 1251149.7448
30 | 2683859.3135 | 1251126.0525
31 | 2683895.7059 | 1251117.5572
32 | 2683793.4512 | 1251039.1811
33 | 2683770.007 | 1251065.6787
34 | 2683819.3114 | 1250971.4787
35 | 2683859.0748 | 1251077.1214
36 | 2683873.3366 | 1251082.1715
37 | 2683828.6205 | 1250890.8048
38 | 2683865.8897 | 1250942.1394
39 | 2683886.4858 | 1250939.9446
40 | 2683873.8747 | 1250941.2885
41 | 2683911.2568 | 1251113.5948
42 | 2683903.4795 | 1251115.5765
43 | 2683797.1794 | 1250943.0247
44 | 2683843.2393 | 1251129.9912
45 | 2683769.6462 | 1251089.6514
46 | 2683769.8281 | 1251077.0332
47 | 2683802.1299 | 1251037.6074
48 | 2683841.9638 | 1251021.5345

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99622 | -0.072221 | 0.014143 | 0.0035447
1 | 0.99278 | -0.13856 | 0.020228 | 0.0050696
2 | 0.99963 | -0.0069908 | 0 | 0
3 | 0.99159 | -0.16152 | 0 | 0
4 | 1 | 0 | -0.43648 | -0.10995
5 | 0.9992 | -0.015332 | 0 | 0
6 | 0.9911 | -0.17087 | 0 | 0
7 | 0.99008 | -0.19066 | 0.037023 | 0.0092788
8 | 0.99886 | -0.021832 | 0 | 0
9 | 0.99938 | -0.011878 | 0.0038274 | 0.00095925
10 | 0.99614 | -0.074122 | 0 | 0
11 | 0.99603 | -0.076401 | 0 | 0
12 | 0.99606 | -0.075678 | 0 | 0
13 | 0.99669 | -0.063511 | 0.0046731 | 0.0011712
14 | 0.99601 | -0.076626 | 0 | 0
15 | 0.99845 | -0.029752 | 0 | 0
16 | 0.9976 | -0.046069 | 0.021596 | 0.0054125
17 | 0.99789 | -0.040443 | 0.017586 | 0.0044076
18 | 0.99777 | -0.042791 | 0.010987 | 0.0027535
19 | 0.99914 | -0.016424 | 0.0053064 | 0.0013299
20 | 0.99796 | -0.03898 | 0.045003 | 0.011279
21 | 0.9902 | -0.1884 | 0 | 0
22 | 0.98957 | -0.2007 | 0.03446 | 0.0086366
23 | 0.99087 | -0.17558 | 0.0062443 | 0.001565
24 | 0.99198 | -0.15395 | 0 | 0
25 | 0.99062 | -0.18028 | 0.0045519 | 0.0011408
26 | 0.99411 | -0.11282 | 0.022573 | 0.0056574
27 | 0.99144 | -0.16453 | 0.0061907 | 0.0015515
28 | 0.9959 | -0.078761 | 0 | 0
29 | 0.99584 | -0.08002 | 0.0057991 | 0.0014534
30 | 0.99597 | -0.077451 | 0.0051193 | 0.001283
31 | 0.996 | -0.076844 | 0.0021291 | 0.00053361
32 | 0.99069 | -0.17899 | 0.016281 | 0.0040804
33 | 0.99001 | -0.19212 | 0.0097443 | 0.0024422
34 | 0.99897 | -0.019793 | 0.0090696 | 0.0022731
35 | 0.99716 | -0.054552 | 0.011185 | 0.0028031
36 | 0.99724 | -0.053032 | 0.011754 | 0.0029457
37 | 0.9894 | -0.20394 | 0.0058948 | 0.0014774
38 | 0.99017 | -0.18908 | 0.0045533 | 0.0011412
39 | 0.98988 | -0.19477 | 0.0026442 | 0.0006627
40 | 0.98991 | -0.19418 | 0.033051 | 0.0082833
41 | 0.99596 | -0.077735 | 0.0021051 | 0.00052759
42 | 0.99597 | -0.077438 | 0.0021059 | 0.0005278
43 | 0.99861 | -0.026776 | 0.01105 | 0.0027693
44 | 0.99589 | -0.078954 | 0.0051684 | 0.0012953
45 | 0.98945 | -0.2029 | 0.018378 | 0.0046059
46 | 0.98967 | -0.19877 | 0.01456 | 0.003649
47 | 0.99063 | -0.18013 | 0.0073053 | 0.0018309
48 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.12417 | 0.031374 | -0.12378 | -0.031122 | 0.00039349 | 0.00025144 | 0.18556 | 0.18556 | 0.18556 | 0.99622 | -0.072221 | 0.99278 | -0.13856 | 50.9788
1 | -0.13832 | -0.034918 | 0.13875 | 0.035195 | 0.0004337 | 0.00027721 | 0.20669 | 0.20669 | 0.20669 | 0.99622 | -0.072221 | 0.99963 | -0.0069908 | 56.7824
2 | 0.10355 | 0.026053 | -0.10344 | -0.02598 | 0.0001135 | 7.2475e-05 | 0.15524 | 0.15524 | 0.15524 | 0.99278 | -0.13856 | 0.99159 | -0.16152 | 42.6496
3 | -0.19346 | -0.048958 | 0.19353 | 0.048999 | 6.4935e-05 | 4.1449e-05 | 0.28815 | 0.28815 | 0.28815 | 0.99963 | -0.0069908 | 1 | 0 | 39.581
4 | 0.054713 | 0.013762 | -0.054692 | -0.013749 | 2.1792e-05 | 1.3832e-05 | 0.081462 | 0.081462 | 0.081462 | 0.99963 | -0.0069908 | 0.9992 | -0.015332 | 22.3797
5 | 0.066365 | 0.016669 | -0.066335 | -0.01665 | 2.9601e-05 | 1.8842e-05 | 0.099603 | 0.099603 | 0.099603 | 0.99159 | -0.16152 | 0.9911 | -0.17087 | 27.3633
6 | 0.037074 | 0.0093111 | -0.037023 | -0.0092788 | 5.1461e-05 | 3.2364e-05 | 0.055642 | 0.055642 | 0.055642 | 0.99159 | -0.16152 | 0.99008 | -0.19066 | 15.2863
7 | 0.21733 | 0.054939 | -0.2171 | -0.054794 | 0.00022727 | 0.00014515 | 0.32355 | 0.32355 | 0.32355 | 1 | 0 | 0.99886 | -0.021832 | 44.4438
8 | 0.023972 | 0.0060164 | -0.023958 | -0.006008 | 1.3572e-05 | 8.3129e-06 | 0.035673 | 0.035673 | 0.035673 | 1 | 0 | 0.99938 | -0.011878 | 9.8003
9 | 0.049385 | 0.012419 | -0.04932 | -0.012378 | 6.4675e-05 | 4.0975e-05 | 0.073559 | 0.073559 | 0.073559 | 0.9992 | -0.015332 | 0.99777 | -0.042791 | 20.2086
10 | 0.0053066 | 0.0013299 | -0.0053064 | -0.0013299 | 2.76e-07 | 2.2288e-08 | 0.0079027 | 0.0079027 | 0.0079027 | 0.9992 | -0.015332 | 0.99914 | -0.016424 | 2.1711
11 | 0.023596 | 0.005917 | -0.023587 | -0.0059114 | 9.1221e-06 | 5.5885e-06 | 0.035427 | 0.035427 | 0.035427 | 0.9911 | -0.17087 | 0.99069 | -0.17899 | 9.7328
12 | 0.042739 | 0.010733 | -0.042696 | -0.010706 | 4.3275e-05 | 2.7336e-05 | 0.064175 | 0.064175 | 0.064175 | 0.9911 | -0.17087 | 0.99001 | -0.19212 | 17.6306
13 | 0.1661 | 0.041992 | -0.16597 | -0.041905 | 0.00013648 | 8.7034e-05 | 0.24758 | 0.24758 | 0.24758 | 0.99886 | -0.021832 | 0.99796 | -0.03898 | 34.0078
14 | 0.050994 | 0.012802 | -0.050975 | -0.012789 | 1.9258e-05 | 1.2209e-05 | 0.075974 | 0.075974 | 0.075974 | 0.99886 | -0.021832 | 0.99845 | -0.029752 | 20.872
15 | 0.02013 | 0.0050488 | -0.020123 | -0.0050442 | 7.591e-06 | 4.5631e-06 | 0.029974 | 0.029974 | 0.029974 | 0.99938 | -0.011878 | 0.99897 | -0.019793 | 8.2347
16 | 0.01609 | 0.0040332 | -0.016089 | -0.0040322 | 1.7472e-06 | 1.0133e-06 | 0.024036 | 0.024036 | 0.024036 | 0.99614 | -0.074122 | 0.99603 | -0.076401 | 6.6032
17 | 0.0063412 | 0.0015891 | -0.0063407 | -0.001589 | 4.7018e-07 | 1.1901e-07 | 0.0094722 | 0.0094723 | 0.0094723 | 0.99614 | -0.074122 | 0.99606 | -0.075678 | 2.6023
18 | -0.022432 | -0.0056223 | 0.022443 | 0.0056292 | 1.1346e-05 | 6.9104e-06 | 0.033508 | 0.033508 | 0.033508 | 0.99614 | -0.074122 | 0.99669 | -0.063511 | 9.2055
19 | 0.010289 | 0.0025786 | -0.010288 | -0.0025784 | 5.1459e-07 | 2.5374e-07 | 0.015371 | 0.015371 | 0.015371 | 0.99603 | -0.076401 | 0.99597 | -0.077451 | 4.2227
20 | 0.0058001 | 0.0014536 | -0.0057995 | -0.0014535 | 6.5211e-07 | 1.1595e-07 | 0.0086651 | 0.0086652 | 0.0086652 | 0.99603 | -0.076401 | 0.9959 | -0.078761 | 2.3805
21 | 0.0063407 | 0.001589 | -0.0063404 | -0.0015889 | 2.8627e-07 | 7.2474e-08 | 0.0094723 | 0.0094723 | 0.0094723 | 0.99606 | -0.075678 | 0.99601 | -0.076626 | 2.6023
22 | -0.027116 | -0.0068004 | 0.027128 | 0.0068076 | 1.1584e-05 | 7.1678e-06 | 0.040485 | 0.040484 | 0.040485 | 0.99669 | -0.063511 | 0.99716 | -0.054552 | 11.1221
23 | 0.0063404 | 0.0015889 | -0.0063403 | -0.0015889 | 6.583e-08 | 1.6668e-08 | 0.0094723 | 0.0094723 | 0.0094723 | 0.99601 | -0.076626 | 0.996 | -0.076844 | 2.6023
24 | 0.033379 | 0.0083765 | -0.033353 | -0.0083603 | 2.595e-05 | 1.6242e-05 | 0.04975 | 0.04975 | 0.04975 | 0.99845 | -0.029752 | 0.9976 | -0.046069 | 13.6677
25 | 0.017595 | 0.0044128 | -0.017586 | -0.0044076 | 8.9616e-06 | 5.2812e-06 | 0.026224 | 0.026224 | 0.026224 | 0.99845 | -0.029752 | 0.99789 | -0.040443 | 7.2044
26 | 0.011757 | 0.0029478 | -0.011754 | -0.0029457 | 3.9e-06 | 2.0547e-06 | 0.017538 | 0.017538 | 0.017538 | 0.9976 | -0.046069 | 0.99724 | -0.053032 | 4.8181
27 | 0.038334 | 0.0096242 | -0.038312 | -0.0096107 | 2.1494e-05 | 1.3528e-05 | 0.057175 | 0.057175 | 0.057175 | 0.99777 | -0.042791 | 0.99716 | -0.054552 | 15.7073
28 | 0.12097 | 0.030626 | -0.12054 | -0.030353 | 0.00042721 | 0.00027296 | 0.18048 | 0.18048 | 0.18048 | 0.99796 | -0.03898 | 0.99411 | -0.11282 | 49.5814
29 | 0.04038 | 0.010129 | -0.040356 | -0.010114 | 2.3661e-05 | 1.4923e-05 | 0.060683 | 0.060683 | 0.060683 | 0.9902 | -0.1884 | 0.98957 | -0.2007 | 16.6713
30 | -0.04038 | -0.010129 | 0.040404 | 0.010145 | 2.4697e-05 | 1.5576e-05 | 0.060683 | 0.060683 | 0.060683 | 0.9902 | -0.1884 | 0.99087 | -0.17558 | 16.6712
31 | 0.0058957 | 0.0014776 | -0.0058948 | -0.0014774 | 9.0984e-07 | 1.8578e-07 | 0.0088654 | 0.0088655 | 0.0088655 | 0.98957 | -0.2007 | 0.9894 | -0.20394 | 2.4356
32 | -0.046649 | -0.01171 | 0.046673 | 0.011725 | 2.4593e-05 | 1.5568e-05 | 0.07006 | 0.07006 | 0.07006 | 0.99087 | -0.17558 | 0.99144 | -0.16453 | 19.2474
33 | 0.044882 | 0.01128 | -0.044826 | -0.011244 | 5.635e-05 | 3.5637e-05 | 0.067336 | 0.067336 | 0.067336 | 0.99198 | -0.15395 | 0.99062 | -0.18028 | 18.499
34 | -0.097773 | -0.024573 | 0.097965 | 0.024696 | 0.00019238 | 0.00012281 | 0.14669 | 0.14669 | 0.14669 | 0.99198 | -0.15395 | 0.99411 | -0.11282 | 40.2989
35 | 0.052891 | 0.013294 | -0.052864 | -0.013277 | 2.6709e-05 | 1.6948e-05 | 0.079352 | 0.079352 | 0.079352 | 0.99198 | -0.15395 | 0.99144 | -0.16453 | 21.8
36 | 0.040274 | 0.010103 | -0.040257 | -0.010093 | 1.6885e-05 | 1.0648e-05 | 0.060499 | 0.060499 | 0.060499 | 0.99062 | -0.18028 | 0.99017 | -0.18908 | 16.6206
37 | 0.0057995 | 0.0014535 | -0.0057991 | -0.0014534 | 3.4767e-07 | 6.1855e-08 | 0.0086652 | 0.0086652 | 0.0086652 | 0.9959 | -0.078761 | 0.99584 | -0.08002 | 2.3806
38 | 0.0051688 | 0.0012953 | -0.0051684 | -0.0012953 | 3.701e-07 | 2.1507e-08 | 0.0077223 | 0.0077224 | 0.0077224 | 0.99597 | -0.077451 | 0.99589 | -0.078954 | 2.1215
39 | 0.0042112 | 0.0010553 | -0.0042111 | -0.0010553 | 1.1907e-07 | -2.8192e-08 | 0.0062915 | 0.0062915 | 0.0062915 | 0.996 | -0.076844 | 0.99597 | -0.077438 | 1.7284
40 | 0.0073057 | 0.001831 | -0.0073053 | -0.0018309 | 3.9827e-07 | 1.4133e-07 | 0.010973 | 0.010973 | 0.010973 | 0.99069 | -0.17899 | 0.99063 | -0.18013 | 3.0146
41 | 0.032952 | 0.0082636 | -0.032941 | -0.0082571 | 1.0448e-05 | 6.5405e-06 | 0.049529 | 0.049529 | 0.049529 | 0.99001 | -0.19212 | 0.98967 | -0.19877 | 13.607
42 | 0.011053 | 0.0027712 | -0.01105 | -0.0027693 | 3.6771e-06 | 1.88e-06 | 0.016465 | 0.016465 | 0.016465 | 0.99897 | -0.019793 | 0.99861 | -0.026776 | 4.5233
43 | 0.035704 | 0.0089513 | -0.035695 | -0.0089459 | 8.6696e-06 | 5.4453e-06 | 0.053656 | 0.053656 | 0.053656 | 0.99017 | -0.18908 | 0.98991 | -0.19418 | 14.7408
44 | -0.0026442 | -0.0006627 | 0.0026443 | 0.00066259 | 7.5141e-08 | -1.1495e-07 | 0.0039749 | 0.0039748 | 0.0039749 | 0.98988 | -0.19477 | 0.98991 | -0.19418 | 1.092
45 | -0.0021051 | -0.00052759 | 0.0021052 | 0.00052751 | 2.9772e-08 | -8.539e-08 | 0.0031452 | 0.0031451 | 0.0031452 | 0.99596 | -0.077735 | 0.99597 | -0.077438 | 0.86406
46 | -0.018378 | -0.0046059 | 0.018382 | 0.0046081 | 3.6148e-06 | 2.1514e-06 | 0.027638 | 0.027638 | 0.027638 | 0.98945 | -0.2029 | 0.98967 | -0.19877 | 7.5929

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43648 | 0.10995

## res_load
| p_mw | q_mvar
0 | 0.014143 | 0.0035447
1 | 0.020228 | 0.0050696
2 | 0.037023 | 0.0092788
3 | 0.0038274 | 0.00095925
4 | 0.0046731 | 0.0011712
5 | 0.021596 | 0.0054125
6 | 0.017586 | 0.0044076
7 | 0.010987 | 0.0027535
8 | 0.0053064 | 0.0013299
9 | 0.045003 | 0.011279
10 | 0.03446 | 0.0086366
11 | 0.0062443 | 0.001565
12 | 0.0045519 | 0.0011408
13 | 0.022573 | 0.0056574
14 | 0.0061907 | 0.0015515
15 | 0.0057991 | 0.0014534
16 | 0.0051193 | 0.001283
17 | 0.0021291 | 0.00053361
18 | 0.016281 | 0.0040804
19 | 0.0097443 | 0.0024422
20 | 0.0090696 | 0.0022731
21 | 0.011185 | 0.0028031
22 | 0.011754 | 0.0029457
23 | 0.0058948 | 0.0014774
24 | 0.0045533 | 0.0011412
25 | 0.0026442 | 0.0006627
26 | 0.033051 | 0.0082833
27 | 0.0021051 | 0.00052759
28 | 0.0021059 | 0.0005278
29 | 0.01105 | 0.0027693
30 | 0.0051684 | 0.0012953
31 | 0.018378 | 0.0046059
32 | 0.01456 | 0.003649
33 | 0.0073053 | 0.0018309

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1