## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-926_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-926_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-926_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-926_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-926_0_5_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_261-926_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-926_0_5_node_111 | 0.4 | n |  | TRUE
7 | bus_LV_261-926_0_5_node_99 | 0.4 | n |  | TRUE
8 | bus_LV_261-926_0_5_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_261-926_0_5_node_97 | 0.4 | n |  | TRUE
10 | bus_LV_261-926_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_261-926_0_5_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_261-926_0_5_node_65 | 0.4 | n |  | TRUE
13 | bus_LV_261-926_0_5_node_62 | 0.4 | n |  | TRUE
14 | bus_LV_261-926_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_261-926_0_5_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_261-926_0_5_node_106 | 0.4 | n |  | TRUE
17 | bus_LV_261-926_0_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_261-926_0_5_node_85 | 0.4 | n |  | TRUE
19 | bus_LV_261-926_0_5_node_103 | 0.4 | n |  | TRUE
20 | bus_LV_261-926_0_5_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_261-926_0_5_node_132 | 0.4 | n |  | TRUE
22 | bus_LV_261-926_0_5_node_40 | 0.4 | n |  | TRUE
23 | bus_LV_261-926_0_5_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_261-926_0_5_node_109 | 0.4 | n |  | TRUE
25 | bus_LV_261-926_0_5_node_112 | 0.4 | n |  | TRUE
26 | bus_LV_261-926_0_5_node_101 | 0.4 | n |  | TRUE
27 | bus_LV_261-926_0_5_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_261-926_0_5_node_107 | 0.4 | n |  | TRUE
29 | bus_LV_261-926_0_5_node_104 | 0.4 | n |  | TRUE
30 | bus_LV_261-926_0_5_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_261-926_0_5_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_261-926_0_5_node_53 | 0.4 | n |  | TRUE
33 | bus_LV_261-926_0_5_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_261-926_0_5_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_261-926_0_5_node_96 | 0.4 | n |  | TRUE
36 | bus_LV_261-926_0_5_node_57 | 0.4 | n |  | TRUE
37 | bus_LV_261-926_0_5_node_98 | 0.4 | n |  | TRUE
38 | bus_LV_261-926_0_5_node_120 | 0.4 | n |  | TRUE
39 | bus_LV_261-926_0_5_node_63 | 0.4 | n |  | TRUE
40 | bus_LV_261-926_0_5_node_105 | 0.4 | n |  | TRUE
41 | bus_LV_261-926_0_5_node_88 | 0.4 | n |  | TRUE
42 | bus_LV_261-926_0_5_node_119 | 0.4 | n |  | TRUE
43 | bus_LV_261-926_0_5_node_86 | 0.4 | n |  | TRUE
44 | bus_LV_261-926_0_5_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_261-926_0_5_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_261-926_0_5_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_261-926_0_5_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_261-926_0_5_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_261-926_0_5_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_261-926_0_5_node_73 | 0.4 | n |  | TRUE
51 | bus_LV_261-926_0_5_node_71 | 0.4 | n |  | TRUE
52 | bus_LV_261-926_0_5_node_90 | 0.4 | n |  | TRUE
53 | bus_LV_261-926_0_5_node_58 | 0.4 | n |  | TRUE
54 | bus_LV_261-926_0_5_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_261-926_0_5_node_56 | 0.4 | n |  | TRUE
56 | bus_LV_261-926_0_5_node_108 | 0.4 | n |  | TRUE
57 | bus_LV_261-926_0_5_node_100 | 0.4 | n |  | TRUE
58 | bus_LV_261-926_0_5_node_131 | 0.4 | n |  | TRUE
59 | bus_LV_261-926_0_5_node_129 | 0.4 | n |  | TRUE
60 | bus_LV_261-926_0_5_node_21 | 0.4 | n |  | TRUE
61 | bus_LV_261-926_0_5_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_261-926_0_5_node_95 | 0.4 | n |  | TRUE
63 | bus_LV_261-926_0_5_node_20 | 0.4 | n |  | TRUE
64 | bus_LV_261-926_0_5_node_22 | 0.4 | n |  | TRUE
65 | bus_LV_261-926_0_5_node_24 | 0.4 | n |  | TRUE
66 | bus_LV_261-926_0_5_node_89 | 0.4 | n |  | TRUE
67 | bus_LV_261-926_0_5_node_25 | 0.4 | n |  | TRUE
68 | bus_LV_261-926_0_5_node_26 | 0.4 | n |  | TRUE
69 | bus_LV_261-926_0_5_node_27 | 0.4 | n |  | TRUE
70 | bus_LV_261-926_0_5_node_28 | 0.4 | n |  | TRUE
71 | bus_LV_261-926_0_5_node_29 | 0.4 | n |  | TRUE
72 | bus_LV_261-926_0_5_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_261-926_0_5_node_45 | 0.4 | n |  | TRUE
74 | bus_LV_261-926_0_5_node_66 | 0.4 | n |  | TRUE
75 | bus_LV_261-926_0_5_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_261-926_0_5_node_31 | 0.4 | n |  | TRUE
77 | bus_LV_261-926_0_5_node_33 | 0.4 | n |  | TRUE
78 | bus_LV_261-926_0_5_node_113 | 0.4 | n |  | TRUE
79 | bus_LV_261-926_0_5_node_44 | 0.4 | n |  | TRUE
80 | bus_LV_261-926_0_5_node_43 | 0.4 | n |  | TRUE
81 | bus_LV_261-926_0_5_node_42 | 0.4 | n |  | TRUE
82 | bus_LV_261-926_0_5_node_41 | 0.4 | n |  | TRUE
83 | bus_LV_261-926_0_5_node_61 | 0.4 | n |  | TRUE
84 | bus_LV_261-926_0_5_node_60 | 0.4 | n |  | TRUE
85 | bus_LV_261-926_0_5_node_72 | 0.4 | n |  | TRUE
86 | bus_LV_261-926_0_5_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_261-926_0_5_node_75 | 0.4 | n |  | TRUE
88 | bus_LV_261-926_0_5_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_261-926_0_5_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_261-926_0_5_node_47 | 0.4 | n |  | TRUE
91 | bus_LV_261-926_0_5_node_48 | 0.4 | n |  | TRUE
92 | bus_LV_261-926_0_5_node_49 | 0.4 | n |  | TRUE
93 | bus_LV_261-926_0_5_node_50 | 0.4 | n |  | TRUE
94 | bus_LV_261-926_0_5_node_51 | 0.4 | n |  | TRUE
95 | bus_LV_261-926_0_5_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_261-926_0_5_node_93 | 0.4 | n |  | TRUE
97 | bus_LV_261-926_0_5_node_59 | 0.4 | n |  | TRUE
98 | bus_LV_261-926_0_5_node_84 | 0.4 | n |  | TRUE
99 | bus_LV_261-926_0_5_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_261-926_0_5_node_91 | 0.4 | n |  | TRUE
101 | bus_LV_261-926_0_5_node_54 | 0.4 | n |  | TRUE
102 | bus_LV_261-926_0_5_node_64 | 0.4 | n |  | TRUE
103 | bus_LV_261-926_0_5_node_123 | 0.4 | n |  | TRUE
104 | bus_LV_261-926_0_5_node_124 | 0.4 | n |  | TRUE
105 | bus_LV_261-926_0_5_node_121 | 0.4 | n |  | TRUE
106 | bus_LV_261-926_0_5_node_68 | 0.4 | n |  | TRUE
107 | bus_LV_261-926_0_5_node_69 | 0.4 | n |  | TRUE
108 | bus_LV_261-926_0_5_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_261-926_0_5_node_92 | 0.4 | n |  | TRUE
110 | bus_LV_261-926_0_5_node_87 | 0.4 | n |  | TRUE
111 | bus_LV_261-926_0_5_node_77 | 0.4 | n |  | TRUE
112 | bus_LV_261-926_0_5_node_78 | 0.4 | n |  | TRUE
113 | bus_LV_261-926_0_5_node_79 | 0.4 | n |  | TRUE
114 | bus_LV_261-926_0_5_node_80 | 0.4 | n |  | TRUE
115 | bus_LV_261-926_0_5_node_81 | 0.4 | n |  | TRUE
116 | bus_LV_261-926_0_5_node_114 | 0.4 | n |  | TRUE
117 | bus_LV_261-926_0_5_node_115 | 0.4 | n |  | TRUE
118 | bus_LV_261-926_0_5_node_110 | 0.4 | n |  | TRUE
119 | bus_LV_261-926_0_5_node_128 | 0.4 | n |  | TRUE
120 | bus_LV_261-926_0_5_node_127 | 0.4 | n |  | TRUE
121 | bus_LV_261-926_0_5_node_130 | 0.4 | n |  | TRUE
122 | bus_LV_261-926_0_5_node_116 | 0.4 | n |  | TRUE
123 | bus_LV_261-926_0_5_node_117 | 0.4 | n |  | TRUE
124 | bus_LV_261-926_0_5_node_118 | 0.4 | n |  | TRUE
125 | bus_LV_261-926_0_5_node_122 | 0.4 | n |  | TRUE
126 | bus_LV_261-926_0_5_node_125 | 0.4 | n |  | TRUE
127 | bus_MV_539_0_node_121 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-926_0_5_load_0 | 0 | 0.0030054 | 0.00075321 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-926_0_5_load_111 | 6 | 0.0042745 | 0.0010713 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-926_0_5_load_99 | 7 | 0.0064331 | 0.0016123 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-926_0_5_load_4 | 8 | 0.0031518 | 0.00078991 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-926_0_5_load_18 | 11 | 0.0045699 | 0.0011453 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-926_0_5_load_62 | 13 | 0.0026453 | 0.00066298 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-926_0_5_load_106 | 16 | 0.015595 | 0.0039085 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-926_0_5_load_85 | 18 | 0.0045922 | 0.0011509 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-926_0_5_load_103 | 19 | 0.005944 | 0.0014897 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-926_0_5_load_132 | 21 | 0.0036927 | 0.00092548 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-926_0_5_load_109 | 24 | 0.0030487 | 0.00076409 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-926_0_5_load_112 | 25 | 0.0082747 | 0.0020738 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-926_0_5_load_101 | 26 | 0.0025497 | 0.00063901 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-926_0_5_load_104 | 29 | 0.0080259 | 0.0020115 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-926_0_5_load_23 | 31 | 0.0022425 | 0.00056201 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-926_0_5_load_53 | 32 | 0.0048453 | 0.0012144 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-926_0_5_load_19 | 34 | 0.0025011 | 0.00062683 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-926_0_5_load_96 | 35 | 0.0023156 | 0.00058035 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-926_0_5_load_57 | 36 | 0.0024455 | 0.0006129 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-926_0_5_load_120 | 38 | 0.0029226 | 0.00073247 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-926_0_5_load_63 | 39 | 0.0023319 | 0.00058443 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-926_0_5_load_105 | 40 | 0.0056892 | 0.0014258 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-926_0_5_load_88 | 41 | 0.003818 | 0.00095687 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-926_0_5_load_119 | 42 | 0.0029551 | 0.00074061 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-926_0_5_load_86 | 43 | 0.0030961 | 0.00077597 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-926_0_5_load_35 | 45 | 0.0094534 | 0.0023692 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-926_0_5_load_30 | 46 | 0.0069753 | 0.0017482 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-926_0_5_load_34 | 49 | 0.010277 | 0.0025755 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-926_0_5_load_73 | 50 | 0.00499 | 0.0012506 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-926_0_5_load_71 | 51 | 0.0066301 | 0.0016617 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-926_0_5_load_90 | 52 | 0.0052462 | 0.0013148 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-926_0_5_load_58 | 53 | 0.0068271 | 0.001711 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-926_0_5_load_55 | 54 | 0.0023392 | 0.00058625 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-926_0_5_load_56 | 55 | 0.0024388 | 0.00061123 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-926_0_5_load_108 | 56 | 0.0030949 | 0.00077565 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-926_0_5_load_100 | 57 | 0.0039302 | 0.00098501 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-926_0_5_load_131 | 58 | 0.0037063 | 0.00092888 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-926_0_5_load_129 | 59 | 0.0033508 | 0.00083979 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-926_0_5_load_21 | 60 | 0.0022494 | 0.00056375 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-926_0_5_load_52 | 61 | 0.0094108 | 0.0023586 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-926_0_5_load_95 | 62 | 0.0025558 | 0.00064055 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-926_0_5_load_20 | 63 | 0.0021761 | 0.00054537 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-926_0_5_load_22 | 64 | 0.0022064 | 0.00055298 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-926_0_5_load_24 | 65 | 0.0020784 | 0.0005209 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-926_0_5_load_89 | 66 | 0.0022092 | 0.00055367 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-926_0_5_load_25 | 67 | 0.0023403 | 0.00058653 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-926_0_5_load_26 | 68 | 0.0019848 | 0.00049745 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-926_0_5_load_27 | 69 | 0.0024809 | 0.00062177 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-926_0_5_load_28 | 70 | 0.002061 | 0.00051653 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-926_0_5_load_29 | 71 | 0.003605 | 0.00090349 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-926_0_5_load_67 | 72 | 0.0024046 | 0.00060266 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-926_0_5_load_45 | 73 | 0.0042911 | 0.0010755 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-926_0_5_load_66 | 74 | 0.0038554 | 0.00096624 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-926_0_5_load_46 | 75 | 0.0070481 | 0.0017664 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-926_0_5_load_33 | 77 | 0.0047808 | 0.0011982 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-926_0_5_load_113 | 78 | 0.023037 | 0.0057735 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-926_0_5_load_44 | 79 | 0.0057326 | 0.0014367 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-926_0_5_load_42 | 81 | 0.0044373 | 0.0011121 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-926_0_5_load_41 | 82 | 0.0044803 | 0.0011229 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-926_0_5_load_61 | 83 | 0.0079402 | 0.00199 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-926_0_5_load_72 | 85 | 0.0041282 | 0.0010346 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-926_0_5_load_70 | 86 | 0.005053 | 0.0012664 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-926_0_5_load_75 | 87 | 0.0063634 | 0.0015948 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-926_0_5_load_76 | 89 | 0.0035955 | 0.00090111 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-926_0_5_load_47 | 90 | 0.0049629 | 0.0012438 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-926_0_5_load_48 | 91 | 0.0063511 | 0.0015917 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-926_0_5_load_49 | 92 | 0.0037354 | 0.00093618 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-926_0_5_load_50 | 93 | 0.0043111 | 0.0010805 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-926_0_5_load_93 | 96 | 0.0037325 | 0.00093545 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-926_0_5_load_59 | 97 | 0.0044513 | 0.0011156 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-926_0_5_load_84 | 98 | 0.004524 | 0.0011338 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-926_0_5_load_82 | 99 | 0.0060854 | 0.0015252 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-926_0_5_load_91 | 100 | 0.0045013 | 0.0011281 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-926_0_5_load_54 | 101 | 0.0075984 | 0.0019043 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-926_0_5_load_64 | 102 | 0.0025532 | 0.00063988 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-926_0_5_load_123 | 103 | 0.0024805 | 0.00062166 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-926_0_5_load_124 | 104 | 0.0024401 | 0.00061154 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-926_0_5_load_121 | 105 | 0.0024009 | 0.00060171 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-926_0_5_load_68 | 106 | 0.0024764 | 0.00062064 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-926_0_5_load_69 | 107 | 0.0019883 | 0.00049831 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-926_0_5_load_94 | 108 | 0.0019831 | 0.00049701 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-926_0_5_load_92 | 109 | 0.0024444 | 0.00061262 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-926_0_5_load_87 | 110 | 0.0035214 | 0.00088254 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-926_0_5_load_77 | 111 | 0.0039371 | 0.00098673 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-926_0_5_load_78 | 112 | 0.0027408 | 0.00068691 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-926_0_5_load_79 | 113 | 0.0029279 | 0.0007338 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-926_0_5_load_80 | 114 | 0.0038409 | 0.00096263 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-926_0_5_load_81 | 115 | 0.0037137 | 0.00093075 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-926_0_5_load_114 | 116 | 0.004033 | 0.0010108 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-926_0_5_load_115 | 117 | 0.0062027 | 0.0015545 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-926_0_5_load_110 | 118 | 0.0025948 | 0.00065032 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-926_0_5_load_128 | 119 | 0.0028356 | 0.00071066 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-926_0_5_load_127 | 120 | 0.0023618 | 0.00059192 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-926_0_5_load_130 | 121 | 0.0034342 | 0.0008607 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-926_0_5_load_116 | 122 | 0.0040121 | 0.0010055 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-926_0_5_load_117 | 123 | 0.0050706 | 0.0012708 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-926_0_5_load_118 | 124 | 0.010351 | 0.0025941 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-926_0_5_load_122 | 125 | 0.0024806 | 0.00062169 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-926_0_5_load_125 | 126 | 0.0025377 | 0.000636 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 112 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-926_0_5_line_0 |  | 0 | 1 | 0.0065076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-926_0_5_line_1 |  | 0 | 2 | 0.0028988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-926_0_5_line_2 |  | 1 | 3 | 0.005875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-926_0_5_line_3 |  | 2 | 4 | 0.010036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-926_0_5_line_4 |  | 2 | 5 | 0.012242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_261-926_0_5_line_5 |  | 3 | 6 | 0.057286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-926_0_5_line_6 |  | 3 | 7 | 0.029167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-926_0_5_line_7 |  | 4 | 12 | 0.005021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-926_0_5_line_8 |  | 4 | 13 | 0.019568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-926_0_5_line_9 |  | 5 | 10 | 0.012367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_261-926_0_5_line_10 |  | 5 | 11 | 0.0082133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_261-926_0_5_line_11 |  | 6 | 36 | 0.010346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-926_0_5_line_12 |  | 7 | 9 | 0.016892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-926_0_5_line_13 |  | 8 | 9 | 0.0079693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-926_0_5_line_14 |  | 9 | 37 | 0.002785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-926_0_5_line_15 |  | 10 | 17 | 0.081949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-926_0_5_line_16 |  | 10 | 18 | 0.021928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_261-926_0_5_line_17 |  | 11 | 34 | 0.010039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-926_0_5_line_18 |  | 12 | 38 | 0.028414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-926_0_5_line_19 |  | 12 | 15 | 0.010261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-926_0_5_line_20 |  | 13 | 39 | 0.00055528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-926_0_5_line_21 |  | 14 | 15 | 0.011246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-926_0_5_line_22 |  | 14 | 16 | 0.022592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-926_0_5_line_23 |  | 15 | 26 | 0.057488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-926_0_5_line_24 |  | 16 | 40 | 0.030797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-926_0_5_line_25 |  | 17 | 19 | 0.032946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-926_0_5_line_26 |  | 18 | 43 | 0.022894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_261-926_0_5_line_27 |  | 20 | 21 | 0.020138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-926_0_5_line_28 |  | 20 | 22 | 0.080704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-926_0_5_line_29 |  | 22 | 51 | 0.055764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_261-926_0_5_line_30 |  | 22 | 52 | 0.044826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_261-926_0_5_line_31 |  | 23 | 24 | 0.044741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-926_0_5_line_32 |  | 23 | 25 | 0.028853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-926_0_5_line_33 |  | 24 | 56 | 0.0086375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-926_0_5_line_34 |  | 25 | 53 | 0.026784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-926_0_5_line_35 |  | 26 | 57 | 0.00046613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-926_0_5_line_36 |  | 27 | 28 | 0.028062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-926_0_5_line_37 |  | 27 | 29 | 0.012738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-926_0_5_line_38 |  | 28 | 58 | 0.011496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-926_0_5_line_39 |  | 28 | 59 | 0.0045618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-926_0_5_line_40 |  | 29 | 40 | 0.024152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-926_0_5_line_41 |  | 30 | 31 | 0.013512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-926_0_5_line_42 |  | 30 | 32 | 0.036688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-926_0_5_line_43 |  | 31 | 60 | 0.0087787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-926_0_5_line_44 |  | 32 | 61 | 0.041191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-926_0_5_line_45 |  | 33 | 34 | 0.028021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-926_0_5_line_46 |  | 33 | 35 | 0.0032087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-926_0_5_line_47 |  | 35 | 62 | 0.0064541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-926_0_5_line_48 |  | 36 | 55 | 0.0089554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-926_0_5_line_49 |  | 37 | 118 | 0.038569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-926_0_5_line_50 |  | 37 | 56 | 0.021262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-926_0_5_line_51 |  | 38 | 105 | 0.0094142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-926_0_5_line_52 |  | 39 | 102 | 0.028062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-926_0_5_line_53 |  | 41 | 42 | 0.0070709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-926_0_5_line_54 |  | 42 | 114 | 0.0033337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-926_0_5_line_55 |  | 43 | 110 | 0.0092733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_261-926_0_5_line_56 |  | 44 | 45 | 0.031896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-926_0_5_line_57 |  | 44 | 46 | 0.023389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-926_0_5_line_58 |  | 45 | 79 | 0.0096938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-926_0_5_line_59 |  | 46 | 76 | 0.022809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-926_0_5_line_60 |  | 47 | 48 | 0.0074625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-926_0_5_line_61 |  | 47 | 49 | 0.015665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-926_0_5_line_62 |  | 48 | 50 | 0.029983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_261-926_0_5_line_63 |  | 49 | 76 | 0.016636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-926_0_5_line_64 |  | 50 | 85 | 0.0084139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_261-926_0_5_line_65 |  | 51 | 86 | 0.028416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_261-926_0_5_line_66 |  | 52 | 87 | 0.024959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_261-926_0_5_line_67 |  | 54 | 55 | 0.017675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-926_0_5_line_68 |  | 59 | 121 | 0.0026429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-926_0_5_line_69 |  | 60 | 63 | 0.0087233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-926_0_5_line_70 |  | 61 | 101 | 0.0054222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-926_0_5_line_71 |  | 62 | 66 | 0.0010917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-926_0_5_line_72 |  | 63 | 64 | 0.01676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-926_0_5_line_73 |  | 64 | 65 | 0.0087998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-926_0_5_line_74 |  | 65 | 66 | 0.017075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-926_0_5_line_75 |  | 67 | 68 | 3.9801e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_261-926_0_5_line_76 |  | 67 | 69 | 0.0022068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_261-926_0_5_line_77 |  | 68 | 70 | 4.9494e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_261-926_0_5_line_78 |  | 69 | 71 | 0.009787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_261-926_0_5_line_79 |  | 70 | 72 | 0.022182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_261-926_0_5_line_80 |  | 71 | 73 | 0.012292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_261-926_0_5_line_81 |  | 72 | 74 | 0.00077506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_261-926_0_5_line_82 |  | 73 | 75 | 0.013936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_261-926_0_5_line_83 |  | 74 | 106 | 0.020956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_261-926_0_5_line_84 |  | 75 | 88 | 0.03272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_261-926_0_5_line_85 |  | 76 | 77 | 0.036841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-926_0_5_line_86 |  | 77 | 78 | 0.0099408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-926_0_5_line_87 |  | 79 | 80 | 0.027968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-926_0_5_line_88 |  | 80 | 82 | 0.019941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-926_0_5_line_89 |  | 81 | 82 | 0.016441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-926_0_5_line_90 |  | 83 | 84 | 0.019488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-926_0_5_line_91 |  | 84 | 97 | 0.017198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-926_0_5_line_92 |  | 84 | 93 | 0.0074386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-926_0_5_line_93 |  | 85 | 86 | 0.0080539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_261-926_0_5_line_94 |  | 87 | 88 | 0.012555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_261-926_0_5_line_95 |  | 88 | 89 | 0.029879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_261-926_0_5_line_96 |  | 89 | 110 | 0.011387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_261-926_0_5_line_97 |  | 90 | 91 | 0.015086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-926_0_5_line_98 |  | 90 | 92 | 0.011528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-926_0_5_line_99 |  | 91 | 93 | 0.020336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-926_0_5_line_100 |  | 92 | 94 | 0.0037829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-926_0_5_line_101 |  | 94 | 95 | 0.033211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_261-926_0_5_line_102 |  | 94 | 96 | 0.009954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_261-926_0_5_line_103 |  | 95 | 98 | 0.015537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-926_0_5_line_104 |  | 95 | 99 | 0.005936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_261-926_0_5_line_105 |  | 96 | 100 | 0.0089498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_261-926_0_5_line_106 |  | 98 | 116 | 0.008528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-926_0_5_line_107 |  | 99 | 115 | 0.024245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_261-926_0_5_line_108 |  | 100 | 109 | 0.011863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_261-926_0_5_line_109 |  | 102 | 103 | 0.0099402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-926_0_5_line_110 |  | 103 | 104 | 0.0092437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-926_0_5_line_111 |  | 104 | 126 | 0.0086597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-926_0_5_line_112 |  | 105 | 125 | 0.0091758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-926_0_5_line_113 |  | 106 | 107 | 0.00033873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_261-926_0_5_line_114 |  | 107 | 108 | 3.5035e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_261-926_0_5_line_115 |  | 108 | 109 | 0.0037461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_261-926_0_5_line_116 |  | 111 | 112 | 0.016719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_261-926_0_5_line_117 |  | 111 | 113 | 0.00023591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_261-926_0_5_line_118 |  | 112 | 114 | 0.00624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-926_0_5_line_119 |  | 113 | 115 | 0.009901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_261-926_0_5_line_120 |  | 116 | 117 | 0.011702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-926_0_5_line_121 |  | 117 | 122 | 0.011699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-926_0_5_line_122 |  | 119 | 120 | 0.0092327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-926_0_5_line_123 |  | 120 | 125 | 0.0092952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-926_0_5_line_124 |  | 122 | 123 | 0.0039497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-926_0_5_line_125 |  | 123 | 124 | 0.0111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-926_0_5_trafo_78 | 0.63 MVA 20/0.4 kV | 127 | 112 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2685595.3071 | 1246188.2948 | 2685589.1007 | 1246190.2515
1 | 2685586.336 | 1246191.123 | 2685589.1007 | 1246190.2515
2 | 2685600.9237 | 1246186.519 | 2685595.3071 | 1246188.2948
3 | 2685579.4243 | 1246197.3057 | 2685582.778 | 1246195.7974 | 2685582.7392 | 1246194.2957 | 2685583.8264 | 1246192.7769 | 2685586.336 | 1246191.123
4 | 2685582.5147 | 1246179.4926 | 2685584.505 | 1246185.5481 | 2685586.336 | 1246191.123
5 | 2685600.9237 | 1246186.519 | 2685604.2783 | 1246185.4667 | 2685611.5703 | 1246184.3377 | 2685620.3321 | 1246183.4524 | 2685650.2864 | 1246181.5279 | 2685657.8355 | 1246180.9776
6 | 2685600.9237 | 1246186.519 | 2685601.7919 | 1246189.178 | 2685603.6498 | 1246191.3175 | 2685615.9777 | 1246198.8009 | 2685623.7721 | 1246203.5254
7 | 2685579.4243 | 1246197.3057 | 2685574.8312 | 1246199.3631
8 | 2685579.4243 | 1246197.3057 | 2685581.0375 | 1246201.7433 | 2685581.0042 | 1246208.2365 | 2685579.5397 | 1246214.4311 | 2685578.6448 | 1246216.2054
9 | 2685570.908 | 1246176.4785 | 2685575.5118 | 1246178.9134 | 2685577.5704 | 1246179.7104 | 2685579.9355 | 1246179.6889 | 2685582.5147 | 1246179.4926
10 | 2685582.5147 | 1246179.4926 | 2685587.4166 | 1246178.029 | 2685590.3679 | 1246177.0881
11 | 2685657.8355 | 1246180.9776 | 2685668.1539 | 1246180.2254
12 | 2685634.0496 | 1246213.4615 | 2685635.5103 | 1246210.6694 | 2685632.4774 | 1246208.802 | 2685623.7721 | 1246203.5254
13 | 2685634.0496 | 1246213.4615 | 2685627.2664 | 1246209.2784
14 | 2685634.0496 | 1246213.4615 | 2685636.4234 | 1246214.9302
15 | 2685504.1101 | 1246184.4545 | 2685534.795 | 1246162.7809 | 2685538.7993 | 1246164.3509 | 2685555.0237 | 1246171.4568 | 2685571.1384 | 1246180.407 | 2685570.908 | 1246176.4785
16 | 2685570.908 | 1246176.4785 | 2685566.7092 | 1246174.2496 | 2685551.337 | 1246166.5902
17 | 2685590.3679 | 1246177.0881 | 2685594.6576 | 1246175.7206 | 2685600.1008 | 1246174.7076
18 | 2685574.8312 | 1246199.3631 | 2685576.662 | 1246201.8136 | 2685576.8366 | 1246205.9414 | 2685575.183 | 1246212.1554 | 2685568.6983 | 1246225.4514
19 | 2685574.8312 | 1246199.3631 | 2685571.8687 | 1246197.8526 | 2685569.02 | 1246198.4008 | 2685565.4414 | 1246200.3173
20 | 2685578.3948 | 1246216.7012 | 2685578.6448 | 1246216.2054
21 | 2685560.3731 | 1246190.2812 | 2685563.014 | 1246195.2341 | 2685565.4414 | 1246200.3173
22 | 2685560.3731 | 1246190.2812 | 2685540.1429 | 1246200.3372
23 | 2685565.4414 | 1246200.3173 | 2685514.0539 | 1246226.0901
24 | 2685540.1429 | 1246200.3372 | 2685520.6574 | 1246210.023 | 2685512.587 | 1246214.0901
25 | 2685504.1101 | 1246184.4545 | 2685502.5663 | 1246182.0082 | 2685507.3028 | 1246177.3397 | 2685507.7564 | 1246173.6547 | 2685504.2843 | 1246168.7121 | 2685502.3778 | 1246167.3169 | 2685500.0402 | 1246167.5278 | 2685492.8524 | 1246172.8447
26 | 2685551.337 | 1246166.5902 | 2685549.0361 | 1246165.4438 | 2685536.2737 | 1246160.3115 | 2685531.6914 | 1246158.4774 | 2685530.1206 | 1246158.0346
27 | 2685473.1523 | 1246148.5708 | 2685471.2805 | 1246152.1019 | 2685455.1184 | 1246151.1462
28 | 2685405.3591 | 1246115.4921 | 2685402.8005 | 1246118.9801 | 2685411.8042 | 1246123.8577 | 2685473.1523 | 1246148.5708
29 | 2685405.3591 | 1246115.4921 | 2685438.2898 | 1246070.49
30 | 2685405.3591 | 1246115.4921 | 2685413.4683 | 1246121.1019 | 2685443.8565 | 1246134.1603 | 2685445.6234 | 1246134.8325
31 | 2685697.0204 | 1246257.5034 | 2685690.3992 | 1246249.3351 | 2685679.569 | 1246241.2282 | 2685662.0595 | 1246230.1919
32 | 2685697.0204 | 1246257.5034 | 2685706.0609 | 1246252.4859 | 2685712.1366 | 1246245.602 | 2685716.373 | 1246237.2875
33 | 2685654.7524 | 1246225.5862 | 2685662.0595 | 1246230.1919
34 | 2685728.7088 | 1246215.091 | 2685728.4661 | 1246215.638 | 2685729.391 | 1246217.5083 | 2685728.6967 | 1246219.0216 | 2685724.0619 | 1246229.1844 | 2685717.2376 | 1246235.5905 | 2685716.373 | 1246237.2875
35 | 2685514.0539 | 1246226.0901 | 2685513.6372 | 1246226.299
36 | 2685466.6378 | 1246205.808 | 2685479.6442 | 1246230.6916
37 | 2685479.6442 | 1246230.6916 | 2685491.0193 | 1246224.9591
38 | 2685466.6378 | 1246205.808 | 2685475.4409 | 1246198.3849
39 | 2685466.6378 | 1246205.808 | 2685464.5278 | 1246201.7635
40 | 2685491.0193 | 1246224.9591 | 2685512.587 | 1246214.0901
41 | 2685711.4384 | 1246164.3096 | 2685697.9598 | 1246165.2636
42 | 2685711.4384 | 1246164.3096 | 2685707.2469 | 1246157.9221 | 2685706.405 | 1246153.4511 | 2685704.9236 | 1246128.9976
43 | 2685689.203 | 1246165.8835 | 2685697.9598 | 1246165.2636
44 | 2685686.8168 | 1246100.996 | 2685686.8168 | 1246100.996 | 2685691.3301 | 1246099.7603 | 2685696.1941 | 1246103.0107 | 2685700.141 | 1246103.8461 | 2685701.8434 | 1246105.7722 | 2685703.0128 | 1246106.4118 | 2685703.6907 | 1246108.6454 | 2685704.9236 | 1246128.9976
45 | 2685627.9537 | 1246172.0651 | 2685620.4655 | 1246172.1238 | 2685608.4016 | 1246173.5618 | 2685602.309 | 1246174.2967 | 2685600.1008 | 1246174.7076
46 | 2685627.9537 | 1246172.0651 | 2685630.4459 | 1246170.0441
47 | 2685636.8839 | 1246169.5882 | 2685630.4459 | 1246170.0441
48 | 2685668.1539 | 1246180.2254 | 2685677.0856 | 1246179.5743
49 | 2685636.4234 | 1246214.9302 | 2685622.2591 | 1246236.7752 | 2685620.6058 | 1246249.1992
50 | 2685636.4234 | 1246214.9302 | 2685640.0824 | 1246216.3396 | 2685654.7524 | 1246225.5862
51 | 2685568.6983 | 1246225.4514 | 2685568.6508 | 1246225.5489 | 2685564.6281 | 1246233.9403
52 | 2685565.7578 | 1246241.7573 | 2685578.3948 | 1246216.7012
53 | 2685581.9852 | 1246134.9951 | 2685578.3303 | 1246141.0481
54 | 2685581.9852 | 1246134.9951 | 2685583.7084 | 1246132.1414
55 | 2685521.051 | 1246156.1795 | 2685521.6068 | 1246156.2637 | 2685526.6198 | 1246157.0477 | 2685530.1206 | 1246158.0346
56 | 2685517.4491 | 1245948.5172 | 2685540.7036 | 1245970.3478
57 | 2685517.4491 | 1245948.5172 | 2685500.5079 | 1245964.6433
58 | 2685547.771 | 1245976.9825 | 2685540.7036 | 1245970.3478
59 | 2685483.987 | 1245980.3695 | 2685500.5079 | 1245964.6433
60 | 2685458.0966 | 1246007.9834 | 2685456.7447 | 1246006.3739 | 2685460.6211 | 1246002.6715
61 | 2685460.6211 | 1246002.6715 | 2685471.9527 | 1245991.8558
62 | 2685458.0966 | 1246007.9834 | 2685466.8468 | 1246018.9176 | 2685467.7849 | 1246024.6019 | 2685466.9101 | 1246030.2491 | 2685464.3679 | 1246033.9657
63 | 2685483.987 | 1245980.3695 | 2685471.9527 | 1245991.8558
64 | 2685459.6176 | 1246040.9104 | 2685464.3679 | 1246033.9657
65 | 2685455.0705 | 1246047.5579 | 2685438.2898 | 1246070.49
66 | 2685445.6234 | 1246134.8325 | 2685465.2717 | 1246142.3081 | 2685468.9507 | 1246143.7096
67 | 2685694.7254 | 1246178.5066 | 2685689.3657 | 1246178.6791 | 2685677.0856 | 1246179.5743
68 | 2685464.5278 | 1246201.7635 | 2685462.1663 | 1246202.9501
69 | 2685680.5016 | 1246166.4994 | 2685681.4359 | 1246166.4333 | 2685689.203 | 1246165.8835
70 | 2685682.8125 | 1246104.652 | 2685686.8168 | 1246100.996
71 | 2685636.8839 | 1246169.5882 | 2685637.9729 | 1246169.5111
72 | 2685663.7834 | 1246167.6833 | 2685680.5016 | 1246166.4994
73 | 2685663.7834 | 1246167.6833 | 2685655.0056 | 1246168.3049
74 | 2685655.0056 | 1246168.3049 | 2685637.9729 | 1246169.5111
75 | 2685535.0463 | 1246102.6017 | 2685535.0768 | 1246102.5762
76 | 2685535.0463 | 1246102.6017 | 2685533.3523 | 1246104.016
77 | 2685535.0768 | 1246102.5762 | 2685535.1148 | 1246102.5445
78 | 2685533.3523 | 1246104.016 | 2685525.8394 | 1246110.2883
79 | 2685552.1427 | 1246088.3284 | 2685535.1148 | 1246102.5445
80 | 2685516.4036 | 1246118.166 | 2685525.8394 | 1246110.2883
81 | 2685552.1427 | 1246088.3284 | 2685552.7377 | 1246087.8317
82 | 2685505.7059 | 1246127.0972 | 2685516.4036 | 1246118.166
83 | 2685552.7377 | 1246087.8317 | 2685568.8243 | 1246074.4014
84 | 2685480.683 | 1246148.179 | 2685496.6536 | 1246134.6547 | 2685505.7059 | 1246127.0972
85 | 2685483.987 | 1245980.3695 | 2685511.4438 | 1246004.9335
86 | 2685520.8699 | 1246007.8213 | 2685512.0562 | 1246005.4814 | 2685511.4438 | 1246004.9335
87 | 2685571.1713 | 1245991.8127 | 2685554.8486 | 1245983.6268 | 2685547.771 | 1245976.9825
88 | 2685571.1713 | 1245991.8127 | 2685574.8203 | 1245997.5918 | 2685585.1981 | 1245989.5873
89 | 2685585.1981 | 1245989.5873 | 2685598.2165 | 1245979.5461
90 | 2685639.4723 | 1246013.8368 | 2685627.036 | 1245998.8322
91 | 2685639.4723 | 1246013.8368 | 2685650.1205 | 1246004.7728 | 2685652.7598 | 1246002.9385
92 | 2685639.4723 | 1246013.8368 | 2685633.8629 | 1246018.7223
93 | 2685455.0705 | 1246047.5579 | 2685455.0705 | 1246047.5579 | 2685459.6176 | 1246040.9104
94 | 2685480.683 | 1246148.179 | 2685468.9507 | 1246143.7096
95 | 2685480.683 | 1246148.179 | 2685485.9734 | 1246150.1567 | 2685493.1627 | 1246151.9616 | 2685501.0108 | 1246153.1423 | 2685509.7923 | 1246154.4732
96 | 2685509.7923 | 1246154.4732 | 2685521.051 | 1246156.1795
97 | 2685618.5276 | 1246032.0786 | 2685607.1511 | 1246041.9869
98 | 2685598.4576 | 1246049.5585 | 2685607.1511 | 1246041.9869
99 | 2685633.8629 | 1246018.7223 | 2685618.5276 | 1246032.0786
100 | 2685595.605 | 1246052.043 | 2685598.4576 | 1246049.5585
101 | 2685616.4159 | 1246077.9736 | 2685595.605 | 1246052.043
102 | 2685595.605 | 1246052.043 | 2685587.9639 | 1246058.4223
103 | 2685616.4159 | 1246077.9736 | 2685629.3685 | 1246069.3921
104 | 2685616.4159 | 1246077.9736 | 2685613.3476 | 1246083.055
105 | 2685581.0936 | 1246064.1581 | 2685587.9639 | 1246058.4223
106 | 2685629.3685 | 1246069.3921 | 2685632.1838 | 1246067.5268 | 2685636.2667 | 1246064.3866
107 | 2685613.3476 | 1246083.055 | 2685600.8155 | 1246103.8098
108 | 2685581.0936 | 1246064.1581 | 2685571.9869 | 1246071.7611
109 | 2685565.7578 | 1246241.7573 | 2685564.3962 | 1246244.457 | 2685561.4552 | 1246250.7171
110 | 2685561.4552 | 1246250.7171 | 2685557.5245 | 1246259.0835
111 | 2685553.8423 | 1246266.9214 | 2685557.5245 | 1246259.0835
112 | 2685564.6281 | 1246233.9403 | 2685560.6616 | 1246242.2145
113 | 2685568.8243 | 1246074.4014 | 2685569.0843 | 1246074.1843
114 | 2685569.0843 | 1246074.1843 | 2685569.1112 | 1246074.1619
115 | 2685569.1112 | 1246074.1619 | 2685571.9869 | 1246071.7611
116 | 2685595.5758 | 1246112.4874 | 2685586.9338 | 1246126.7997
117 | 2685595.5758 | 1246112.4874 | 2685595.6977 | 1246112.2855
118 | 2685583.7084 | 1246132.1414 | 2685586.9338 | 1246126.7997
119 | 2685600.8155 | 1246103.8098 | 2685595.6977 | 1246112.2855
120 | 2685636.2667 | 1246064.3866 | 2685645.5429 | 1246057.2523
121 | 2685645.5429 | 1246057.2523 | 2685649.6954 | 1246054.0586 | 2685654.8147 | 1246050.1186
122 | 2685556.5422 | 1246250.5465 | 2685552.3856 | 1246258.7907
123 | 2685560.6616 | 1246242.2145 | 2685559.0849 | 1246245.5034 | 2685556.5422 | 1246250.5465
124 | 2685657.9447 | 1246047.7096 | 2685654.8147 | 1246050.1186
125 | 2685666.7412 | 1246040.9395 | 2685657.9447 | 1246047.7096

## bus_geodata
| x | y | coords
0 | 2685589.1007 | 1246190.2515
1 | 2685595.3071 | 1246188.2948
2 | 2685586.336 | 1246191.123
3 | 2685600.9237 | 1246186.519
4 | 2685579.4243 | 1246197.3057
5 | 2685582.5147 | 1246179.4926
6 | 2685657.8355 | 1246180.9776
7 | 2685623.7721 | 1246203.5254
8 | 2685627.2664 | 1246209.2784
9 | 2685634.0496 | 1246213.4615
10 | 2685570.908 | 1246176.4785
11 | 2685590.3679 | 1246177.0881
12 | 2685574.8312 | 1246199.3631
13 | 2685578.6448 | 1246216.2054
14 | 2685560.3731 | 1246190.2812
15 | 2685565.4414 | 1246200.3173
16 | 2685540.1429 | 1246200.3372
17 | 2685504.1101 | 1246184.4545
18 | 2685551.337 | 1246166.5902
19 | 2685492.8524 | 1246172.8447
20 | 2685473.1523 | 1246148.5708
21 | 2685455.1184 | 1246151.1462
22 | 2685405.3591 | 1246115.4921
23 | 2685697.0204 | 1246257.5034
24 | 2685662.0595 | 1246230.1919
25 | 2685716.373 | 1246237.2875
26 | 2685514.0539 | 1246226.0901
27 | 2685479.6442 | 1246230.6916
28 | 2685466.6378 | 1246205.808
29 | 2685491.0193 | 1246224.9591
30 | 2685711.4384 | 1246164.3096
31 | 2685697.9598 | 1246165.2636
32 | 2685704.9236 | 1246128.9976
33 | 2685627.9537 | 1246172.0651
34 | 2685600.1008 | 1246174.7076
35 | 2685630.4459 | 1246170.0441
36 | 2685668.1539 | 1246180.2254
37 | 2685636.4234 | 1246214.9302
38 | 2685568.6983 | 1246225.4514
39 | 2685578.3948 | 1246216.7012
40 | 2685512.587 | 1246214.0901
41 | 2685578.3303 | 1246141.0481
42 | 2685581.9852 | 1246134.9951
43 | 2685530.1206 | 1246158.0346
44 | 2685517.4491 | 1245948.5172
45 | 2685540.7036 | 1245970.3478
46 | 2685500.5079 | 1245964.6433
47 | 2685460.6211 | 1246002.6714
48 | 2685458.0966 | 1246007.9834
49 | 2685471.9527 | 1245991.8558
50 | 2685464.3679 | 1246033.9657
51 | 2685438.2898 | 1246070.49
52 | 2685445.6234 | 1246134.8325
53 | 2685728.7088 | 1246215.091
54 | 2685694.7254 | 1246178.5066
55 | 2685677.0856 | 1246179.5743
56 | 2685654.7524 | 1246225.5862
57 | 2685513.6372 | 1246226.299
58 | 2685475.4409 | 1246198.3849
59 | 2685464.5278 | 1246201.7635
60 | 2685689.203 | 1246165.8835
61 | 2685686.8168 | 1246100.996
62 | 2685636.8839 | 1246169.5882
63 | 2685680.5016 | 1246166.4994
64 | 2685663.7834 | 1246167.6833
65 | 2685655.0056 | 1246168.3049
66 | 2685637.9729 | 1246169.5111
67 | 2685535.0463 | 1246102.6017
68 | 2685535.0768 | 1246102.5762
69 | 2685533.3523 | 1246104.016
70 | 2685535.1148 | 1246102.5445
71 | 2685525.8394 | 1246110.2883
72 | 2685552.1427 | 1246088.3284
73 | 2685516.4036 | 1246118.166
74 | 2685552.7377 | 1246087.8317
75 | 2685505.7059 | 1246127.0972
76 | 2685483.987 | 1245980.3695
77 | 2685511.4438 | 1246004.9335
78 | 2685520.8699 | 1246007.8213
79 | 2685547.771 | 1245976.9825
80 | 2685571.1713 | 1245991.8127
81 | 2685598.2165 | 1245979.5461
82 | 2685585.1981 | 1245989.5873
83 | 2685627.036 | 1245998.8322
84 | 2685639.4723 | 1246013.8368
85 | 2685459.6176 | 1246040.9104
86 | 2685455.0705 | 1246047.5579
87 | 2685468.9507 | 1246143.7096
88 | 2685480.683 | 1246148.179
89 | 2685509.7923 | 1246154.4732
90 | 2685607.1511 | 1246041.9869
91 | 2685618.5276 | 1246032.0786
92 | 2685598.4576 | 1246049.5585
93 | 2685633.8629 | 1246018.7223
94 | 2685595.605 | 1246052.043
95 | 2685616.4159 | 1246077.9736
96 | 2685587.9639 | 1246058.4223
97 | 2685652.7598 | 1246002.9385
98 | 2685629.3685 | 1246069.3921
99 | 2685613.3476 | 1246083.055
100 | 2685581.0936 | 1246064.1581
101 | 2685682.8125 | 1246104.652
102 | 2685565.7578 | 1246241.7573
103 | 2685561.4552 | 1246250.7171
104 | 2685557.5245 | 1246259.0835
105 | 2685564.6281 | 1246233.9403
106 | 2685568.8243 | 1246074.4014
107 | 2685569.0843 | 1246074.1843
108 | 2685569.1112 | 1246074.1619
109 | 2685571.9869 | 1246071.7611
110 | 2685521.051 | 1246156.1795
111 | 2685595.5758 | 1246112.4874
112 | 2685586.9338 | 1246126.7997
113 | 2685595.6977 | 1246112.2855
114 | 2685583.7084 | 1246132.1414
115 | 2685600.8155 | 1246103.8098
116 | 2685636.2667 | 1246064.3866
117 | 2685645.5429 | 1246057.2523
118 | 2685620.6058 | 1246249.1992
119 | 2685552.3856 | 1246258.7907
120 | 2685556.5422 | 1246250.5465
121 | 2685462.1663 | 1246202.9501
122 | 2685654.8147 | 1246050.1186
123 | 2685657.9447 | 1246047.7096
124 | 2685666.7412 | 1246040.9395
125 | 2685560.6616 | 1246242.2145
126 | 2685553.8423 | 1246266.9214
127 | 2685570.908 | 1246176.4785

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97469 | -0.48614 | 0.0030054 | 0.00075321
1 | 0.97442 | -0.49151 | 0 | 0
2 | 0.97482 | -0.48359 | 0 | 0
3 | 0.97417 | -0.49636 | 0 | 0
4 | 0.97413 | -0.49728 | 0 | 0
5 | 0.97552 | -0.46988 | 0 | 0
6 | 0.97356 | -0.50846 | 0.0042745 | 0.0010713
7 | 0.97326 | -0.51428 | 0.0064331 | 0.0016123
8 | 0.97282 | -0.52314 | 0.0031518 | 0.00078991
9 | 0.97284 | -0.52268 | 0 | 0
10 | 0.9765 | -0.45074 | 0 | 0
11 | 0.97534 | -0.47342 | 0.0045699 | 0.0011453
12 | 0.97385 | -0.50275 | 0 | 0
13 | 0.97385 | -0.50267 | 0.0026453 | 0.00066298
14 | 0.97299 | -0.51972 | 0 | 0
15 | 0.97341 | -0.51148 | 0 | 0
16 | 0.97215 | -0.53629 | 0.015595 | 0.0039085
17 | 0.97604 | -0.45965 | 0 | 0
18 | 0.97739 | -0.43321 | 0.0045922 | 0.0011509
19 | 0.97586 | -0.46324 | 0.005944 | 0.0014897
20 | 0.97843 | -0.41305 | 0 | 0
21 | 0.97836 | -0.41441 | 0.0036927 | 0.00092548
22 | 0.9787 | -0.40762 | 0 | 0
23 | 0.97158 | -0.54759 | 0 | 0
24 | 0.97221 | -0.53512 | 0.0030487 | 0.00076409
25 | 0.97117 | -0.55564 | 0.0082747 | 0.0020738
26 | 0.97306 | -0.51834 | 0.0025497 | 0.00063901
27 | 0.97091 | -0.56078 | 0 | 0
28 | 0.97064 | -0.56623 | 0 | 0
29 | 0.97104 | -0.55831 | 0.0080259 | 0.0020115
30 | 0.97161 | -0.54694 | 0 | 0
31 | 0.97188 | -0.54149 | 0.0022425 | 0.00056201
32 | 0.97086 | -0.56176 | 0.0048453 | 0.0012144
33 | 0.9739 | -0.50174 | 0 | 0
34 | 0.97494 | -0.48122 | 0.0025011 | 0.00062683
35 | 0.97378 | -0.50409 | 0.0023156 | 0.00058035
36 | 0.97349 | -0.50984 | 0.0024455 | 0.0006129
37 | 0.97278 | -0.5239 | 0 | 0
38 | 0.97351 | -0.50954 | 0.0029226 | 0.00073247
39 | 0.97385 | -0.50279 | 0.0023319 | 0.00058443
40 | 0.97145 | -0.55005 | 0.0056892 | 0.0014258
41 | 0.9999 | -0.0020187 | 0.003818 | 0.00095687
42 | 0.99992 | -0.0015481 | 0.0029551 | 0.00074061
43 | 0.97835 | -0.41446 | 0.0030961 | 0.00077597
44 | 0.97213 | -0.53678 | 0 | 0
45 | 0.97141 | -0.55097 | 0.0094534 | 0.0023692
46 | 0.97265 | -0.52639 | 0.0069753 | 0.0017482
47 | 0.97524 | -0.47544 | 0 | 0
48 | 0.97572 | -0.46599 | 0 | 0
49 | 0.97423 | -0.49532 | 0.010277 | 0.0025755
50 | 0.97669 | -0.44702 | 0.00499 | 0.0012506
51 | 0.97753 | -0.43048 | 0.0066301 | 0.0016617
52 | 0.97968 | -0.38854 | 0.0052462 | 0.0013148
53 | 0.971 | -0.55902 | 0.0068271 | 0.001711
54 | 0.97341 | -0.51139 | 0.0023392 | 0.00058625
55 | 0.97345 | -0.51063 | 0.0024388 | 0.00061123
56 | 0.97236 | -0.53223 | 0.0030949 | 0.00077565
57 | 0.97306 | -0.51837 | 0.0039302 | 0.00098501
58 | 0.9706 | -0.56702 | 0.0037063 | 0.00092888
59 | 0.97061 | -0.5668 | 0.0033508 | 0.00083979
60 | 0.97208 | -0.53759 | 0.0022494 | 0.00056375
61 | 0.9702 | -0.57473 | 0.0094108 | 0.0023586
62 | 0.97355 | -0.50855 | 0.0025558 | 0.00064055
63 | 0.9723 | -0.53335 | 0.0021761 | 0.00054537
64 | 0.97274 | -0.52454 | 0.0022064 | 0.00055298
65 | 0.97299 | -0.51956 | 0.0020784 | 0.0005209
66 | 0.97352 | -0.50925 | 0.0022092 | 0.00055367
67 | 0.98554 | -0.27499 | 0.0023403 | 0.00058653
68 | 0.98554 | -0.27493 | 0.0019848 | 0.00049745
69 | 0.98538 | -0.27808 | 0.0024809 | 0.00062177
70 | 0.98555 | -0.27486 | 0.002061 | 0.00051653
71 | 0.98467 | -0.29172 | 0.003605 | 0.00090349
72 | 0.9872 | -0.24316 | 0.0024046 | 0.00060266
73 | 0.9838 | -0.30867 | 0.0042911 | 0.0010755
74 | 0.98725 | -0.24204 | 0.0038554 | 0.00096624
75 | 0.98281 | -0.32766 | 0.0070481 | 0.0017664
76 | 0.97331 | -0.51333 | 0 | 0
77 | 0.97236 | -0.53221 | 0.0047808 | 0.0011982
78 | 0.97215 | -0.53643 | 0.023037 | 0.0057735
79 | 0.97128 | -0.5536 | 0.0057326 | 0.0014367
80 | 0.97104 | -0.5582 | 0 | 0
81 | 0.97081 | -0.56284 | 0.0044373 | 0.0011121
82 | 0.97088 | -0.56149 | 0.0044803 | 0.0011229
83 | 0.99032 | -0.18375 | 0.0079402 | 0.00199
84 | 0.99046 | -0.181 | 0 | 0
85 | 0.97683 | -0.44417 | 0.0041282 | 0.0010346
86 | 0.97698 | -0.44129 | 0.005053 | 0.0012664
87 | 0.98026 | -0.37733 | 0.0063634 | 0.0015948
88 | 0.98056 | -0.37134 | 0 | 0
89 | 0.97924 | -0.39709 | 0.0035955 | 0.00090111
90 | 0.99118 | -0.16716 | 0.0049629 | 0.0012438
91 | 0.99086 | -0.17333 | 0.0063511 | 0.0015917
92 | 0.99147 | -0.16143 | 0.0037354 | 0.00093618
93 | 0.99055 | -0.17936 | 0.0043111 | 0.0010805
94 | 0.99158 | -0.1593 | 0 | 0
95 | 0.99447 | -0.10438 | 0 | 0
96 | 0.99079 | -0.17442 | 0.0037325 | 0.00093545
97 | 0.99039 | -0.18236 | 0.0044513 | 0.0011156
98 | 0.99399 | -0.11375 | 0.004524 | 0.0011338
99 | 0.99503 | -0.093703 | 0.0060854 | 0.0015252
100 | 0.99008 | -0.18789 | 0.0045013 | 0.0011281
101 | 0.97017 | -0.57549 | 0.0075984 | 0.0019043
102 | 0.97359 | -0.50796 | 0.0025532 | 0.00063988
103 | 0.97352 | -0.50932 | 0.0024805 | 0.00062166
104 | 0.97347 | -0.51017 | 0.0024401 | 0.00061154
105 | 0.97342 | -0.51129 | 0.0024009 | 0.00060171
106 | 0.98884 | -0.21161 | 0.0024764 | 0.00062064
107 | 0.98887 | -0.21112 | 0.0019883 | 0.00049831
108 | 0.98887 | -0.21107 | 0.0019831 | 0.00049701
109 | 0.98916 | -0.20553 | 0.0024444 | 0.00061262
110 | 0.97875 | -0.40674 | 0.0035214 | 0.00088254
111 | 0.99835 | -0.031021 | 0.0039371 | 0.00098673
112 | 1 | 0 | -0.44576 | -0.11457
113 | 0.99833 | -0.031455 | 0.0029279 | 0.0007338
114 | 0.99994 | -0.0011545 | 0.0038409 | 0.00096263
115 | 0.99737 | -0.049577 | 0.0037137 | 0.00093075
116 | 0.99376 | -0.11821 | 0.004033 | 0.0010108
117 | 0.99348 | -0.12351 | 0.0062027 | 0.0015545
118 | 0.97268 | -0.52574 | 0.0025948 | 0.00065032
119 | 0.97328 | -0.51395 | 0.0028356 | 0.00071066
120 | 0.97331 | -0.51347 | 0.0023618 | 0.00059192
121 | 0.9706 | -0.56697 | 0.0034342 | 0.0008607
122 | 0.99327 | -0.12752 | 0.0040121 | 0.0010055
123 | 0.99322 | -0.1286 | 0.0050706 | 0.0012708
124 | 0.99311 | -0.13063 | 0.010351 | 0.0025941
125 | 0.97335 | -0.51258 | 0.0024806 | 0.00062169
126 | 0.97345 | -0.51057 | 0.0025377 | 0.000636
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.04502 | 0.011317 | -0.045009 | -0.01131 | 1.1532e-05 | 7.2994e-06 | 0.068743 | 0.068743 | 0.068743 | 0.97469 | -0.48614 | 0.97442 | -0.49151 | 18.8853
1 | -0.048026 | -0.01207 | 0.048032 | 0.012074 | 5.8455e-06 | 3.705e-06 | 0.073331 | 0.073331 | 0.073331 | 0.97469 | -0.48614 | 0.97482 | -0.48359 | 20.1458
2 | 0.045009 | 0.01131 | -0.044998 | -0.011303 | 1.0411e-05 | 6.5899e-06 | 0.068743 | 0.068743 | 0.068743 | 0.97442 | -0.49151 | 0.97417 | -0.49636 | 18.8853
3 | 0.074445 | 0.01872 | -0.074396 | -0.018689 | 4.8618e-05 | 3.0991e-05 | 0.11366 | 0.11366 | 0.11366 | 0.97482 | -0.48359 | 0.97413 | -0.49728 | 31.225
4 | -0.12248 | -0.030794 | 0.12256 | 0.030845 | 8.0258e-05 | 5.106e-05 | 0.18699 | 0.18699 | 0.18699 | 0.97482 | -0.48359 | 0.97552 | -0.46988 | 25.6854
5 | 0.011505 | 0.0028852 | -0.011499 | -0.0028817 | 6.6353e-06 | 3.5338e-06 | 0.017575 | 0.017575 | 0.017575 | 0.97417 | -0.49636 | 0.97356 | -0.50846 | 4.8283
6 | 0.033493 | 0.0084178 | -0.033464 | -0.0083999 | 2.8636e-05 | 1.7964e-05 | 0.051168 | 0.051168 | 0.051168 | 0.97417 | -0.49636 | 0.97326 | -0.51428 | 14.0572
7 | 0.0594 | 0.014929 | -0.059385 | -0.014919 | 1.5507e-05 | 9.8621e-06 | 0.090752 | 0.090752 | 0.090752 | 0.97413 | -0.49728 | 0.97385 | -0.50275 | 24.9318
8 | 0.014996 | 0.0037601 | -0.014992 | -0.0037579 | 3.8505e-06 | 2.2208e-06 | 0.022907 | 0.022907 | 0.022907 | 0.97413 | -0.49728 | 0.97385 | -0.50267 | 6.2932
9 | -0.16967 | -0.04271 | 0.16982 | 0.042809 | 0.0001554 | 9.9148e-05 | 0.25887 | 0.25887 | 0.25887 | 0.97552 | -0.46988 | 0.9765 | -0.45074 | 35.5596
10 | 0.047113 | 0.011865 | -0.047105 | -0.01186 | 7.9578e-06 | 4.8879e-06 | 0.071885 | 0.071885 | 0.071885 | 0.97552 | -0.46988 | 0.97534 | -0.47342 | 9.8743
11 | 0.0072242 | 0.0018104 | -0.0072238 | -0.0018102 | 4.73e-07 | 1.7408e-07 | 0.011042 | 0.011042 | 0.011042 | 0.97356 | -0.50846 | 0.97349 | -0.50984 | 3.0334
12 | 0.027031 | 0.0067876 | -0.027021 | -0.0067809 | 1.0822e-05 | 6.7163e-06 | 0.041333 | 0.041333 | 0.041333 | 0.97326 | -0.51428 | 0.97284 | -0.52268 | 11.3551
13 | -0.0031518 | -0.00078991 | 0.0031518 | 0.00078985 | 6.9457e-08 | -5.4495e-08 | 0.0048209 | 0.0048209 | 0.0048209 | 0.97282 | -0.52314 | 0.97284 | -0.52268 | 1.3244
14 | 0.023869 | 0.005991 | -0.023867 | -0.0059901 | 1.3923e-06 | 8.5648e-07 | 0.036512 | 0.036512 | 0.036512 | 0.97284 | -0.52268 | 0.97278 | -0.5239 | 10.0307
15 | 0.0059476 | 0.0014905 | -0.005945 | -0.0014899 | 2.5243e-06 | 5.9087e-07 | 0.0090631 | 0.0090634 | 0.0090634 | 0.9765 | -0.45074 | 0.97604 | -0.45965 | 2.49
16 | -0.17577 | -0.0443 | 0.17592 | 0.044393 | 0.00014759 | 9.3356e-05 | 0.26794 | 0.26794 | 0.26794 | 0.9765 | -0.45074 | 0.97739 | -0.43321 | 18.4023
17 | 0.042535 | 0.010715 | -0.042519 | -0.010705 | 1.5863e-05 | 1.0027e-05 | 0.064913 | 0.064913 | 0.064913 | 0.97534 | -0.47342 | 0.97494 | -0.48122 | 17.8332
18 | 0.013007 | 0.0032614 | -0.013003 | -0.003259 | 4.2091e-06 | 2.3404e-06 | 0.019875 | 0.019875 | 0.019875 | 0.97385 | -0.50275 | 0.97351 | -0.50954 | 5.4603
19 | 0.046378 | 0.011658 | -0.046358 | -0.011646 | 1.933e-05 | 1.2243e-05 | 0.070876 | 0.070876 | 0.070876 | 0.97385 | -0.50275 | 0.97341 | -0.51148 | 19.4716
20 | 0.012347 | 0.0030949 | -0.012346 | -0.0030949 | 7.4109e-08 | 4.0521e-08 | 0.018865 | 0.018865 | 0.018865 | 0.97385 | -0.50267 | 0.97385 | -0.50279 | 5.1828
21 | -0.039861 | -0.010011 | 0.039876 | 0.010021 | 1.5676e-05 | 9.8927e-06 | 0.060968 | 0.060968 | 0.060968 | 0.97299 | -0.51972 | 0.97341 | -0.51148 | 16.7493
22 | 0.039861 | 0.010011 | -0.039829 | -0.0099914 | 3.1491e-05 | 1.9874e-05 | 0.060968 | 0.060968 | 0.060968 | 0.97299 | -0.51972 | 0.97215 | -0.53629 | 16.7494
23 | 0.0064821 | 0.0016247 | -0.0064799 | -0.001624 | 2.1168e-06 | 6.4038e-07 | 0.009909 | 0.0099092 | 0.0099092 | 0.97341 | -0.51148 | 0.97306 | -0.51834 | 2.7223
24 | 0.024234 | 0.0060829 | -0.024218 | -0.0060731 | 1.5893e-05 | 9.7903e-06 | 0.037097 | 0.037097 | 0.037097 | 0.97215 | -0.53629 | 0.97145 | -0.55005 | 10.1915
25 | 0.005945 | 0.0014899 | -0.005944 | -0.0014897 | 1.0149e-06 | 2.3785e-07 | 0.0090634 | 0.0090636 | 0.0090636 | 0.97604 | -0.45965 | 0.97586 | -0.46324 | 2.49
26 | -0.18051 | -0.045544 | 0.18067 | 0.045647 | 0.00016223 | 0.00010268 | 0.27493 | 0.27493 | 0.27493 | 0.97739 | -0.43321 | 0.97835 | -0.41446 | 18.8824
27 | 0.003693 | 0.00092538 | -0.0036927 | -0.00092548 | 2.3821e-07 | -1.0045e-07 | 0.0056163 | 0.0056164 | 0.0056164 | 0.97843 | -0.41305 | 0.97836 | -0.41441 | 1.543
28 | -0.003693 | -0.00092538 | 0.0036939 | 0.00092498 | 9.5456e-07 | -4.0296e-07 | 0.0056163 | 0.0056159 | 0.0056163 | 0.97843 | -0.41305 | 0.9787 | -0.40762 | 1.5429
29 | 0.090431 | 0.022833 | -0.090332 | -0.022773 | 9.8915e-05 | 6.0506e-05 | 0.13755 | 0.13755 | 0.13755 | 0.9787 | -0.40762 | 0.97753 | -0.43048 | 9.4473
30 | -0.094125 | -0.023758 | 0.094211 | 0.023811 | 8.6137e-05 | 5.2872e-05 | 0.14317 | 0.14317 | 0.14317 | 0.9787 | -0.40762 | 0.97968 | -0.38854 | 9.833
31 | -0.015109 | -0.0037886 | 0.015118 | 0.0037938 | 8.984e-06 | 5.1953e-06 | 0.02314 | 0.02314 | 0.02314 | 0.97158 | -0.54759 | 0.97221 | -0.53512 | 6.3572
32 | 0.015109 | 0.0037886 | -0.015103 | -0.0037852 | 5.7938e-06 | 3.3508e-06 | 0.02314 | 0.023141 | 0.023141 | 0.97158 | -0.54759 | 0.97117 | -0.55564 | 6.3573
33 | -0.018166 | -0.0045579 | 0.018169 | 0.0045594 | 2.5044e-06 | 1.4957e-06 | 0.027806 | 0.027806 | 0.027806 | 0.97221 | -0.53512 | 0.97236 | -0.53223 | 7.6391
34 | 0.0068282 | 0.0017114 | -0.0068271 | -0.001711 | 1.0994e-06 | 3.7226e-07 | 0.010462 | 0.010462 | 0.010462 | 0.97117 | -0.55564 | 0.971 | -0.55902 | 2.8743
35 | 0.0039303 | 0.00098501 | -0.0039302 | -0.00098501 | 6.3144e-09 | -1.7492e-09 | 0.0060102 | 0.0060102 | 0.0060102 | 0.97306 | -0.51834 | 0.97306 | -0.51837 | 1.6512
36 | 0.010494 | 0.0026308 | -0.010492 | -0.0026294 | 2.7223e-06 | 1.3953e-06 | 0.016084 | 0.016084 | 0.016084 | 0.97091 | -0.56078 | 0.97064 | -0.56623 | 4.4187
37 | -0.010494 | -0.0026308 | 0.010496 | 0.0026314 | 1.2357e-06 | 6.3329e-07 | 0.016084 | 0.016084 | 0.016084 | 0.97091 | -0.56078 | 0.97104 | -0.55831 | 4.4187
38 | 0.0037064 | 0.00092883 | -0.0037063 | -0.00092888 | 1.3918e-07 | -5.3009e-08 | 0.005682 | 0.0056821 | 0.0056821 | 0.97064 | -0.56623 | 0.9706 | -0.56702 | 1.561
39 | 0.0067853 | 0.0017005 | -0.0067851 | -0.0017005 | 1.851e-07 | 6.2081e-08 | 0.010402 | 0.010402 | 0.010402 | 0.97064 | -0.56623 | 0.97061 | -0.5668 | 2.8577
40 | -0.018522 | -0.0046429 | 0.018529 | 0.0046472 | 7.296e-06 | 4.3705e-06 | 0.028383 | 0.028383 | 0.028383 | 0.97104 | -0.55831 | 0.97145 | -0.55005 | 7.7975
41 | -0.021881 | -0.005493 | 0.021886 | 0.0054965 | 5.6912e-06 | 3.475e-06 | 0.033514 | 0.033514 | 0.033514 | 0.97161 | -0.54694 | 0.97188 | -0.54149 | 9.2071
42 | 0.021881 | 0.005493 | -0.021865 | -0.0054836 | 1.5453e-05 | 9.4356e-06 | 0.033514 | 0.033514 | 0.033514 | 0.97161 | -0.54694 | 0.97086 | -0.56176 | 9.2071
43 | -0.024129 | -0.0060585 | 0.024133 | 0.0060613 | 4.4939e-06 | 2.7673e-06 | 0.036947 | 0.036947 | 0.036947 | 0.97188 | -0.54149 | 0.97208 | -0.53759 | 10.1503
44 | 0.01702 | 0.0042692 | -0.017009 | -0.004263 | 1.0512e-05 | 6.2189e-06 | 0.026088 | 0.026088 | 0.026088 | 0.97086 | -0.56176 | 0.9702 | -0.57473 | 7.167
45 | -0.039979 | -0.010053 | 0.040018 | 0.010078 | 3.9222e-05 | 2.4753e-05 | 0.061096 | 0.061095 | 0.061096 | 0.9739 | -0.50174 | 0.97494 | -0.48122 | 16.7845
46 | 0.039979 | 0.010053 | -0.039974 | -0.01005 | 4.4914e-06 | 2.8346e-06 | 0.061096 | 0.061096 | 0.061096 | 0.9739 | -0.50174 | 0.97378 | -0.50409 | 16.7845
47 | 0.037659 | 0.0094698 | -0.037651 | -0.0094647 | 8.018e-06 | 5.0512e-06 | 0.057557 | 0.057557 | 0.057557 | 0.97378 | -0.50409 | 0.97355 | -0.50855 | 15.8124
48 | 0.0047783 | 0.0011973 | -0.0047781 | -0.0011973 | 1.7914e-07 | 3.3142e-09 | 0.0073037 | 0.0073037 | 0.0073037 | 0.97349 | -0.50984 | 0.97345 | -0.51063 | 2.0065
49 | 0.002595 | 0.00064998 | -0.0025948 | -0.00065032 | 2.2789e-07 | -3.3292e-07 | 0.0039694 | 0.0039695 | 0.0039695 | 0.97278 | -0.5239 | 0.97268 | -0.52574 | 1.0905
50 | 0.021272 | 0.0053402 | -0.021264 | -0.005335 | 8.4438e-06 | 5.1402e-06 | 0.032542 | 0.032543 | 0.032543 | 0.97278 | -0.5239 | 0.97236 | -0.53223 | 8.9403
51 | 0.01008 | 0.0025266 | -0.01008 | -0.0025261 | 8.3814e-07 | 4.1937e-07 | 0.015408 | 0.015408 | 0.015408 | 0.97351 | -0.50954 | 0.97342 | -0.51129 | 4.233
52 | 0.010015 | 0.0025104 | -0.010012 | -0.0025092 | 2.4642e-06 | 1.228e-06 | 0.015302 | 0.015302 | 0.015302 | 0.97385 | -0.50279 | 0.97359 | -0.50796 | 4.204
53 | -0.003818 | -0.00095687 | 0.003818 | 0.00095683 | 8.5599e-08 | -3.7964e-08 | 0.0056818 | 0.0056818 | 0.0056818 | 0.9999 | -0.0020187 | 0.99992 | -0.0015481 | 1.5609
54 | -0.0067731 | -0.0016974 | 0.0067732 | 0.0016975 | 1.27e-07 | 3.7552e-08 | 0.010079 | 0.010079 | 0.010079 | 0.99992 | -0.0015481 | 0.99994 | -0.0011545 | 2.769
55 | -0.18377 | -0.046423 | 0.18384 | 0.046466 | 6.7982e-05 | 4.3042e-05 | 0.27964 | 0.27964 | 0.27964 | 0.97835 | -0.41446 | 0.97875 | -0.40674 | 19.2058
56 | 0.024125 | 0.0060535 | -0.024109 | -0.0060435 | 1.6313e-05 | 1.0045e-05 | 0.036931 | 0.036931 | 0.036931 | 0.97213 | -0.53678 | 0.97141 | -0.55097 | 10.1458
57 | -0.024125 | -0.0060535 | 0.024137 | 0.0060609 | 1.1963e-05 | 7.3659e-06 | 0.036931 | 0.036931 | 0.036931 | 0.97213 | -0.53678 | 0.97265 | -0.52639 | 10.1458
58 | 0.014656 | 0.0036743 | -0.014654 | -0.0036732 | 1.8322e-06 | 1.0526e-06 | 0.02245 | 0.02245 | 0.02245 | 0.97141 | -0.55097 | 0.97128 | -0.5536 | 6.1676
59 | -0.031113 | -0.0078091 | 0.031132 | 0.0078212 | 1.9381e-05 | 1.2121e-05 | 0.047602 | 0.047602 | 0.047602 | 0.97265 | -0.52639 | 0.97331 | -0.51333 | 13.0774
60 | -0.069372 | -0.017461 | 0.069404 | 0.017481 | 3.1369e-05 | 1.9983e-05 | 0.10587 | 0.10587 | 0.10587 | 0.97524 | -0.47544 | 0.97572 | -0.46599 | 29.0865
61 | 0.069372 | 0.017461 | -0.069306 | -0.017419 | 6.5847e-05 | 4.1947e-05 | 0.10587 | 0.10587 | 0.10587 | 0.97524 | -0.47544 | 0.97423 | -0.49532 | 29.0865
62 | -0.069404 | -0.017481 | 0.069467 | 0.017521 | 6.3017e-05 | 3.9581e-05 | 0.10587 | 0.10587 | 0.10587 | 0.97572 | -0.46599 | 0.97669 | -0.44702 | 14.5432
63 | 0.05903 | 0.014844 | -0.058979 | -0.014811 | 5.0733e-05 | 3.2262e-05 | 0.090179 | 0.090179 | 0.090179 | 0.97423 | -0.49532 | 0.97331 | -0.51333 | 24.7744
64 | -0.074457 | -0.018771 | 0.074467 | 0.018777 | 1.0157e-05 | 6.0795e-06 | 0.11348 | 0.11348 | 0.11348 | 0.97669 | -0.44702 | 0.97683 | -0.44417 | 7.7937
65 | 0.083702 | 0.021111 | -0.083659 | -0.021085 | 4.328e-05 | 2.6275e-05 | 0.12746 | 0.12746 | 0.12746 | 0.97753 | -0.43048 | 0.97698 | -0.44129 | 8.7542
66 | -0.099457 | -0.025126 | 0.099511 | 0.025159 | 5.3449e-05 | 3.2949e-05 | 0.15114 | 0.15113 | 0.15114 | 0.97968 | -0.38854 | 0.98026 | -0.37733 | 10.3802
67 | -0.0023392 | -0.00058625 | 0.0023393 | 0.00058609 | 8.4748e-08 | -1.6549e-07 | 0.0035758 | 0.0035757 | 0.0035758 | 0.97341 | -0.51139 | 0.97345 | -0.51063 | 0.98236
68 | 0.0034343 | 0.00086069 | -0.0034342 | -0.0008607 | 2.7473e-08 | -1.5081e-08 | 0.005265 | 0.005265 | 0.005265 | 0.97061 | -0.5668 | 0.9706 | -0.56697 | 1.4464
69 | -0.026383 | -0.006625 | 0.026388 | 0.0066283 | 5.3366e-06 | 3.3072e-06 | 0.04039 | 0.04039 | 0.04039 | 0.97208 | -0.53759 | 0.9723 | -0.53335 | 11.0962
70 | 0.0075987 | 0.0019045 | -0.0075984 | -0.0019043 | 2.7617e-07 | 1.0979e-07 | 0.011654 | 0.011654 | 0.011654 | 0.9702 | -0.57473 | 0.97017 | -0.57549 | 3.2017
71 | 0.035095 | 0.0088242 | -0.035094 | -0.0088235 | 1.1784e-06 | 7.4057e-07 | 0.053651 | 0.053651 | 0.053651 | 0.97355 | -0.50855 | 0.97352 | -0.50925 | 14.7392
72 | -0.028564 | -0.0071737 | 0.028576 | 0.0071812 | 1.2014e-05 | 7.4808e-06 | 0.04372 | 0.04372 | 0.04372 | 0.9723 | -0.53335 | 0.97274 | -0.52454 | 12.0111
73 | -0.030783 | -0.0077342 | 0.03079 | 0.0077387 | 7.3192e-06 | 4.575e-06 | 0.047096 | 0.047096 | 0.047096 | 0.97274 | -0.52454 | 0.97299 | -0.51956 | 12.9383
74 | -0.032868 | -0.0082596 | 0.032885 | 0.0082698 | 1.6184e-05 | 1.0146e-05 | 0.050274 | 0.050274 | 0.050274 | 0.97299 | -0.51956 | 0.97352 | -0.50925 | 13.8116
75 | -0.31836 | -0.081079 | 0.31836 | 0.081079 | 8.6377e-07 | 5.5077e-07 | 0.48113 | 0.48113 | 0.48113 | 0.98554 | -0.27499 | 0.98554 | -0.27493 | 33.045
76 | 0.31602 | 0.080492 | -0.31597 | -0.080462 | 4.7192e-05 | 3.009e-05 | 0.4776 | 0.4776 | 0.4776 | 0.98554 | -0.27499 | 0.98538 | -0.27808 | 32.8023
77 | -0.32034 | -0.081577 | 0.32034 | 0.081577 | 1.0876e-06 | 6.9352e-07 | 0.48413 | 0.48413 | 0.48413 | 0.98554 | -0.27493 | 0.98555 | -0.27486 | 33.2508
78 | 0.31349 | 0.07984 | -0.31328 | -0.079709 | 0.00020602 | 0.00013135 | 0.47385 | 0.47385 | 0.47385 | 0.98538 | -0.27808 | 0.98467 | -0.29172 | 32.545
79 | -0.32241 | -0.082094 | 0.3229 | 0.082409 | 0.0004937 | 0.00031484 | 0.48724 | 0.48724 | 0.48724 | 0.98555 | -0.27486 | 0.9872 | -0.24316 | 33.4645
80 | 0.30968 | 0.078806 | -0.30943 | -0.078644 | 0.00025284 | 0.00016119 | 0.46841 | 0.46841 | 0.46841 | 0.98467 | -0.29172 | 0.9838 | -0.30867 | 32.1708
81 | -0.3253 | -0.083011 | 0.32532 | 0.083023 | 1.7508e-05 | 1.1165e-05 | 0.49087 | 0.49087 | 0.49087 | 0.9872 | -0.24316 | 0.98725 | -0.24204 | 33.7134
82 | 0.30513 | 0.077569 | -0.30486 | -0.077391 | 0.00027876 | 0.0001777 | 0.46192 | 0.46192 | 0.46192 | 0.9838 | -0.30867 | 0.98281 | -0.32766 | 31.7251
83 | -0.32918 | -0.083989 | 0.32966 | 0.084298 | 0.00048465 | 0.0003091 | 0.49668 | 0.49668 | 0.49668 | 0.98725 | -0.24204 | 0.98884 | -0.21161 | 34.1125
84 | 0.29781 | 0.075625 | -0.29718 | -0.075227 | 0.00062461 | 0.0003981 | 0.45125 | 0.45125 | 0.45125 | 0.98281 | -0.32766 | 0.98056 | -0.37134 | 30.9922
85 | 0.027847 | 0.0069901 | -0.027822 | -0.0069746 | 2.5045e-05 | 1.5571e-05 | 0.042577 | 0.042577 | 0.042577 | 0.97331 | -0.51333 | 0.97236 | -0.53221 | 11.6971
86 | 0.023041 | 0.0057764 | -0.023037 | -0.0057735 | 4.635e-06 | 2.8431e-06 | 0.035261 | 0.035261 | 0.035261 | 0.97236 | -0.53221 | 0.97215 | -0.53643 | 9.6871
87 | 0.0089212 | 0.0022365 | -0.0089193 | -0.0022356 | 1.9592e-06 | 9.0786e-07 | 0.013668 | 0.013668 | 0.013668 | 0.97128 | -0.5536 | 0.97104 | -0.5582 | 3.7549
88 | 0.0089193 | 0.0022356 | -0.0089179 | -0.0022349 | 1.397e-06 | 6.4741e-07 | 0.013668 | 0.013668 | 0.013668 | 0.97104 | -0.5582 | 0.97088 | -0.56149 | 3.7549
89 | -0.0044373 | -0.0011121 | 0.0044375 | 0.0011121 | 2.8519e-07 | -2.0779e-08 | 0.0068012 | 0.0068012 | 0.0068012 | 0.97081 | -0.56284 | 0.97088 | -0.56149 | 1.8685
90 | -0.0079402 | -0.00199 | 0.0079412 | 0.0019904 | 1.0402e-06 | 4.1496e-07 | 0.011931 | 0.01193 | 0.011931 | 0.99032 | -0.18375 | 0.99046 | -0.181 | 3.2776
91 | 0.0044515 | 0.0011156 | -0.0044513 | -0.0011156 | 2.8844e-07 | -3.6719e-08 | 0.0066877 | 0.0066878 | 0.0066878 | 0.99046 | -0.181 | 0.99039 | -0.18236 | 1.8373
92 | -0.012393 | -0.003106 | 0.012394 | 0.0031065 | 9.6693e-07 | 5.2309e-07 | 0.018618 | 0.018618 | 0.018618 | 0.99046 | -0.181 | 0.99055 | -0.17936 | 5.1149
93 | -0.078595 | -0.019812 | 0.078606 | 0.019819 | 1.083e-05 | 6.528e-06 | 0.11977 | 0.11977 | 0.11977 | 0.97683 | -0.44417 | 0.97698 | -0.44129 | 8.2256
94 | -0.10587 | -0.026754 | 0.1059 | 0.026773 | 3.0431e-05 | 1.8843e-05 | 0.16079 | 0.16079 | 0.16079 | 0.98026 | -0.37733 | 0.98056 | -0.37134 | 11.0436
95 | 0.19128 | 0.048454 | -0.19104 | -0.048304 | 0.00023631 | 0.00014973 | 0.29045 | 0.29045 | 0.29045 | 0.98056 | -0.37134 | 0.97924 | -0.39709 | 19.9487
96 | 0.18745 | 0.047403 | -0.18736 | -0.047348 | 8.6707e-05 | 5.492e-05 | 0.28499 | 0.28499 | 0.28499 | 0.97924 | -0.39709 | 0.97875 | -0.40674 | 19.5735
97 | 0.023067 | 0.0057856 | -0.023061 | -0.0057815 | 6.7853e-06 | 4.1482e-06 | 0.034632 | 0.034632 | 0.034632 | 0.99118 | -0.16716 | 0.99086 | -0.17333 | 9.5143
98 | -0.02803 | -0.0070295 | 0.028038 | 0.0070342 | 7.6561e-06 | 4.7513e-06 | 0.042083 | 0.042082 | 0.042083 | 0.99118 | -0.16716 | 0.99147 | -0.16143 | 11.5611
99 | 0.01671 | 0.0041898 | -0.016705 | -0.0041869 | 4.8023e-06 | 2.8116e-06 | 0.025094 | 0.025094 | 0.025094 | 0.99086 | -0.17333 | 0.99055 | -0.17936 | 6.8941
100 | -0.031773 | -0.0079704 | 0.031777 | 0.0079724 | 3.2261e-06 | 2.0159e-06 | 0.047689 | 0.047689 | 0.047689 | 0.99147 | -0.16143 | 0.99158 | -0.1593 | 13.1013
101 | -0.37943 | -0.097116 | 0.38044 | 0.097762 | 0.001012 | 0.00064596 | 0.57011 | 0.57011 | 0.57011 | 0.99158 | -0.1593 | 0.99447 | -0.10438 | 39.1562
102 | 0.34765 | 0.089143 | -0.3474 | -0.088981 | 0.0002547 | 0.00016249 | 0.52243 | 0.52243 | 0.52243 | 0.99158 | -0.1593 | 0.99079 | -0.17442 | 35.881
103 | 0.034227 | 0.0085902 | -0.034211 | -0.0085807 | 1.5284e-05 | 9.5804e-06 | 0.051217 | 0.051217 | 0.051217 | 0.99447 | -0.10438 | 0.99399 | -0.11375 | 14.0707
104 | -0.41467 | -0.10635 | 0.41488 | 0.10649 | 0.00021484 | 0.00013719 | 0.62133 | 0.62133 | 0.62133 | 0.99447 | -0.10438 | 0.99503 | -0.093703 | 42.6738
105 | 0.34367 | 0.088045 | -0.34344 | -0.087902 | 0.00022411 | 0.00014297 | 0.51682 | 0.51682 | 0.51682 | 0.99079 | -0.17442 | 0.99008 | -0.18789 | 35.496
106 | 0.029687 | 0.0074469 | -0.029681 | -0.0074429 | 6.3171e-06 | 3.9324e-06 | 0.044445 | 0.044445 | 0.044445 | 0.99399 | -0.11375 | 0.99376 | -0.11821 | 12.2101
107 | -0.42097 | -0.10801 | 0.42187 | 0.10859 | 0.00090337 | 0.00057689 | 0.63043 | 0.63043 | 0.63043 | 0.99503 | -0.093703 | 0.99737 | -0.049577 | 43.2988
108 | 0.33894 | 0.086774 | -0.33865 | -0.08659 | 0.00028934 | 0.00018457 | 0.51006 | 0.51006 | 0.51006 | 0.99008 | -0.18789 | 0.98916 | -0.20553 | 35.0314
109 | 0.007459 | 0.0018693 | -0.0074585 | -0.0018691 | 4.8445e-07 | 1.8645e-07 | 0.0114 | 0.0114 | 0.0114 | 0.97359 | -0.50796 | 0.97352 | -0.50932 | 3.1319
110 | 0.004978 | 0.0012475 | -0.0049778 | -0.0012475 | 2.0069e-07 | 1.3511e-08 | 0.0076088 | 0.0076089 | 0.0076089 | 0.97352 | -0.50932 | 0.97347 | -0.51017 | 2.0904
111 | 0.0025377 | 0.00063593 | -0.0025377 | -0.000636 | 4.8864e-08 | -7.6387e-08 | 0.0038791 | 0.0038791 | 0.0038791 | 0.97347 | -0.51017 | 0.97345 | -0.51057 | 1.0657
112 | 0.0076787 | 0.0019244 | -0.0076782 | -0.0019242 | 4.741e-07 | 1.8937e-07 | 0.011738 | 0.011738 | 0.011738 | 0.97342 | -0.51129 | 0.97335 | -0.51258 | 3.2248
113 | -0.33214 | -0.084919 | 0.33215 | 0.084924 | 7.9517e-06 | 5.0717e-06 | 0.5004 | 0.5004 | 0.5004 | 0.98884 | -0.21161 | 0.98887 | -0.21112 | 34.3684
114 | -0.33413 | -0.085422 | 0.33413 | 0.085423 | 8.3233e-07 | 5.309e-07 | 0.5034 | 0.5034 | 0.5034 | 0.98887 | -0.21112 | 0.98887 | -0.21107 | 34.5739
115 | -0.33612 | -0.08592 | 0.33621 | 0.085977 | 9.0054e-05 | 5.7442e-05 | 0.50638 | 0.50638 | 0.50638 | 0.98887 | -0.21107 | 0.98916 | -0.20553 | 34.7788
116 | -0.43284 | -0.11149 | 0.43349 | 0.11191 | 0.00065451 | 0.00041801 | 0.6462 | 0.6462 | 0.6462 | 0.99835 | -0.031021 | 1 | 0 | 44.3821
117 | 0.4289 | 0.1105 | -0.42889 | -0.1105 | 9.0684e-06 | 5.7914e-06 | 0.64033 | 0.64033 | 0.64033 | 0.99835 | -0.031021 | 0.99833 | -0.031455 | 43.979
118 | 0.010615 | 0.0026604 | -0.010614 | -0.0026601 | 5.8378e-07 | 2.9176e-07 | 0.015795 | 0.015795 | 0.015795 | 1 | 0 | 0.99994 | -0.0011545 | 4.3393
119 | 0.42596 | 0.10976 | -0.42559 | -0.10952 | 0.00037542 | 0.00023975 | 0.63597 | 0.63597 | 0.63597 | 0.99833 | -0.031455 | 0.99737 | -0.049577 | 43.6793
120 | 0.025648 | 0.0064321 | -0.025641 | -0.0064282 | 6.473e-06 | 3.9911e-06 | 0.038406 | 0.038406 | 0.038406 | 0.99376 | -0.11821 | 0.99348 | -0.12351 | 10.5511
121 | 0.019439 | 0.0048736 | -0.019435 | -0.0048714 | 3.7189e-06 | 2.2287e-06 | 0.029116 | 0.029116 | 0.029116 | 0.99348 | -0.12351 | 0.99327 | -0.12752 | 7.9988
122 | -0.0028356 | -0.00071066 | 0.0028356 | 0.00071059 | 6.5069e-08 | -7.3099e-08 | 0.0043352 | 0.0043352 | 0.0043352 | 0.97328 | -0.51395 | 0.97331 | -0.51347 | 1.191
123 | -0.0051974 | -0.0013025 | 0.0051977 | 0.0013025 | 2.2008e-07 | 2.5322e-08 | 0.007946 | 0.0079459 | 0.007946 | 0.97331 | -0.51347 | 0.97335 | -0.51258 | 2.183
124 | 0.015423 | 0.0038659 | -0.015422 | -0.0038654 | 7.907e-07 | 4.5493e-07 | 0.023105 | 0.023105 | 0.023105 | 0.99327 | -0.12752 | 0.99322 | -0.1286 | 6.3476
125 | 0.010352 | 0.0025946 | -0.010351 | -0.0025941 | 1.0011e-06 | 4.9709e-07 | 0.015508 | 0.015509 | 0.015509 | 0.99322 | -0.1286 | 0.99311 | -0.13063 | 4.2606

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4485 | 0.11525

## res_load
| p_mw | q_mvar
0 | 0.0030054 | 0.00075321
1 | 0.0042745 | 0.0010713
2 | 0.0064331 | 0.0016123
3 | 0.0031518 | 0.00078991
4 | 0.0045699 | 0.0011453
5 | 0.0026453 | 0.00066298
6 | 0.015595 | 0.0039085
7 | 0.0045922 | 0.0011509
8 | 0.005944 | 0.0014897
9 | 0.0036927 | 0.00092548
10 | 0.0030487 | 0.00076409
11 | 0.0082747 | 0.0020738
12 | 0.0025497 | 0.00063901
13 | 0.0080259 | 0.0020115
14 | 0.0022425 | 0.00056201
15 | 0.0048453 | 0.0012144
16 | 0.0025011 | 0.00062683
17 | 0.0023156 | 0.00058035
18 | 0.0024455 | 0.0006129
19 | 0.0029226 | 0.00073247
20 | 0.0023319 | 0.00058443
21 | 0.0056892 | 0.0014258
22 | 0.003818 | 0.00095687
23 | 0.0029551 | 0.00074061
24 | 0.0030961 | 0.00077597
25 | 0.0094534 | 0.0023692
26 | 0.0069753 | 0.0017482
27 | 0.010277 | 0.0025755
28 | 0.00499 | 0.0012506
29 | 0.0066301 | 0.0016617
30 | 0.0052462 | 0.0013148
31 | 0.0068271 | 0.001711
32 | 0.0023392 | 0.00058625
33 | 0.0024388 | 0.00061123
34 | 0.0030949 | 0.00077565
35 | 0.0039302 | 0.00098501
36 | 0.0037063 | 0.00092888
37 | 0.0033508 | 0.00083979
38 | 0.0022494 | 0.00056375
39 | 0.0094108 | 0.0023586
40 | 0.0025558 | 0.00064055
41 | 0.0021761 | 0.00054537
42 | 0.0022064 | 0.00055298
43 | 0.0020784 | 0.0005209
44 | 0.0022092 | 0.00055367
45 | 0.0023403 | 0.00058653
46 | 0.0019848 | 0.00049745
47 | 0.0024809 | 0.00062177
48 | 0.002061 | 0.00051653
49 | 0.003605 | 0.00090349
50 | 0.0024046 | 0.00060266
51 | 0.0042911 | 0.0010755
52 | 0.0038554 | 0.00096624
53 | 0.0070481 | 0.0017664
54 | 0.0047808 | 0.0011982
55 | 0.023037 | 0.0057735
56 | 0.0057326 | 0.0014367
57 | 0.0044373 | 0.0011121
58 | 0.0044803 | 0.0011229
59 | 0.0079402 | 0.00199
60 | 0.0041282 | 0.0010346
61 | 0.005053 | 0.0012664
62 | 0.0063634 | 0.0015948
63 | 0.0035955 | 0.00090111
64 | 0.0049629 | 0.0012438
65 | 0.0063511 | 0.0015917
66 | 0.0037354 | 0.00093618
67 | 0.0043111 | 0.0010805
68 | 0.0037325 | 0.00093545
69 | 0.0044513 | 0.0011156
70 | 0.004524 | 0.0011338
71 | 0.0060854 | 0.0015252
72 | 0.0045013 | 0.0011281
73 | 0.0075984 | 0.0019043
74 | 0.0025532 | 0.00063988
75 | 0.0024805 | 0.00062166
76 | 0.0024401 | 0.00061154
77 | 0.0024009 | 0.00060171
78 | 0.0024764 | 0.00062064
79 | 0.0019883 | 0.00049831
80 | 0.0019831 | 0.00049701
81 | 0.0024444 | 0.00061262
82 | 0.0035214 | 0.00088254
83 | 0.0039371 | 0.00098673
84 | 0.0027408 | 0.00068691
85 | 0.0029279 | 0.0007338
86 | 0.0038409 | 0.00096263
87 | 0.0037137 | 0.00093075
88 | 0.004033 | 0.0010108
89 | 0.0062027 | 0.0015545
90 | 0.0025948 | 0.00065032
91 | 0.0028356 | 0.00071066
92 | 0.0023618 | 0.00059192
93 | 0.0034342 | 0.0008607
94 | 0.0040121 | 0.0010055
95 | 0.0050706 | 0.0012708
96 | 0.010351 | 0.0025941
97 | 0.0024806 | 0.00062169
98 | 0.0025377 | 0.000636

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1