## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-935_1_2_node_5 | 0.4 | n |  | TRUE
1 | bus_LV_261-935_1_2_node_8 | 0.4 | n |  | TRUE
2 | bus_LV_261-935_1_2_node_68 | 0.4 | n |  | TRUE
3 | bus_LV_261-935_1_2_node_75 | 0.4 | n |  | TRUE
4 | bus_LV_261-935_1_2_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_261-935_1_2_node_23 | 0.4 | n |  | TRUE
6 | bus_LV_261-935_1_2_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_261-935_1_2_node_91 | 0.4 | n |  | TRUE
8 | bus_LV_261-935_1_2_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_261-935_1_2_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_261-935_1_2_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_261-935_1_2_node_71 | 0.4 | n |  | TRUE
12 | bus_LV_261-935_1_2_node_66 | 0.4 | n |  | TRUE
13 | bus_LV_261-935_1_2_node_65 | 0.4 | n |  | TRUE
14 | bus_LV_261-935_1_2_node_109 | 0.4 | n |  | TRUE
15 | bus_LV_261-935_1_2_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_261-935_1_2_node_67 | 0.4 | n |  | TRUE
17 | bus_LV_261-935_1_2_node_53 | 0.4 | n |  | TRUE
18 | bus_LV_261-935_1_2_node_119 | 0.4 | n |  | TRUE
19 | bus_LV_261-935_1_2_node_54 | 0.4 | n |  | TRUE
20 | bus_LV_261-935_1_2_node_55 | 0.4 | n |  | TRUE
21 | bus_LV_261-935_1_2_node_113 | 0.4 | n |  | TRUE
22 | bus_LV_261-935_1_2_node_112 | 0.4 | n |  | TRUE
23 | bus_LV_261-935_1_2_node_69 | 0.4 | n |  | TRUE
24 | bus_LV_261-935_1_2_node_70 | 0.4 | n |  | TRUE
25 | bus_LV_261-935_1_2_node_72 | 0.4 | n |  | TRUE
26 | bus_LV_261-935_1_2_node_74 | 0.4 | n |  | TRUE
27 | bus_LV_261-935_1_2_node_78 | 0.4 | n |  | TRUE
28 | bus_LV_261-935_1_2_node_76 | 0.4 | n |  | TRUE
29 | bus_LV_261-935_1_2_node_77 | 0.4 | n |  | TRUE
30 | bus_LV_261-935_1_2_node_80 | 0.4 | n |  | TRUE
31 | bus_LV_261-935_1_2_node_79 | 0.4 | n |  | TRUE
32 | bus_LV_261-935_1_2_node_121 | 0.4 | n |  | TRUE
33 | bus_LV_261-935_1_2_node_120 | 0.4 | n |  | TRUE
34 | bus_MV_543_0_node_86 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-935_1_2_load_68 | 2 | 0.011025 | 0.002763 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-935_1_2_load_75 | 3 | 0.010333 | 0.0025898 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-935_1_2_load_91 | 7 | 0.001575 | 0.00039472 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-935_1_2_load_71 | 11 | 0.010466 | 0.0026231 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-935_1_2_load_65 | 13 | 0.011379 | 0.0028519 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-935_1_2_load_109 | 14 | 0.0024346 | 0.00061017 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-935_1_2_load_67 | 16 | 0.0044348 | 0.0011115 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-935_1_2_load_53 | 17 | 0.0075052 | 0.001881 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-935_1_2_load_119 | 18 | 0.001343 | 0.0003366 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-935_1_2_load_54 | 19 | 0.011826 | 0.0029639 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-935_1_2_load_55 | 20 | 0.0091628 | 0.0022964 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-935_1_2_load_112 | 22 | 0.014934 | 0.0037427 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-935_1_2_load_69 | 23 | 0.010874 | 0.0027254 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-935_1_2_load_70 | 24 | 0.014864 | 0.0037252 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-935_1_2_load_78 | 27 | 0.039001 | 0.0097746 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-935_1_2_load_76 | 28 | 0.010361 | 0.0025967 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-935_1_2_load_77 | 29 | 0.017773 | 0.0044543 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-935_1_2_load_80 | 30 | 0.005694 | 0.0014271 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-935_1_2_load_79 | 31 | 0.0050773 | 0.0012725 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-935_1_2_load_121 | 32 | 0.03708 | 0.009293 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-935_1_2_load_120 | 33 | 0.0041486 | 0.0010397 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-935_1_2_line_0 |  | 0 | 1 | 0.016994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-935_1_2_line_1 |  | 0 | 2 | 0.011156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-935_1_2_line_2 |  | 1 | 3 | 0.014548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-935_1_2_line_3 |  | 2 | 23 | 0.019729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-935_1_2_line_4 |  | 3 | 28 | 0.019879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-935_1_2_line_5 |  | 4 | 5 | 0.003805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-935_1_2_line_6 |  | 4 | 6 | 0.044632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-935_1_2_line_7 |  | 4 | 7 | 0.0096934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-935_1_2_line_8 |  | 5 | 18 | 0.013836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-935_1_2_line_9 |  | 6 | 8 | 0.046288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-935_1_2_line_10 |  | 6 | 9 | 0.02643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-935_1_2_line_11 |  | 6 | 10 | 0.052298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-935_1_2_line_12 |  | 6 | 11 | 0.0077158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-935_1_2_line_13 |  | 8 | 14 | 0.019258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-935_1_2_line_14 |  | 9 | 12 | 0.025948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-935_1_2_line_15 |  | 9 | 13 | 0.010641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-935_1_2_line_16 |  | 10 | 15 | 0.25934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-935_1_2_line_17 |  | 10 | 16 | 0.016132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-935_1_2_line_18 |  | 11 | 25 | 0.031444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-935_1_2_line_19 |  | 12 | 21 | 0.003484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-935_1_2_line_20 |  | 12 | 22 | 0.0091934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-935_1_2_line_21 |  | 15 | 17 | 0.21866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-935_1_2_line_22 |  | 17 | 19 | 0.018973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-935_1_2_line_23 |  | 18 | 33 | 0.0056603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-935_1_2_line_24 |  | 19 | 20 | 0.02082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-935_1_2_line_25 |  | 21 | 32 | 0.004866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-935_1_2_line_26 |  | 23 | 24 | 0.025391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-935_1_2_line_27 |  | 24 | 25 | 0.015434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-935_1_2_line_28 |  | 26 | 27 | 0.016129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-935_1_2_line_29 |  | 26 | 28 | 0.0080245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-935_1_2_line_30 |  | 27 | 31 | 0.040176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-935_1_2_line_31 |  | 27 | 29 | 0.020352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-935_1_2_line_32 |  | 29 | 30 | 0.047166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-935_1_2_trafo_69 | 0.63 MVA 20/0.4 kV | 34 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2684572.0928 | 1251018.9056 | 2684571.6129 | 1251013.9173 | 2684559.7244 | 1251015.4154
1 | 2684559.7244 | 1251015.4154 | 2684562.204 | 1251021.5109 | 2684562.8709 | 1251026.0377
2 | 2684572.0928 | 1251018.9056 | 2684565.378 | 1251019.6882 | 2684566.3845 | 1251027.4107
3 | 2684562.8709 | 1251026.0377 | 2684563.0987 | 1251027.5838 | 2684562.4828 | 1251034.2356 | 2684562.476 | 1251037.36 | 2684565.2579 | 1251042.9039 | 2684565.5186 | 1251045.0474
4 | 2684566.3845 | 1251027.4107 | 2684568.9538 | 1251047.1233
5 | 2684529.9057 | 1251132.8225 | 2684529.4387 | 1251129.0464
6 | 2684529.4387 | 1251129.0464 | 2684528.5117 | 1251121.5386 | 2684528.0113 | 1251117.9844 | 2684526.4351 | 1251106.7757 | 2684532.6825 | 1251105.9309 | 2684531.6749 | 1251098.7778 | 2684530.4683 | 1251090.232
7 | 2684529.4387 | 1251129.0464 | 2684539.0425 | 1251127.7309
8 | 2684529.9057 | 1251132.8225 | 2684543.6004 | 1251130.8479
9 | 2684530.4683 | 1251090.232 | 2684531.6749 | 1251098.7778 | 2684532.6825 | 1251105.9309 | 2684553.1215 | 1251103.0091 | 2684559.2563 | 1251102.1293 | 2684562.8114 | 1251101.6352
10 | 2684521.4783 | 1251071.1339 | 2684524.1088 | 1251090.9863 | 2684530.4683 | 1251090.232
11 | 2684478.8431 | 1251089.0172 | 2684480.4135 | 1251089.5289 | 2684487.758 | 1251091.6907 | 2684494.9662 | 1251092.8277 | 2684500.6739 | 1251093.3094 | 2684507.8206 | 1251092.9333 | 2684524.1088 | 1251090.9863 | 2684530.4683 | 1251090.232
12 | 2684530.4683 | 1251090.232 | 2684534.4534 | 1251089.7551 | 2684538.1187 | 1251089.2335
13 | 2684562.8114 | 1251101.6352 | 2684565.5253 | 1251120.7007
14 | 2684518.0784 | 1251045.4106 | 2684521.4783 | 1251071.1339
15 | 2684521.4783 | 1251071.1339 | 2684511.1814 | 1251068.4508
16 | 2684336.2227 | 1250894.8185 | 2684360.138 | 1250911.8271 | 2684375.469 | 1250927.2902 | 2684385.6351 | 1250940.7228 | 2684395.931 | 1250959.8726 | 2684411.7743 | 1250997.6488 | 2684414.8262 | 1251027.1588 | 2684422.5908 | 1251046.9953 | 2684432.7404 | 1251043.5596 | 2684433.8001 | 1251046.5324 | 2684436.4873 | 1251052.9088 | 2684440.0659 | 1251058.1749 | 2684444.7305 | 1251064.5795 | 2684448.163 | 1251068.9761 | 2684452.4679 | 1251073.0738 | 2684456.7784 | 1251076.7714 | 2684461.8026 | 1251080.7237 | 2684467.5516 | 1251084.1304 | 2684473.854 | 1251087.3782 | 2684478.8431 | 1251089.0172
17 | 2684478.8431 | 1251089.0172 | 2684483.8412 | 1251073.6789
18 | 2684569.2494 | 1251084.8033 | 2684538.1187 | 1251089.2335
19 | 2684518.0784 | 1251045.4106 | 2684517.6219 | 1251041.957
20 | 2684518.0784 | 1251045.4106 | 2684508.9695 | 1251046.6538
21 | 2684336.2227 | 1250894.8185 | 2684371.1622 | 1250909.5379 | 2684524.605 | 1250973.1717 | 2684538.2336 | 1250978.4857
22 | 2684555.9103 | 1250985.3782 | 2684538.2336 | 1250978.4857
23 | 2684549.2027 | 1251130.0401 | 2684543.6004 | 1251130.8479
24 | 2684575.308 | 1250992.9417 | 2684555.9103 | 1250985.3782
25 | 2684517.2684 | 1251037.1039 | 2684517.6219 | 1251041.957
26 | 2684565.2738 | 1251070.0454 | 2684564.7894 | 1251064.6135 | 2684566.7135 | 1251058.8588 | 2684566.2578 | 1251051.1243 | 2684565.5186 | 1251045.0474
27 | 2684569.2494 | 1251084.8033 | 2684565.811 | 1251076.07 | 2684565.2738 | 1251070.0454
28 | 2684569.9909 | 1251055.0805 | 2684585.973 | 1251052.907
29 | 2684569.9909 | 1251055.0805 | 2684568.9538 | 1251047.1233
30 | 2684585.973 | 1251052.907 | 2684622.8955 | 1251068.7459
31 | 2684583.0882 | 1251032.7608 | 2684585.973 | 1251052.907
32 | 2684583.0882 | 1251032.7608 | 2684630.2534 | 1251032.4571

## bus_geodata
| x | y | coords
0 | 2684559.7244 | 1251015.4154
1 | 2684572.0928 | 1251018.9056
2 | 2684562.8709 | 1251026.0377
3 | 2684566.3845 | 1251027.4107
4 | 2684529.4387 | 1251129.0464
5 | 2684529.9057 | 1251132.8225
6 | 2684530.4683 | 1251090.232
7 | 2684539.0425 | 1251127.7309
8 | 2684562.8114 | 1251101.6352
9 | 2684521.4783 | 1251071.1339
10 | 2684478.8431 | 1251089.0172
11 | 2684538.1187 | 1251089.2335
12 | 2684518.0784 | 1251045.4106
13 | 2684511.1814 | 1251068.4508
14 | 2684565.5253 | 1251120.7007
15 | 2684336.2227 | 1250894.8185
16 | 2684483.8412 | 1251073.6789
17 | 2684538.2336 | 1250978.4857
18 | 2684543.6004 | 1251130.8479
19 | 2684555.9103 | 1250985.3782
20 | 2684575.308 | 1250992.9417
21 | 2684517.6219 | 1251041.957
22 | 2684508.9695 | 1251046.6538
23 | 2684565.5186 | 1251045.0474
24 | 2684565.2738 | 1251070.0454
25 | 2684569.2494 | 1251084.8033
26 | 2684569.9909 | 1251055.0805
27 | 2684585.973 | 1251052.907
28 | 2684568.9538 | 1251047.1233
29 | 2684583.0882 | 1251032.7608
30 | 2684630.2534 | 1251032.4571
31 | 2684622.8955 | 1251068.7459
32 | 2684517.2684 | 1251037.1039
33 | 2684549.2027 | 1251130.0401
34 | 2684559.7244 | 1251015.4154

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99731 | -0.051434 | 0 | 0
1 | 0.99594 | -0.077749 | 0 | 0
2 | 0.99821 | -0.034198 | 0.011025 | 0.002763
3 | 0.99477 | -0.10033 | 0.010333 | 0.0025898
4 | 0.99088 | -0.17442 | 0 | 0
5 | 0.99086 | -0.17479 | 0 | 0
6 | 0.99117 | -0.16882 | 0 | 0
7 | 0.99087 | -0.17469 | 0.001575 | 0.00039472
8 | 0.99107 | -0.17082 | 0 | 0
9 | 0.98963 | -0.19859 | 0 | 0
10 | 0.98957 | -0.19944 | 0 | 0
11 | 0.99192 | -0.15434 | 0.010466 | 0.0026231
12 | 0.98839 | -0.22264 | 0 | 0
13 | 0.98952 | -0.20074 | 0.011379 | 0.0028519
14 | 0.99102 | -0.17165 | 0.0024346 | 0.00061017
15 | 0.98271 | -0.33194 | 0 | 0
16 | 0.98951 | -0.20071 | 0.0044348 | 0.0011115
17 | 0.97692 | -0.44507 | 0.0075052 | 0.001881
18 | 0.99079 | -0.17614 | 0.001343 | 0.0003366
19 | 0.97655 | -0.45235 | 0.011826 | 0.0029639
20 | 0.97637 | -0.45584 | 0.0091628 | 0.0022964
21 | 0.98828 | -0.22494 | 0 | 0
22 | 0.98827 | -0.22509 | 0.014934 | 0.0037427
23 | 1 | 0 | -0.23427 | -0.059142
24 | 0.99694 | -0.058232 | 0.014864 | 0.0037252
25 | 0.99529 | -0.089768 | 0 | 0
26 | 0.99286 | -0.13723 | 0 | 0
27 | 0.99186 | -0.15652 | 0.039001 | 0.0097746
28 | 0.99335 | -0.12765 | 0.010361 | 0.0025967
29 | 0.99142 | -0.16498 | 0.017773 | 0.0044543
30 | 0.99118 | -0.16974 | 0.005694 | 0.0014271
31 | 0.99167 | -0.16013 | 0.0050773 | 0.0012725
32 | 0.98811 | -0.22816 | 0.03708 | 0.009293
33 | 0.99077 | -0.17655 | 0.0041486 | 0.0010397
34 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.088653 | 0.022377 | -0.088542 | -0.022306 | 0.00011159 | 7.1198e-05 | 0.13233 | 0.13233 | 0.13233 | 0.99731 | -0.051434 | 0.99594 | -0.077749 | 36.3542
1 | -0.088653 | -0.022377 | 0.088727 | 0.022424 | 7.3259e-05 | 4.674e-05 | 0.13233 | 0.13233 | 0.13233 | 0.99731 | -0.051434 | 0.99821 | -0.034198 | 36.3542
2 | 0.088542 | 0.022306 | -0.088446 | -0.022245 | 9.5531e-05 | 6.0951e-05 | 0.13233 | 0.13233 | 0.13233 | 0.99594 | -0.077749 | 0.99477 | -0.10033 | 36.3542
3 | -0.099751 | -0.025187 | 0.099915 | 0.025292 | 0.00016373 | 0.00010453 | 0.14876 | 0.14876 | 0.14876 | 0.99821 | -0.034198 | 1 | 0 | 40.869
4 | 0.078113 | 0.019655 | -0.078011 | -0.01959 | 0.00010183 | 6.4911e-05 | 0.11687 | 0.11687 | 0.11687 | 0.99477 | -0.10033 | 0.99335 | -0.12765 | 32.1078
5 | 0.0054922 | 0.0013764 | -0.0054921 | -0.0013764 | 9.7061e-08 | 1.3107e-08 | 0.0082476 | 0.0082476 | 0.0082476 | 0.99088 | -0.17442 | 0.99086 | -0.17479 | 2.2658
6 | -0.0070671 | -0.001771 | 0.007069 | 0.0017716 | 1.885e-06 | 6.3135e-07 | 0.010613 | 0.010613 | 0.010613 | 0.99088 | -0.17442 | 0.99117 | -0.16882 | 2.9156
7 | 0.001575 | 0.00039461 | -0.001575 | -0.00039472 | 2.0334e-08 | -1.1185e-07 | 0.0023651 | 0.0023652 | 0.0023652 | 0.99088 | -0.17442 | 0.99087 | -0.17469 | 0.64977
8 | 0.0054921 | 0.0013764 | -0.0054917 | -0.0013763 | 3.5295e-07 | 4.768e-08 | 0.0082476 | 0.0082477 | 0.0082477 | 0.99086 | -0.17479 | 0.99079 | -0.17614 | 2.2658
9 | 0.0024349 | 0.00060953 | -0.0024347 | -0.00060998 | 2.3193e-07 | -4.4809e-07 | 0.0036552 | 0.0036554 | 0.0036554 | 0.99117 | -0.16882 | 0.99107 | -0.17082 | 1.0042
10 | 0.063555 | 0.015991 | -0.063465 | -0.015933 | 9.0271e-05 | 5.7433e-05 | 0.095435 | 0.095436 | 0.095436 | 0.99117 | -0.16882 | 0.98963 | -0.19859 | 26.2186
11 | 0.033325 | 0.0084989 | -0.033276 | -0.0084681 | 4.9191e-05 | 3.081e-05 | 0.050082 | 0.050083 | 0.050083 | 0.99117 | -0.16882 | 0.98957 | -0.19944 | 13.759
12 | -0.10638 | -0.026871 | 0.10646 | 0.026918 | 7.3873e-05 | 4.7179e-05 | 0.15979 | 0.15979 | 0.15979 | 0.99117 | -0.16882 | 0.99192 | -0.15434 | 43.8971
13 | 0.0024347 | 0.00060998 | -0.0024346 | -0.00061017 | 9.6499e-08 | -1.8638e-07 | 0.0036554 | 0.0036555 | 0.0036555 | 0.99107 | -0.17082 | 0.99102 | -0.17165 | 1.0043
14 | 0.052084 | 0.013081 | -0.052025 | -0.013043 | 5.9693e-05 | 3.7871e-05 | 0.078324 | 0.078324 | 0.078324 | 0.98963 | -0.19859 | 0.98839 | -0.22264 | 21.5176
15 | 0.01138 | 0.0028525 | -0.011379 | -0.0028519 | 1.1684e-06 | 6.1107e-07 | 0.017112 | 0.017112 | 0.017112 | 0.98963 | -0.19859 | 0.98952 | -0.20074 | 4.701
16 | 0.028841 | 0.0073566 | -0.028658 | -0.0072426 | 0.0001833 | 0.00011401 | 0.043414 | 0.043415 | 0.043415 | 0.98957 | -0.19944 | 0.98271 | -0.33194 | 11.9272
17 | 0.004435 | 0.0011114 | -0.0044348 | -0.0011115 | 2.6905e-07 | -3.5043e-08 | 0.0066689 | 0.006669 | 0.006669 | 0.98957 | -0.19944 | 0.98951 | -0.20071 | 1.8321
18 | -0.11692 | -0.029541 | 0.11729 | 0.029773 | 0.00036313 | 0.00023199 | 0.17549 | 0.17549 | 0.17549 | 0.99192 | -0.15434 | 0.99529 | -0.089768 | 48.2105
19 | 0.037089 | 0.0092991 | -0.037085 | -0.0092966 | 4.0736e-06 | 2.5625e-06 | 0.055839 | 0.055839 | 0.055839 | 0.98839 | -0.22264 | 0.98828 | -0.22494 | 15.3403
20 | 0.014935 | 0.0037437 | -0.014934 | -0.0037427 | 1.743e-06 | 9.9771e-07 | 0.022485 | 0.022485 | 0.022485 | 0.98839 | -0.22264 | 0.98827 | -0.22509 | 6.1772
21 | 0.028658 | 0.0072426 | -0.028503 | -0.0071465 | 0.00015455 | 9.6161e-05 | 0.043415 | 0.043416 | 0.043416 | 0.98271 | -0.33194 | 0.97692 | -0.44507 | 11.9275
22 | 0.020998 | 0.0052655 | -0.020991 | -0.0052611 | 7.2785e-06 | 4.4208e-06 | 0.031984 | 0.031984 | 0.031984 | 0.97692 | -0.44507 | 0.97655 | -0.45235 | 8.7869
23 | 0.0041487 | 0.0010397 | -0.0041486 | -0.0010397 | 8.2402e-08 | -2.0159e-08 | 0.0062306 | 0.0062307 | 0.0062307 | 0.99079 | -0.17614 | 0.99077 | -0.17655 | 1.7117
24 | 0.0091644 | 0.0022971 | -0.0091628 | -0.0022964 | 1.5225e-06 | 7.1395e-07 | 0.013964 | 0.013964 | 0.013964 | 0.97655 | -0.45235 | 0.97637 | -0.45584 | 3.8364
25 | 0.037085 | 0.0092966 | -0.03708 | -0.009293 | 5.6895e-06 | 3.579e-06 | 0.055839 | 0.055839 | 0.055839 | 0.98828 | -0.22494 | 0.98811 | -0.22816 | 15.3403
26 | 0.1327 | 0.03385 | -0.13233 | -0.033612 | 0.00037205 | 0.00023778 | 0.19767 | 0.19767 | 0.19767 | 1 | 0 | 0.99694 | -0.058232 | 54.3053
27 | 0.11747 | 0.029887 | -0.11729 | -0.029773 | 0.00017824 | 0.00011387 | 0.17549 | 0.17549 | 0.17549 | 0.99694 | -0.058232 | 0.99529 | -0.089768 | 48.2104
28 | 0.067619 | 0.016974 | -0.067557 | -0.016934 | 6.2131e-05 | 3.9555e-05 | 0.10135 | 0.10135 | 0.10135 | 0.99286 | -0.13723 | 0.99186 | -0.15652 | 27.8438
29 | -0.067619 | -0.016974 | 0.06765 | 0.016994 | 3.0911e-05 | 1.9679e-05 | 0.10135 | 0.10135 | 0.10135 | 0.99286 | -0.13723 | 0.99335 | -0.12765 | 27.8438
30 | 0.0050782 | 0.0012725 | -0.0050773 | -0.0012725 | 8.7446e-07 | 4.1212e-08 | 0.0076184 | 0.0076186 | 0.0076186 | 0.99186 | -0.15652 | 0.99167 | -0.16013 | 2.093
31 | 0.023478 | 0.0058873 | -0.023468 | -0.0058815 | 9.4685e-06 | 5.7973e-06 | 0.035223 | 0.035223 | 0.035223 | 0.99186 | -0.15652 | 0.99142 | -0.16498 | 9.6766
32 | 0.0056953 | 0.0014273 | -0.005694 | -0.0014271 | 1.2924e-06 | 2.1908e-07 | 0.008548 | 0.0085482 | 0.0085482 | 0.99142 | -0.16498 | 0.99118 | -0.16974 | 2.3484

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.24514 | 0.061867

## res_load
| p_mw | q_mvar
0 | 0.011025 | 0.002763
1 | 0.010333 | 0.0025898
2 | 0.001575 | 0.00039472
3 | 0.010466 | 0.0026231
4 | 0.011379 | 0.0028519
5 | 0.0024346 | 0.00061017
6 | 0.0044348 | 0.0011115
7 | 0.0075052 | 0.001881
8 | 0.001343 | 0.0003366
9 | 0.011826 | 0.0029639
10 | 0.0091628 | 0.0022964
11 | 0.014934 | 0.0037427
12 | 0.010874 | 0.0027254
13 | 0.014864 | 0.0037252
14 | 0.039001 | 0.0097746
15 | 0.010361 | 0.0025967
16 | 0.017773 | 0.0044543
17 | 0.005694 | 0.0014271
18 | 0.0050773 | 0.0012725
19 | 0.03708 | 0.009293
20 | 0.0041486 | 0.0010397

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1