## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-945_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-945_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-945_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-945_0_5_node_15 | 0.4 | n |  | TRUE
4 | bus_LV_261-945_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-945_0_5_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_261-945_0_5_node_24 | 0.4 | n |  | TRUE
7 | bus_LV_261-945_0_5_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-945_0_5_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_261-945_0_5_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_261-945_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_261-945_0_5_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_261-945_0_5_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_261-945_0_5_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_261-945_0_5_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_261-945_0_5_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_261-945_0_5_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_261-945_0_5_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_261-945_0_5_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_261-945_0_5_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_261-945_0_5_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_261-945_0_5_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_261-945_0_5_node_31 | 0.4 | n |  | TRUE
23 | bus_LV_261-945_0_5_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_261-945_0_5_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_261-945_0_5_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_261-945_0_5_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_261-945_0_5_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_261-945_0_5_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_261-945_0_5_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_261-945_0_5_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_261-945_0_5_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_261-945_0_5_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_261-945_0_5_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_261-945_0_5_node_21 | 0.4 | n |  | TRUE
35 | bus_MV_539_0_node_126 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-945_0_5_load_0 | 0 | 0.008261 | 0.0020704 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-945_0_5_load_1 | 1 | 0.0077569 | 0.0019441 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-945_0_5_load_15 | 3 | 0.017579 | 0.0044057 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-945_0_5_load_24 | 6 | 0.015964 | 0.0040011 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-945_0_5_load_16 | 9 | 0.0095247 | 0.0023871 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-945_0_5_load_18 | 11 | 0.026827 | 0.0067235 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-945_0_5_load_25 | 12 | 0.0082463 | 0.0020667 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-945_0_5_load_33 | 15 | 0.020499 | 0.0051375 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-945_0_5_load_38 | 16 | 0.0037048 | 0.00092852 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-945_0_5_load_28 | 17 | 0.0056404 | 0.0014136 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-945_0_5_load_32 | 18 | 0.025688 | 0.006438 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-945_0_5_load_27 | 20 | 0.02859 | 0.0071653 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-945_0_5_load_26 | 21 | 0.029297 | 0.0073426 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-945_0_5_load_31 | 22 | 0.028586 | 0.0071644 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-945_0_5_load_29 | 23 | 0.039 | 0.0097744 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-945_0_5_load_17 | 24 | 0.011395 | 0.0028557 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-945_0_5_load_20 | 25 | 0.026115 | 0.006545 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-945_0_5_load_19 | 26 | 0.031454 | 0.0078831 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-945_0_5_load_36 | 27 | 0.0031155 | 0.00078082 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-945_0_5_load_37 | 28 | 0.0031812 | 0.00079727 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-945_0_5_load_34 | 29 | 0.029142 | 0.0073036 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-945_0_5_load_23 | 30 | 0.060506 | 0.015164 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-945_0_5_load_30 | 31 | 0.019269 | 0.0048293 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-945_0_5_load_35 | 32 | 0.027233 | 0.0068252 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-945_0_5_load_22 | 33 | 0.024695 | 0.0061892 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-945_0_5_line_0 |  | 0 | 1 | 0.02132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-945_0_5_line_1 |  | 1 | 2 | 0.00084364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-945_0_5_line_2 |  | 2 | 3 | 0.036797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-945_0_5_line_3 |  | 3 | 5 | 0.0019716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-945_0_5_line_4 |  | 4 | 5 | 0.036138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-945_0_5_line_5 |  | 4 | 6 | 0.0093593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-945_0_5_line_6 |  | 6 | 12 | 0.014248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-945_0_5_line_7 |  | 7 | 8 | 0.022864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-945_0_5_line_8 |  | 7 | 9 | 0.04281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-945_0_5_line_9 |  | 8 | 17 | 0.021631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_261-945_0_5_line_10 |  | 8 | 18 | 0.048162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_261-945_0_5_line_11 |  | 9 | 24 | 0.023611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-945_0_5_line_12 |  | 10 | 11 | 0.027814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-945_0_5_line_13 |  | 10 | 12 | 0.014948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-945_0_5_line_14 |  | 11 | 24 | 0.031597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-945_0_5_line_15 |  | 13 | 14 | 0.014511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-945_0_5_line_16 |  | 13 | 15 | 0.011444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-945_0_5_line_17 |  | 14 | 16 | 0.013362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-945_0_5_line_18 |  | 15 | 29 | 0.018123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-945_0_5_line_19 |  | 16 | 28 | 0.014903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-945_0_5_line_20 |  | 17 | 30 | 0.014469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_261-945_0_5_line_21 |  | 18 | 31 | 0.014736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_261-945_0_5_line_22 |  | 19 | 20 | 0.013186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-945_0_5_line_23 |  | 19 | 21 | 0.032454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-945_0_5_line_24 |  | 20 | 32 | 0.019607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-945_0_5_line_25 |  | 21 | 33 | 0.014634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_261-945_0_5_line_26 |  | 22 | 23 | 0.015709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-945_0_5_line_27 |  | 23 | 31 | 0.016063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-945_0_5_line_28 |  | 25 | 26 | 0.018399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-945_0_5_line_29 |  | 26 | 34 | 0.016098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-945_0_5_line_30 |  | 27 | 28 | 0.013645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-945_0_5_line_31 |  | 29 | 32 | 0.029456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-945_0_5_line_32 |  | 30 | 34 | 0.010203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_261-945_0_5_line_33 |  | 33 | 34 | 0.015319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-945_0_5_trafo_30 | 0.63 MVA 20/0.4 kV | 35 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2685201.099 | 1246250.0142 | 2685214.8024 | 1246233.6812
1 | 2685214.8024 | 1246233.6812 | 2685215.3446 | 1246233.0349
2 | 2685215.3446 | 1246233.0349 | 2685238.9982 | 1246204.8481
3 | 2685240.2657 | 1246203.3378 | 2685238.9982 | 1246204.8481
4 | 2685234.921 | 1246177.2862 | 2685250.0743 | 1246191.6479 | 2685240.2657 | 1246203.3378
5 | 2685234.921 | 1246177.2862 | 2685228.2961 | 1246170.675
6 | 2685218.2107 | 1246160.6106 | 2685228.2961 | 1246170.675
7 | 2685121.0136 | 1246240.7084 | 2685116.6886 | 1246236.7434 | 2685124.9527 | 1246227.8888 | 2685121.443 | 1246224.4915
8 | 2685121.0136 | 1246240.7084 | 2685121.4629 | 1246238.3576 | 2685122.9161 | 1246236.0767 | 2685149.3768 | 1246209.2065
9 | 2685121.443 | 1246224.4915 | 2685117.0986 | 1246220.2927 | 2685117.5096 | 1246204.7085
10 | 2685121.443 | 1246224.4915 | 2685128.6776 | 1246217.8793 | 2685155.5305 | 1246190.484
11 | 2685149.3768 | 1246209.2065 | 2685165.9435 | 1246192.3834
12 | 2685207.63 | 1246150.0518 | 2685188.1138 | 1246169.8699
13 | 2685207.63 | 1246150.0518 | 2685218.2107 | 1246160.6106
14 | 2685188.1138 | 1246169.8699 | 2685165.9435 | 1246192.3834
15 | 2685212.5086 | 1246113.406 | 2685212.7102 | 1246106.2147 | 2685212.9136 | 1246098.9011
16 | 2685212.5086 | 1246113.406 | 2685201.0692 | 1246113.0943
17 | 2685212.9136 | 1246098.9011 | 2685199.5586 | 1246098.4582
18 | 2685182.9532 | 1246112.6007 | 2685201.0692 | 1246113.0943
19 | 2685184.6639 | 1246097.9642 | 2685199.5586 | 1246098.4582
20 | 2685117.5096 | 1246204.7085 | 2685117.8911 | 1246190.2442
21 | 2685155.5305 | 1246190.484 | 2685165.8458 | 1246179.9603
22 | 2685121.1405 | 1246117.7084 | 2685129.2197 | 1246115.9564 | 2685134.0751 | 1246115.1683
23 | 2685121.1405 | 1246117.7084 | 2685119.5906 | 1246150.1259
24 | 2685134.0751 | 1246115.1683 | 2685143.8204 | 1246113.5864 | 2685153.5271 | 1246112.8556
25 | 2685118.8917 | 1246164.7429 | 2685119.5906 | 1246150.1259
26 | 2685188.0862 | 1246157.2706 | 2685177.0902 | 1246168.4888
27 | 2685165.8458 | 1246179.9603 | 2685177.0902 | 1246168.4888
28 | 2685083.6744 | 1246179.1813 | 2685102.0675 | 1246179.6419
29 | 2685118.1601 | 1246180.045 | 2685102.0675 | 1246179.6419
30 | 2685171.0261 | 1246097.512 | 2685184.6639 | 1246097.9642
31 | 2685182.9532 | 1246112.6007 | 2685172.7755 | 1246112.3234 | 2685162.5477 | 1246112.1765 | 2685153.5271 | 1246112.8556
32 | 2685118.1601 | 1246180.045 | 2685117.8911 | 1246190.2442
33 | 2685118.1601 | 1246180.045 | 2685118.8917 | 1246164.7429

## bus_geodata
| x | y | coords
0 | 2685201.099 | 1246250.0142
1 | 2685214.8024 | 1246233.6812
2 | 2685215.3446 | 1246233.0349
3 | 2685238.9982 | 1246204.8481
4 | 2685234.921 | 1246177.2862
5 | 2685240.2657 | 1246203.3378
6 | 2685228.2961 | 1246170.675
7 | 2685121.0136 | 1246240.7084
8 | 2685121.443 | 1246224.4915
9 | 2685149.3768 | 1246209.2065
10 | 2685207.63 | 1246150.0518
11 | 2685188.1138 | 1246169.8699
12 | 2685218.2107 | 1246160.6106
13 | 2685212.5086 | 1246113.406
14 | 2685212.9136 | 1246098.9011
15 | 2685201.0692 | 1246113.0943
16 | 2685199.5586 | 1246098.4582
17 | 2685117.5096 | 1246204.7085
18 | 2685155.5305 | 1246190.484
19 | 2685121.1405 | 1246117.7084
20 | 2685134.0751 | 1246115.1683
21 | 2685119.5906 | 1246150.1259
22 | 2685188.0862 | 1246157.2706
23 | 2685177.0902 | 1246168.4888
24 | 2685165.9435 | 1246192.3834
25 | 2685083.6744 | 1246179.1813
26 | 2685102.0675 | 1246179.6419
27 | 2685171.0261 | 1246097.512
28 | 2685184.6639 | 1246097.9642
29 | 2685182.9532 | 1246112.6007
30 | 2685117.8911 | 1246190.2442
31 | 2685165.8458 | 1246179.9603
32 | 2685153.5271 | 1246112.8556
33 | 2685118.8917 | 1246164.7429
34 | 2685118.1601 | 1246180.045
35 | 2685121.443 | 1246224.4915

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97802 | -0.42398 | 0.008261 | 0.0020704
1 | 0.97818 | -0.42078 | 0.0077569 | 0.0019441
2 | 0.9782 | -0.42053 | 0 | 0
3 | 0.97874 | -0.4098 | 0.017579 | 0.0044057
4 | 0.97993 | -0.38653 | 0 | 0
5 | 0.9788 | -0.40859 | 0 | 0
6 | 0.98022 | -0.38082 | 0.015964 | 0.0040011
7 | 0.99191 | -0.15425 | 0 | 0
8 | 0.99414 | -0.11159 | 0 | 0
9 | 0.98773 | -0.23464 | 0.0095247 | 0.0023871
10 | 0.98168 | -0.35238 | 0 | 0
11 | 0.98316 | -0.32334 | 0.026827 | 0.0067235
12 | 0.98088 | -0.36802 | 0.0082463 | 0.0020667
13 | 0.98095 | -0.36736 | 0 | 0
14 | 0.98081 | -0.36999 | 0 | 0
15 | 0.98105 | -0.36529 | 0.020499 | 0.0051375
16 | 0.98069 | -0.37241 | 0.0037048 | 0.00092852
17 | 0.99269 | -0.13959 | 0.0056404 | 0.0014136
18 | 0.99856 | -0.027293 | 0.025688 | 0.006438
19 | 0.98616 | -0.26556 | 0 | 0
20 | 0.98476 | -0.29288 | 0.02859 | 0.0071653
21 | 0.98962 | -0.19863 | 0.029297 | 0.0073426
22 | 0.99861 | -0.026787 | 0.028586 | 0.0071644
23 | 0.99901 | -0.018941 | 0.039 | 0.0097744
24 | 0.98564 | -0.27524 | 0.011395 | 0.0028557
25 | 0.98991 | -0.19327 | 0.026115 | 0.006545
26 | 0.99035 | -0.18473 | 0.031454 | 0.0078831
27 | 0.98056 | -0.37488 | 0.0031155 | 0.00078082
28 | 0.9806 | -0.37411 | 0.0031812 | 0.00079727
29 | 0.98156 | -0.35528 | 0.029142 | 0.0073036
30 | 0.99173 | -0.15801 | 0.060506 | 0.015164
31 | 1 | 0 | -0.49895 | -0.12669
32 | 0.98319 | -0.32355 | 0.027233 | 0.0068252
33 | 0.9906 | -0.1798 | 0.024695 | 0.0061892
34 | 0.9912 | -0.16828 | 0 | 0
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.008261 | -0.0020704 | 0.0082622 | 0.0020709 | 1.263e-06 | 5.4072e-07 | 0.012569 | 0.012569 | 0.012569 | 0.97802 | -0.42398 | 0.97818 | -0.42078 | 3.4529
1 | -0.016019 | -0.004015 | 0.016019 | 0.0040151 | 1.8786e-07 | 1.0964e-07 | 0.024368 | 0.024368 | 0.024368 | 0.97818 | -0.42078 | 0.9782 | -0.42053 | 6.6946
2 | -0.016019 | -0.0040151 | 0.016027 | 0.0040199 | 8.1939e-06 | 4.7819e-06 | 0.024368 | 0.024368 | 0.024368 | 0.9782 | -0.42053 | 0.97874 | -0.4098 | 6.6946
3 | -0.033606 | -0.0084256 | 0.033608 | 0.0084268 | 1.9302e-06 | 1.2105e-06 | 0.051094 | 0.051094 | 0.051094 | 0.97874 | -0.4098 | 0.9788 | -0.40859 | 14.0368
4 | 0.033644 | 0.008449 | -0.033608 | -0.0084268 | 3.5378e-05 | 2.2187e-05 | 0.051094 | 0.051094 | 0.051094 | 0.97993 | -0.38653 | 0.9788 | -0.40859 | 14.0368
5 | -0.033644 | -0.008449 | 0.033653 | 0.0084547 | 9.1624e-06 | 5.746e-06 | 0.051094 | 0.051094 | 0.051094 | 0.97993 | -0.38653 | 0.98022 | -0.38082 | 14.0368
6 | -0.049617 | -0.012456 | 0.049648 | 0.012475 | 3.0318e-05 | 1.9224e-05 | 0.075328 | 0.075328 | 0.075328 | 0.98022 | -0.38082 | 0.98088 | -0.36802 | 20.6946
7 | -0.10656 | -0.027094 | 0.10678 | 0.027234 | 0.00021947 | 0.00014017 | 0.15999 | 0.15999 | 0.15999 | 0.99191 | -0.15425 | 0.99414 | -0.11159 | 43.9536
8 | 0.10656 | 0.027094 | -0.10615 | -0.026831 | 0.00041093 | 0.00026244 | 0.15999 | 0.15999 | 0.15999 | 0.99191 | -0.15425 | 0.98773 | -0.23464 | 43.9537
9 | 0.29498 | 0.074624 | -0.29458 | -0.074372 | 0.00039577 | 0.00025217 | 0.44176 | 0.44176 | 0.44176 | 0.99414 | -0.11159 | 0.99269 | -0.13959 | 30.341
10 | -0.40175 | -0.10186 | 0.40339 | 0.1029 | 0.001635 | 0.0010439 | 0.60175 | 0.60175 | 0.60175 | 0.99414 | -0.11159 | 0.99856 | -0.027293 | 41.3293
11 | 0.096622 | 0.024444 | -0.096435 | -0.024324 | 0.00018781 | 0.0001199 | 0.14564 | 0.14564 | 0.14564 | 0.98773 | -0.23464 | 0.98564 | -0.27524 | 40.0117
12 | -0.057937 | -0.014569 | 0.058018 | 0.01462 | 8.0476e-05 | 5.1152e-05 | 0.087838 | 0.087838 | 0.087838 | 0.98168 | -0.35238 | 0.98316 | -0.32334 | 24.1314
13 | 0.057937 | 0.014569 | -0.057894 | -0.014542 | 4.3249e-05 | 2.7491e-05 | 0.087838 | 0.087838 | 0.087838 | 0.98168 | -0.35238 | 0.98088 | -0.36802 | 24.1314
14 | -0.084845 | -0.021344 | 0.08504 | 0.021469 | 0.00019547 | 0.0001247 | 0.12844 | 0.12844 | 0.12844 | 0.98316 | -0.32334 | 0.98564 | -0.27524 | 35.2859
15 | 0.010005 | 0.0025078 | -0.010003 | -0.0025072 | 1.2533e-06 | 6.1894e-07 | 0.015176 | 0.015176 | 0.015176 | 0.98095 | -0.36736 | 0.98081 | -0.36999 | 4.1693
16 | -0.010005 | -0.0025078 | 0.010006 | 0.0025083 | 9.8838e-07 | 4.8808e-07 | 0.015176 | 0.015176 | 0.015176 | 0.98095 | -0.36736 | 0.98105 | -0.36529 | 4.1693
17 | 0.010003 | 0.0025072 | -0.010002 | -0.0025067 | 1.1541e-06 | 5.7001e-07 | 0.015176 | 0.015176 | 0.015176 | 0.98081 | -0.36999 | 0.98069 | -0.37241 | 4.1693
18 | -0.030504 | -0.0076459 | 0.030519 | 0.0076549 | 1.4548e-05 | 9.0821e-06 | 0.046268 | 0.046268 | 0.046268 | 0.98105 | -0.36529 | 0.98156 | -0.35528 | 12.711
19 | 0.0062973 | 0.0015781 | -0.0062968 | -0.001578 | 5.1023e-07 | 1.3853e-07 | 0.009555 | 0.009555 | 0.009555 | 0.98069 | -0.37241 | 0.9806 | -0.37411 | 2.625
20 | 0.28894 | 0.072959 | -0.28869 | -0.072796 | 0.00025469 | 0.00016225 | 0.43331 | 0.43331 | 0.43331 | 0.99269 | -0.13959 | 0.99173 | -0.15801 | 29.7603
21 | -0.42908 | -0.10934 | 0.42964 | 0.1097 | 0.00056593 | 0.00036142 | 0.64003 | 0.64003 | 0.64003 | 0.99856 | -0.027293 | 1 | 0 | 43.9583
22 | 0.11585 | 0.029184 | -0.1157 | -0.029088 | 0.00015119 | 9.6596e-05 | 0.17486 | 0.17486 | 0.17486 | 0.98616 | -0.26556 | 0.98476 | -0.29288 | 48.0392
23 | -0.11585 | -0.029184 | 0.11622 | 0.029422 | 0.00037213 | 0.00023775 | 0.17486 | 0.17486 | 0.17486 | 0.98616 | -0.26556 | 0.98962 | -0.19863 | 48.0391
24 | 0.087112 | 0.021923 | -0.086984 | -0.021841 | 0.00012746 | 8.1324e-05 | 0.13166 | 0.13166 | 0.13166 | 0.98476 | -0.29288 | 0.98319 | -0.32355 | 36.1709
25 | -0.14552 | -0.036765 | 0.14565 | 0.036849 | 0.00013149 | 8.378e-05 | 0.21891 | 0.21891 | 0.21891 | 0.98962 | -0.19863 | 0.9906 | -0.1798 | 30.0706
26 | -0.028586 | -0.0071644 | 0.028597 | 0.007171 | 1.0688e-05 | 6.6348e-06 | 0.042596 | 0.042596 | 0.042596 | 0.99861 | -0.026787 | 0.99901 | -0.018941 | 11.7022
27 | -0.067597 | -0.016945 | 0.067658 | 0.016984 | 6.1068e-05 | 3.8873e-05 | 0.10069 | 0.10069 | 0.10069 | 0.99901 | -0.018941 | 1 | 0 | 27.6611
28 | -0.026115 | -0.006545 | 0.026125 | 0.0065515 | 1.0632e-05 | 6.5679e-06 | 0.039255 | 0.039255 | 0.039255 | 0.98991 | -0.19327 | 0.99035 | -0.18473 | 10.7844
29 | -0.057579 | -0.014435 | 0.057625 | 0.014463 | 4.5184e-05 | 2.871e-05 | 0.086515 | 0.086515 | 0.086515 | 0.99035 | -0.18473 | 0.9912 | -0.16828 | 23.768
30 | -0.0031155 | -0.00078082 | 0.0031156 | 0.00078072 | 1.1437e-07 | -9.8931e-08 | 0.0047278 | 0.0047278 | 0.0047278 | 0.98056 | -0.37488 | 0.9806 | -0.37411 | 1.2989
31 | -0.059661 | -0.014959 | 0.059751 | 0.015016 | 9.0363e-05 | 5.7459e-05 | 0.090446 | 0.090446 | 0.090446 | 0.98156 | -0.35528 | 0.98319 | -0.32355 | 24.8478
32 | 0.22818 | 0.057632 | -0.22807 | -0.057561 | 0.00011222 | 7.1295e-05 | 0.34252 | 0.34252 | 0.34252 | 0.99173 | -0.15801 | 0.9912 | -0.16828 | 23.5251
33 | -0.17035 | -0.043038 | 0.17044 | 0.043097 | 9.413e-05 | 5.9454e-05 | 0.25601 | 0.25601 | 0.25601 | 0.9906 | -0.1798 | 0.9912 | -0.16828 | 17.5831

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51822 | 0.13152

## res_load
| p_mw | q_mvar
0 | 0.008261 | 0.0020704
1 | 0.0077569 | 0.0019441
2 | 0.017579 | 0.0044057
3 | 0.015964 | 0.0040011
4 | 0.0095247 | 0.0023871
5 | 0.026827 | 0.0067235
6 | 0.0082463 | 0.0020667
7 | 0.020499 | 0.0051375
8 | 0.0037048 | 0.00092852
9 | 0.0056404 | 0.0014136
10 | 0.025688 | 0.006438
11 | 0.02859 | 0.0071653
12 | 0.029297 | 0.0073426
13 | 0.028586 | 0.0071644
14 | 0.039 | 0.0097744
15 | 0.011395 | 0.0028557
16 | 0.026115 | 0.006545
17 | 0.031454 | 0.0078831
18 | 0.0031155 | 0.00078082
19 | 0.0031812 | 0.00079727
20 | 0.029142 | 0.0073036
21 | 0.060506 | 0.015164
22 | 0.019269 | 0.0048293
23 | 0.027233 | 0.0068252
24 | 0.024695 | 0.0061892

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1