## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-963_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-963_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-963_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-963_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-963_0_4_node_43 | 0.4 | n |  | TRUE
5 | bus_LV_261-963_0_4_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_261-963_0_4_node_41 | 0.4 | n |  | TRUE
7 | bus_LV_261-963_0_4_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_261-963_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_261-963_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_261-963_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_261-963_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_261-963_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_261-963_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_261-963_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_261-963_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_261-963_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_261-963_0_4_node_56 | 0.4 | n |  | TRUE
18 | bus_LV_261-963_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_261-963_0_4_node_54 | 0.4 | n |  | TRUE
20 | bus_LV_261-963_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_261-963_0_4_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_261-963_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_261-963_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_261-963_0_4_node_52 | 0.4 | n |  | TRUE
25 | bus_LV_261-963_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_261-963_0_4_node_63 | 0.4 | n |  | TRUE
27 | bus_LV_261-963_0_4_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_261-963_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_261-963_0_4_node_58 | 0.4 | n |  | TRUE
30 | bus_LV_261-963_0_4_node_57 | 0.4 | n |  | TRUE
31 | bus_LV_261-963_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_261-963_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_261-963_0_4_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_261-963_0_4_node_47 | 0.4 | n |  | TRUE
35 | bus_LV_261-963_0_4_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_261-963_0_4_node_46 | 0.4 | n |  | TRUE
37 | bus_LV_261-963_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_261-963_0_4_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_261-963_0_4_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_261-963_0_4_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_261-963_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_261-963_0_4_node_53 | 0.4 | n |  | TRUE
43 | bus_LV_261-963_0_4_node_51 | 0.4 | n |  | TRUE
44 | bus_LV_261-963_0_4_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_261-963_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_261-963_0_4_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_261-963_0_4_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_261-963_0_4_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_261-963_0_4_node_62 | 0.4 | n |  | TRUE
50 | bus_LV_261-963_0_4_node_59 | 0.4 | n |  | TRUE
51 | bus_LV_261-963_0_4_node_60 | 0.4 | n |  | TRUE
52 | bus_LV_261-963_0_4_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_261-963_0_4_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_261-963_0_4_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_261-963_0_4_node_61 | 0.4 | n |  | TRUE
56 | bus_LV_261-963_0_4_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_261-963_0_4_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_261-963_0_4_node_50 | 0.4 | n |  | TRUE
59 | bus_MV_494_0_node_92 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-963_0_4_load_0 | 0 | 0.072269 | 0.018112 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-963_0_4_load_4 | 3 | 0.00050273 | 0.00012599 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-963_0_4_load_43 | 4 | 0.0024803 | 0.00062163 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-963_0_4_load_24 | 5 | 0.0047451 | 0.0011892 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-963_0_4_load_41 | 6 | 0.002387 | 0.00059824 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-963_0_4_load_6 | 8 | 0.0036763 | 0.00092137 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-963_0_4_load_10 | 12 | 0.0087076 | 0.0021823 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-963_0_4_load_12 | 14 | 0.039655 | 0.0099385 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-963_0_4_load_15 | 15 | 0.0013289 | 0.00033304 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-963_0_4_load_13 | 16 | 0.031684 | 0.0079408 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-963_0_4_load_56 | 17 | 0.0087276 | 0.0021873 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-963_0_4_load_20 | 18 | 0.0025242 | 0.00063263 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-963_0_4_load_54 | 19 | 0.008657 | 0.0021697 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-963_0_4_load_16 | 20 | 0.034523 | 0.0086524 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-963_0_4_load_25 | 21 | 0.010089 | 0.0025287 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-963_0_4_load_14 | 22 | 0.049688 | 0.012453 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-963_0_4_load_19 | 23 | 0.0097682 | 0.0024481 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-963_0_4_load_52 | 24 | 0.003202 | 0.0008025 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-963_0_4_load_63 | 26 | 0.061056 | 0.015302 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-963_0_4_load_26 | 27 | 0.008965 | 0.0022468 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-963_0_4_load_58 | 29 | 0.0063172 | 0.0015832 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-963_0_4_load_57 | 30 | 0.0067695 | 0.0016966 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-963_0_4_load_22 | 31 | 0.0024246 | 0.00060767 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-963_0_4_load_23 | 32 | 0.0038613 | 0.00096774 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-963_0_4_load_38 | 33 | 0.0054695 | 0.0013708 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-963_0_4_load_47 | 34 | 0.0038318 | 0.00096034 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-963_0_4_load_39 | 35 | 0.0082758 | 0.0020741 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-963_0_4_load_46 | 36 | 0.010856 | 0.0027207 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-963_0_4_load_27 | 37 | 0.001257 | 0.00031503 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-963_0_4_load_30 | 40 | 0.0057827 | 0.0014493 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-963_0_4_load_32 | 41 | 0.02036 | 0.0051027 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-963_0_4_load_53 | 42 | 0.0086324 | 0.0021635 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-963_0_4_load_51 | 43 | 0.0013648 | 0.00034204 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-963_0_4_load_33 | 44 | 0.014358 | 0.0035984 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-963_0_4_load_62 | 49 | 0.012728 | 0.0031899 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-963_0_4_load_59 | 50 | 0.00061635 | 0.00015447 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-963_0_4_load_40 | 53 | 0.002028 | 0.00050826 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-963_0_4_load_45 | 54 | 0.001768 | 0.00044311 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-963_0_4_load_61 | 55 | 0.00052377 | 0.00013127 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-963_0_4_load_48 | 56 | 0.0016248 | 0.00040723 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-963_0_4_load_49 | 57 | 0.0083425 | 0.0020908 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-963_0_4_load_50 | 58 | 0.0082082 | 0.0020572 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-963_0_4_line_0 |  | 0 | 1 | 0.025784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-963_0_4_line_1 |  | 1 | 2 | 0.026905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-963_0_4_line_2 |  | 1 | 3 | 0.01297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-963_0_4_line_3 |  | 2 | 4 | 0.019459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-963_0_4_line_4 |  | 2 | 5 | 0.048705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-963_0_4_line_5 |  | 4 | 6 | 0.0085531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-963_0_4_line_6 |  | 5 | 7 | 0.05506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-963_0_4_line_7 |  | 6 | 53 | 0.032517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-963_0_4_line_8 |  | 7 | 31 | 0.015137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-963_0_4_line_9 |  | 7 | 32 | 0.027267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-963_0_4_line_10 |  | 7 | 23 | 0.026659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_261-963_0_4_line_11 |  | 8 | 9 | 0.0086528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-963_0_4_line_12 |  | 8 | 10 | 0.020154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_261-963_0_4_line_13 |  | 9 | 11 | 0.037604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_261-963_0_4_line_14 |  | 9 | 12 | 0.017969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-963_0_4_line_15 |  | 10 | 13 | 0.017739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_261-963_0_4_line_16 |  | 10 | 14 | 0.045037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_261-963_0_4_line_17 |  | 11 | 15 | 0.0097205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-963_0_4_line_18 |  | 11 | 16 | 0.023273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-963_0_4_line_19 |  | 12 | 17 | 0.018457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-963_0_4_line_20 |  | 13 | 18 | 0.021333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_261-963_0_4_line_21 |  | 13 | 19 | 0.021342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-963_0_4_line_22 |  | 14 | 20 | 0.032408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-963_0_4_line_23 |  | 15 | 21 | 0.0074923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-963_0_4_line_24 |  | 16 | 22 | 0.035611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-963_0_4_line_25 |  | 18 | 23 | 4.3552e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_261-963_0_4_line_26 |  | 19 | 24 | 0.012792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-963_0_4_line_27 |  | 20 | 25 | 0.03364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-963_0_4_line_28 |  | 21 | 27 | 0.017271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-963_0_4_line_29 |  | 22 | 26 | 0.013013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-963_0_4_line_30 |  | 24 | 58 | 0.0049669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-963_0_4_line_31 |  | 25 | 28 | 0.025813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-963_0_4_line_32 |  | 28 | 29 | 0.018981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-963_0_4_line_33 |  | 29 | 30 | 0.036912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-963_0_4_line_34 |  | 31 | 33 | 0.0056418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-963_0_4_line_35 |  | 32 | 34 | 0.016936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-963_0_4_line_36 |  | 33 | 35 | 0.020308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-963_0_4_line_37 |  | 34 | 36 | 0.0065405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-963_0_4_line_38 |  | 36 | 40 | 0.0047123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-963_0_4_line_39 |  | 37 | 38 | 0.021374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-963_0_4_line_40 |  | 37 | 39 | 0.0055774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-963_0_4_line_41 |  | 38 | 40 | 0.03525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-963_0_4_line_42 |  | 39 | 41 | 0.015071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-963_0_4_line_43 |  | 42 | 43 | 0.0026624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-963_0_4_line_44 |  | 43 | 57 | 0.015216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-963_0_4_line_45 |  | 44 | 45 | 0.022356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-963_0_4_line_46 |  | 45 | 46 | 0.002241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-963_0_4_line_47 |  | 46 | 47 | 0.042122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-963_0_4_line_48 |  | 47 | 48 | 0.047576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-963_0_4_line_49 |  | 47 | 49 | 0.017419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-963_0_4_line_50 |  | 48 | 52 | 0.089584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-963_0_4_line_51 |  | 49 | 51 | 0.021029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-963_0_4_line_52 |  | 50 | 51 | 0.02661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-963_0_4_line_53 |  | 51 | 55 | 0.0083274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-963_0_4_line_54 |  | 52 | 54 | 0.024346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-963_0_4_line_55 |  | 52 | 53 | 0.0071774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-963_0_4_line_56 |  | 56 | 57 | 0.0016518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-963_0_4_line_57 |  | 56 | 58 | 0.01577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-963_0_4_trafo_12 | 0.63 MVA 20/0.4 kV | 59 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2685488.7887 | 1244939.4835 | 2685466.2689 | 1244926.9276
1 | 2685488.7887 | 1244939.4835 | 2685476.0235 | 1244963.1837
2 | 2685488.7887 | 1244939.4835 | 2685495.0109 | 1244928.1031
3 | 2685476.0235 | 1244963.1837 | 2685493.1656 | 1244972.393
4 | 2685476.0235 | 1244963.1837 | 2685450.7181 | 1245004.7982
5 | 2685501.5942 | 1244973.8472 | 2685493.1656 | 1244972.393 | 2685493.1656 | 1244972.393
6 | 2685421.7758 | 1245051.634 | 2685431.229 | 1245035.9142 | 2685433.5478 | 1245032.3227 | 2685442.1314 | 1245018.7474 | 2685444.8689 | 1245014.417 | 2685450.7181 | 1245004.7982
7 | 2685531.3283 | 1244963.9187 | 2685518.6004 | 1244972.493 | 2685504.4878 | 1244974.3465 | 2685501.5942 | 1244973.8472
8 | 2685421.7758 | 1245051.634 | 2685434.5745 | 1245059.7167
9 | 2685421.7758 | 1245051.634 | 2685407.407 | 1245074.8081
10 | 2685421.7758 | 1245051.634 | 2685398.0063 | 1245039.563
11 | 2685334.7208 | 1245014.9988 | 2685342.8875 | 1245017.8585
12 | 2685361.909 | 1245024.5191 | 2685342.8875 | 1245017.8585
13 | 2685300.1535 | 1244999.9573 | 2685334.7208 | 1245014.9988
14 | 2685334.7208 | 1245014.9988 | 2685326.1541 | 1245030.7938
15 | 2685361.909 | 1245024.5191 | 2685378.6278 | 1245030.5864
16 | 2685361.909 | 1245024.5191 | 2685383.7383 | 1244985.1259
17 | 2685300.1535 | 1244999.9573 | 2685291.4881 | 1244995.5531
18 | 2685300.1535 | 1244999.9573 | 2685305.7702 | 1244996.1464 | 2685313.4718 | 1244981.5706
19 | 2685326.1541 | 1245030.7938 | 2685317.3548 | 1245047.0178
20 | 2685378.6278 | 1245030.5864 | 2685386.8922 | 1245033.9189 | 2685397.9675 | 1245039.5433
21 | 2685378.6278 | 1245030.5864 | 2685367.9888 | 1245049.088
22 | 2685399.4461 | 1244956.7796 | 2685383.7383 | 1244985.1259
23 | 2685291.4881 | 1244995.5531 | 2685284.809 | 1244992.1584
24 | 2685330.1085 | 1244950.0848 | 2685313.4718 | 1244981.5706
25 | 2685398.0063 | 1245039.563 | 2685397.9675 | 1245039.5433
26 | 2685361.6123 | 1245060.177 | 2685367.9888 | 1245049.088
27 | 2685420.7458 | 1244943.7511 | 2685409.7786 | 1244938.1335 | 2685399.4461 | 1244956.7796
28 | 2685284.809 | 1244992.1584 | 2685269.4128 | 1244984.3332
29 | 2685330.1085 | 1244950.0848 | 2685336.2661 | 1244938.6205
30 | 2685361.6123 | 1245060.177 | 2685359.1363 | 1245064.4828
31 | 2685420.7458 | 1244943.7511 | 2685443.2474 | 1244956.5178
32 | 2685443.2474 | 1244956.5178 | 2685433.5557 | 1244972.8383
33 | 2685417.9838 | 1245003.7221 | 2685429.1515 | 1244985.0024 | 2685427.0764 | 1244983.7494 | 2685433.5557 | 1244972.8383
34 | 2685439.3447 | 1245062.7292 | 2685434.5745 | 1245059.7167
35 | 2685398.4821 | 1245089.2021 | 2685407.407 | 1245074.8081
36 | 2685456.5151 | 1245073.5727 | 2685439.3447 | 1245062.7292
37 | 2685395.0356 | 1245094.7608 | 2685398.4821 | 1245089.2021
38 | 2685395.0356 | 1245094.7608 | 2685394.4971 | 1245095.6292 | 2685392.1571 | 1245098.483
39 | 2685367.1248 | 1245123.0666 | 2685378.0616 | 1245134.4434 | 2685381.936 | 1245138.4769
40 | 2685385.8275 | 1245142.4722 | 2685383.5634 | 1245140.1713 | 2685381.936 | 1245138.4769
41 | 2685367.1248 | 1245123.0666 | 2685379.3454 | 1245112.9906 | 2685382.1518 | 1245110.6848 | 2685392.1571 | 1245098.483
42 | 2685385.8275 | 1245142.4722 | 2685397.8256 | 1245151.5919
43 | 2685342.8666 | 1245092.7766 | 2685341.5394 | 1245095.0846
44 | 2685342.8666 | 1245092.7766 | 2685350.4517 | 1245079.5857
45 | 2685583.5362 | 1245059.9047 | 2685603.7844 | 1245069.3812
46 | 2685581.5021 | 1245058.9524 | 2685583.5362 | 1245059.9047
47 | 2685595.9073 | 1245022.1665 | 2685598.376 | 1245023.3808 | 2685581.5021 | 1245058.9524
48 | 2685605.9734 | 1244982.8829 | 2685612.8246 | 1244985.6949 | 2685595.9073 | 1245022.1665
49 | 2685595.9073 | 1245022.1665 | 2685580.2834 | 1245014.4651
50 | 2685537.281 | 1244959.9086 | 2685550.9578 | 1244953.1786 | 2685557.5984 | 1244952.2626 | 2685567.3143 | 1244952.9365 | 2685574.5123 | 1244956.3317 | 2685610.2771 | 1244973.1934 | 2685605.9734 | 1244982.8829
51 | 2685561.4218 | 1245005.1677 | 2685580.2834 | 1245014.4651
52 | 2685561.4218 | 1245005.1677 | 2685550.4663 | 1245029.4178
53 | 2685561.4218 | 1245005.1677 | 2685559.6436 | 1245004.2859 | 2685562.3863 | 1244998.567
54 | 2685537.281 | 1244959.9086 | 2685546.2483 | 1244971.0905 | 2685555.2209 | 1244975.6232
55 | 2685537.281 | 1244959.9086 | 2685531.3283 | 1244963.9187
56 | 2685351.2751 | 1245078.1538 | 2685350.4517 | 1245079.5857
57 | 2685351.2751 | 1245078.1538 | 2685359.1363 | 1245064.4828

## bus_geodata
| x | y | coords
0 | 2685466.2689 | 1244926.9276
1 | 2685488.7887 | 1244939.4835
2 | 2685476.0235 | 1244963.1837
3 | 2685495.0109 | 1244928.1031
4 | 2685493.1656 | 1244972.393
5 | 2685450.7181 | 1245004.7982
6 | 2685501.5942 | 1244973.8472
7 | 2685421.7758 | 1245051.634
8 | 2685342.8875 | 1245017.8585
9 | 2685334.7208 | 1245014.9988
10 | 2685361.909 | 1245024.5191
11 | 2685300.1535 | 1244999.9573
12 | 2685326.1541 | 1245030.7938
13 | 2685378.6278 | 1245030.5864
14 | 2685383.7383 | 1244985.1259
15 | 2685291.4881 | 1244995.5531
16 | 2685313.4718 | 1244981.5706
17 | 2685317.3548 | 1245047.0178
18 | 2685397.9675 | 1245039.5433
19 | 2685367.9888 | 1245049.088
20 | 2685399.4461 | 1244956.7796
21 | 2685284.809 | 1244992.1584
22 | 2685330.1085 | 1244950.0848
23 | 2685398.0063 | 1245039.563
24 | 2685361.6123 | 1245060.177
25 | 2685420.7458 | 1244943.7511
26 | 2685336.2661 | 1244938.6205
27 | 2685269.4128 | 1244984.3332
28 | 2685443.2474 | 1244956.5178
29 | 2685433.5557 | 1244972.8383
30 | 2685417.9838 | 1245003.7221
31 | 2685434.5745 | 1245059.7167
32 | 2685407.407 | 1245074.8081
33 | 2685439.3447 | 1245062.7292
34 | 2685398.4821 | 1245089.2021
35 | 2685456.5151 | 1245073.5727
36 | 2685395.0356 | 1245094.7608
37 | 2685381.936 | 1245138.4769
38 | 2685367.1248 | 1245123.0666
39 | 2685385.8275 | 1245142.4722
40 | 2685392.1571 | 1245098.483
41 | 2685397.8256 | 1245151.5919
42 | 2685341.5394 | 1245095.0846
43 | 2685342.8666 | 1245092.7766
44 | 2685603.7844 | 1245069.3812
45 | 2685583.5362 | 1245059.9047
46 | 2685581.5021 | 1245058.9524
47 | 2685595.9073 | 1245022.1665
48 | 2685605.9734 | 1244982.8829
49 | 2685580.2834 | 1245014.4651
50 | 2685550.4663 | 1245029.4178
51 | 2685561.4218 | 1245005.1677
52 | 2685537.281 | 1244959.9086
53 | 2685531.3283 | 1244963.9187
54 | 2685555.2209 | 1244975.6232
55 | 2685562.3863 | 1244998.567
56 | 2685351.2751 | 1245078.1538
57 | 2685350.4517 | 1245079.5857
58 | 2685359.1363 | 1245064.4828
59 | 2685361.909 | 1245024.5191

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97522 | -0.4774 | 0.072269 | 0.018112
1 | 0.97695 | -0.44331 | 0 | 0
2 | 0.97877 | -0.40762 | 0 | 0
3 | 0.97695 | -0.44343 | 0.00050273 | 0.00012599
4 | 0.9781 | -0.42069 | 0.0024803 | 0.00062163
5 | 0.98374 | -0.31092 | 0.0047451 | 0.0011892
6 | 0.97783 | -0.42606 | 0.002387 | 0.00059824
7 | 0.98961 | -0.19813 | 0 | 0
8 | 0.99315 | -0.13045 | 0.0036763 | 0.00092137
9 | 0.99267 | -0.13964 | 0 | 0
10 | 0.99429 | -0.10864 | 0 | 0
11 | 0.9908 | -0.17581 | 0 | 0
12 | 0.99239 | -0.14518 | 0.0087076 | 0.0021823
13 | 0.99304 | -0.13253 | 0 | 0
14 | 1 | 0 | -0.46806 | -0.11922
15 | 0.99062 | -0.17932 | 0.0013289 | 0.00033304
16 | 0.98927 | -0.20528 | 0.031684 | 0.0079408
17 | 0.99224 | -0.14803 | 0.0087276 | 0.0021873
18 | 0.99179 | -0.15629 | 0.0025242 | 0.00063263
19 | 0.99225 | -0.14764 | 0.008657 | 0.0021697
20 | 0.9986 | -0.026933 | 0.034523 | 0.0086524
21 | 0.99048 | -0.18186 | 0.010089 | 0.0025287
22 | 0.98564 | -0.27577 | 0.049688 | 0.012453
23 | 0.99179 | -0.15634 | 0.0097682 | 0.0024481
24 | 0.99189 | -0.15475 | 0.003202 | 0.0008025
25 | 0.9982 | -0.034632 | 0 | 0
26 | 0.98491 | -0.29004 | 0.061056 | 0.015302
27 | 0.99034 | -0.18461 | 0.008965 | 0.0022468
28 | 0.99789 | -0.040544 | 0 | 0
29 | 0.99767 | -0.044893 | 0.0063172 | 0.0015832
30 | 0.99744 | -0.04927 | 0.0067695 | 0.0016966
31 | 0.98938 | -0.20249 | 0.0024246 | 0.00060767
32 | 0.98846 | -0.22046 | 0.0038613 | 0.00096774
33 | 0.98931 | -0.20387 | 0.0054695 | 0.0013708
34 | 0.9878 | -0.23318 | 0.0038318 | 0.00096034
35 | 0.98916 | -0.20686 | 0.0082758 | 0.0020741
36 | 0.98757 | -0.23765 | 0.010856 | 0.0027207
37 | 0.98633 | -0.26187 | 0.001257 | 0.00031503
38 | 0.98675 | -0.25359 | 0 | 0
39 | 0.98622 | -0.2639 | 0 | 0
40 | 0.98745 | -0.23996 | 0.0057827 | 0.0014493
41 | 0.98594 | -0.2694 | 0.02036 | 0.0051027
42 | 0.99128 | -0.16645 | 0.0086324 | 0.0021635
43 | 0.9913 | -0.16604 | 0.0013648 | 0.00034204
44 | 0.97216 | -0.53767 | 0.014358 | 0.0035984
45 | 0.97246 | -0.53175 | 0 | 0
46 | 0.97249 | -0.53116 | 0 | 0
47 | 0.97305 | -0.52002 | 0 | 0
48 | 0.9743 | -0.49532 | 0 | 0
49 | 0.97282 | -0.52446 | 0.012728 | 0.0031899
50 | 0.97279 | -0.52521 | 0.00061635 | 0.00015447
51 | 0.9728 | -0.52491 | 0 | 0
52 | 0.97666 | -0.449 | 0 | 0
53 | 0.97686 | -0.44506 | 0.002028 | 0.00050826
54 | 0.97662 | -0.44978 | 0.001768 | 0.00044311
55 | 0.9728 | -0.52499 | 0.00052377 | 0.00013127
56 | 0.99147 | -0.16281 | 0.0016248 | 0.00040723
57 | 0.99144 | -0.16335 | 0.0083425 | 0.0020908
58 | 0.99176 | -0.15723 | 0.0082082 | 0.0020572
59 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.072269 | -0.018112 | 0.072387 | 0.018187 | 0.00011757 | 7.4922e-05 | 0.11027 | 0.11027 | 0.11027 | 0.97522 | -0.4774 | 0.97695 | -0.44331 | 30.2941
1 | -0.07289 | -0.018313 | 0.073014 | 0.018392 | 0.00012439 | 7.9273e-05 | 0.11104 | 0.11104 | 0.11104 | 0.97695 | -0.44331 | 0.97877 | -0.40762 | 30.5044
2 | 0.00050273 | 0.00012583 | -0.00050273 | -0.00012599 | 2.8516e-09 | -1.6058e-07 | 0.00076566 | 0.00076572 | 0.00076572 | 0.97695 | -0.44331 | 0.97695 | -0.44343 | 0.21036
3 | 0.037067 | 0.0093546 | -0.037044 | -0.00934 | 2.3192e-05 | 1.4599e-05 | 0.056376 | 0.056376 | 0.056376 | 0.97877 | -0.40762 | 0.9781 | -0.42069 | 15.4879
4 | -0.11008 | -0.027747 | 0.11059 | 0.028074 | 0.00051189 | 0.00032699 | 0.16741 | 0.16741 | 0.16741 | 0.97877 | -0.40762 | 0.98374 | -0.31092 | 45.9923
5 | 0.034564 | 0.0087184 | -0.034555 | -0.0087128 | 8.875e-06 | 5.5727e-06 | 0.052603 | 0.052603 | 0.052603 | 0.9781 | -0.42069 | 0.97783 | -0.42606 | 14.4513
6 | -0.11534 | -0.029263 | 0.11597 | 0.029665 | 0.00062937 | 0.00040209 | 0.17459 | 0.17459 | 0.17459 | 0.98374 | -0.31092 | 0.98961 | -0.19813 | 47.964
7 | 0.032168 | 0.0081146 | -0.032138 | -0.0080963 | 2.9242e-05 | 1.8307e-05 | 0.04897 | 0.04897 | 0.04897 | 0.97783 | -0.42606 | 0.97686 | -0.44506 | 13.4534
8 | 0.016175 | 0.0040555 | -0.016172 | -0.0040536 | 3.3581e-06 | 1.9548e-06 | 0.024323 | 0.024323 | 0.024323 | 0.98961 | -0.19813 | 0.98938 | -0.20249 | 6.682
9 | 0.046065 | 0.011588 | -0.046015 | -0.011557 | 4.9078e-05 | 3.106e-05 | 0.06928 | 0.06928 | 0.06928 | 0.98961 | -0.19813 | 0.98846 | -0.22046 | 19.033
10 | -0.17821 | -0.045309 | 0.17857 | 0.045539 | 0.00035953 | 0.00022941 | 0.26819 | 0.26819 | 0.26819 | 0.98961 | -0.19813 | 0.99179 | -0.15634 | 36.8394
11 | 0.18124 | 0.045805 | -0.18116 | -0.045755 | 7.9835e-05 | 5.0759e-05 | 0.27168 | 0.27168 | 0.27168 | 0.99315 | -0.13045 | 0.99267 | -0.13964 | 24.8794
12 | -0.18492 | -0.046727 | 0.18511 | 0.04685 | 0.00019357 | 0.0001231 | 0.27719 | 0.27719 | 0.27719 | 0.99315 | -0.13045 | 0.99429 | -0.10864 | 25.3838
13 | 0.16372 | 0.041382 | -0.16344 | -0.041202 | 0.00028339 | 0.00017991 | 0.24554 | 0.24554 | 0.24554 | 0.99267 | -0.13964 | 0.9908 | -0.17581 | 22.4852
14 | 0.017441 | 0.0043729 | -0.017436 | -0.0043702 | 4.6059e-06 | 2.7155e-06 | 0.026145 | 0.026145 | 0.026145 | 0.99267 | -0.13964 | 0.99239 | -0.14518 | 7.1826
15 | 0.23143 | 0.058993 | -0.23116 | -0.058823 | 0.00026653 | 0.00016989 | 0.3467 | 0.3467 | 0.3467 | 0.99429 | -0.10864 | 0.99304 | -0.13253 | 31.749
16 | -0.41654 | -0.10584 | 0.41873 | 0.10724 | 0.0021913 | 0.0014007 | 0.62389 | 0.62389 | 0.62389 | 0.99429 | -0.10864 | 1 | 0 | 57.1327
17 | 0.02039 | 0.0051125 | -0.020387 | -0.0051104 | 3.4185e-06 | 2.0627e-06 | 0.030624 | 0.030624 | 0.030624 | 0.9908 | -0.17581 | 0.99062 | -0.17932 | 8.4131
18 | 0.14304 | 0.036089 | -0.14284 | -0.035961 | 0.00020155 | 0.00012839 | 0.21492 | 0.21492 | 0.21492 | 0.9908 | -0.17581 | 0.98927 | -0.20528 | 29.5213
19 | 0.0087287 | 0.0021879 | -0.0087276 | -0.0021873 | 1.1856e-06 | 5.2037e-07 | 0.013088 | 0.013088 | 0.013088 | 0.99239 | -0.14518 | 0.99224 | -0.14803 | 3.5957
20 | 0.19108 | 0.048759 | -0.19086 | -0.04862 | 0.00021908 | 0.00013938 | 0.28663 | 0.28663 | 0.28663 | 0.99304 | -0.13253 | 0.99179 | -0.15629 | 26.2484
21 | 0.040082 | 0.010064 | -0.040053 | -0.010046 | 2.8877e-05 | 1.8205e-05 | 0.060067 | 0.060067 | 0.060067 | 0.99304 | -0.13253 | 0.99225 | -0.14764 | 16.502
22 | 0.047684 | 0.011978 | -0.047623 | -0.011939 | 6.12e-05 | 3.8744e-05 | 0.070964 | 0.070964 | 0.070964 | 1 | 0 | 0.9986 | -0.026933 | 19.4956
23 | 0.019058 | 0.0047774 | -0.019056 | -0.004776 | 2.3026e-06 | 1.3772e-06 | 0.028628 | 0.028628 | 0.028628 | 0.99062 | -0.17932 | 0.99048 | -0.18186 | 7.8647
24 | 0.11116 | 0.02802 | -0.11079 | -0.027781 | 0.00037358 | 0.00023864 | 0.16726 | 0.16726 | 0.16726 | 0.98927 | -0.20528 | 0.98564 | -0.27577 | 45.9499
25 | 0.18834 | 0.047987 | -0.18834 | -0.047987 | 4.3553e-07 | 2.7705e-07 | 0.28285 | 0.28285 | 0.28285 | 0.99179 | -0.15629 | 0.99179 | -0.15634 | 25.9016
26 | 0.031396 | 0.0078761 | -0.031385 | -0.0078695 | 1.0635e-05 | 6.641e-06 | 0.047085 | 0.047085 | 0.047085 | 0.99225 | -0.14764 | 0.99189 | -0.15475 | 12.9354
27 | 0.013099 | 0.0032864 | -0.013094 | -0.0032838 | 4.8069e-06 | 2.6365e-06 | 0.01952 | 0.019521 | 0.019521 | 0.9986 | -0.026933 | 0.9982 | -0.034632 | 5.3628
28 | 0.0089662 | 0.0022474 | -0.008965 | -0.0022468 | 1.1751e-06 | 5.2982e-07 | 0.01347 | 0.01347 | 0.01347 | 0.99048 | -0.18186 | 0.99034 | -0.18461 | 3.7006
29 | 0.061098 | 0.015329 | -0.061056 | -0.015302 | 4.1524e-05 | 2.641e-05 | 0.092245 | 0.092245 | 0.092245 | 0.98564 | -0.27577 | 0.98491 | -0.29004 | 25.3419
30 | 0.028183 | 0.007067 | -0.02818 | -0.0070649 | 3.3298e-06 | 2.067e-06 | 0.042281 | 0.042281 | 0.042281 | 0.99189 | -0.15475 | 0.99176 | -0.15723 | 11.6158
31 | 0.013094 | 0.0032838 | -0.013091 | -0.0032817 | 3.6886e-06 | 2.0234e-06 | 0.019521 | 0.019521 | 0.019521 | 0.9982 | -0.034632 | 0.99789 | -0.040544 | 5.3628
32 | 0.013091 | 0.0032817 | -0.013088 | -0.0032802 | 2.7124e-06 | 1.488e-06 | 0.019521 | 0.019521 | 0.019521 | 0.99789 | -0.040544 | 0.99767 | -0.044893 | 5.3629
33 | 0.0067709 | 0.001697 | -0.0067695 | -0.0016966 | 1.4117e-06 | 4.216e-07 | 0.010099 | 0.010099 | 0.010099 | 0.99767 | -0.044893 | 0.99744 | -0.04927 | 2.7744
34 | 0.013747 | 0.0034459 | -0.013746 | -0.0034454 | 9.0445e-07 | 5.064e-07 | 0.020676 | 0.020676 | 0.020676 | 0.98938 | -0.20249 | 0.98931 | -0.20387 | 5.6802
35 | 0.042154 | 0.010589 | -0.042129 | -0.010573 | 2.5583e-05 | 1.6156e-05 | 0.063467 | 0.063467 | 0.063467 | 0.98846 | -0.22046 | 0.9878 | -0.23318 | 17.4361
36 | 0.008277 | 0.0020746 | -0.0082758 | -0.0020741 | 1.1803e-06 | 4.9468e-07 | 0.012449 | 0.01245 | 0.01245 | 0.98931 | -0.20387 | 0.98916 | -0.20686 | 3.4202
37 | 0.038297 | 0.0096129 | -0.038289 | -0.0096078 | 8.1643e-06 | 5.1414e-06 | 0.057695 | 0.057695 | 0.057695 | 0.9878 | -0.23318 | 0.98757 | -0.23765 | 15.8503
38 | 0.027433 | 0.0068871 | -0.02743 | -0.0068852 | 3.0197e-06 | 1.8723e-06 | 0.041338 | 0.041338 | 0.041338 | 0.98757 | -0.23765 | 0.98745 | -0.23996 | 11.3567
39 | -0.021624 | -0.0054222 | 0.021633 | 0.0054274 | 8.5311e-06 | 5.187e-06 | 0.032625 | 0.032624 | 0.032625 | 0.98633 | -0.26187 | 0.98675 | -0.25359 | 8.9628
40 | 0.020367 | 0.0051072 | -0.020366 | -0.005106 | 1.9749e-06 | 1.1927e-06 | 0.030728 | 0.030728 | 0.030728 | 0.98633 | -0.26187 | 0.98622 | -0.2639 | 8.4418
41 | -0.021633 | -0.0054274 | 0.021647 | 0.0054359 | 1.407e-05 | 8.5539e-06 | 0.032624 | 0.032624 | 0.032624 | 0.98675 | -0.25359 | 0.98745 | -0.23996 | 8.9628
42 | 0.020366 | 0.005106 | -0.02036 | -0.0051027 | 5.3363e-06 | 3.223e-06 | 0.030728 | 0.030728 | 0.030728 | 0.98622 | -0.2639 | 0.98594 | -0.2694 | 8.4418
43 | -0.0086324 | -0.0021635 | 0.0086325 | 0.0021635 | 1.6764e-07 | 7.2968e-08 | 0.012958 | 0.012958 | 0.012958 | 0.99128 | -0.16645 | 0.9913 | -0.16604 | 3.5599
44 | -0.0099973 | -0.0025056 | 0.0099986 | 0.0025062 | 1.285e-06 | 6.262e-07 | 0.015007 | 0.015007 | 0.015007 | 0.9913 | -0.16604 | 0.99144 | -0.16335 | 4.1227
45 | -0.014358 | -0.0035984 | 0.014362 | 0.0036007 | 4.0489e-06 | 2.314e-06 | 0.021976 | 0.021976 | 0.021976 | 0.97216 | -0.53767 | 0.97246 | -0.53175 | 6.0374
46 | -0.014362 | -0.0036007 | 0.014362 | 0.0036009 | 4.0586e-07 | 2.3195e-07 | 0.021976 | 0.021976 | 0.021976 | 0.97246 | -0.53175 | 0.97249 | -0.53116 | 6.0374
47 | -0.014362 | -0.0036009 | 0.01437 | 0.0036053 | 7.6285e-06 | 4.3593e-06 | 0.021976 | 0.021976 | 0.021976 | 0.97249 | -0.53116 | 0.97305 | -0.52002 | 6.0374
48 | -0.028241 | -0.0070819 | 0.028274 | 0.0071026 | 3.3277e-05 | 2.0706e-05 | 0.043188 | 0.043188 | 0.043188 | 0.97305 | -0.52002 | 0.9743 | -0.49532 | 11.8649
49 | 0.013871 | 0.0034767 | -0.013868 | -0.003475 | 2.9392e-06 | 1.6647e-06 | 0.021212 | 0.021212 | 0.021212 | 0.97305 | -0.52002 | 0.97282 | -0.52446 | 5.8275
50 | -0.028274 | -0.0071026 | 0.028337 | 0.0071416 | 6.2659e-05 | 3.8983e-05 | 0.043188 | 0.043188 | 0.043188 | 0.9743 | -0.49532 | 0.97666 | -0.449 | 11.8648
51 | 0.0011402 | 0.00028507 | -0.0011401 | -0.00028531 | 2.3978e-08 | -2.4574e-07 | 0.0017437 | 0.0017438 | 0.0017438 | 0.97282 | -0.52446 | 0.9728 | -0.52491 | 0.47907
52 | -0.00061635 | -0.00015447 | 0.00061636 | 0.00015415 | 8.8685e-09 | -3.2469e-07 | 0.00094279 | 0.00094267 | 0.00094279 | 0.97279 | -0.52521 | 0.9728 | -0.52491 | 0.25901
53 | 0.00052377 | 0.00013117 | -0.00052377 | -0.00013127 | 2.0044e-09 | -1.021e-07 | 0.00080114 | 0.00080117 | 0.00080117 | 0.9728 | -0.52491 | 0.9728 | -0.52499 | 0.2201
54 | 0.0017681 | 0.00044285 | -0.001768 | -0.00044311 | 6.6249e-08 | -2.6225e-07 | 0.0026937 | 0.0026938 | 0.0026938 | 0.97666 | -0.449 | 0.97662 | -0.44978 | 0.74006
55 | -0.030105 | -0.0075845 | 0.030111 | 0.007588 | 5.6659e-06 | 3.5364e-06 | 0.045881 | 0.045881 | 0.045881 | 0.97666 | -0.449 | 0.97686 | -0.44506 | 12.6048
56 | 0.018342 | 0.0045973 | -0.018341 | -0.0045971 | 4.6937e-07 | 2.7909e-07 | 0.027528 | 0.027528 | 0.027528 | 0.99147 | -0.16281 | 0.99144 | -0.16335 | 7.5625
57 | -0.019966 | -0.0050046 | 0.019972 | 0.0050078 | 5.3104e-06 | 3.1952e-06 | 0.029966 | 0.029966 | 0.029966 | 0.99147 | -0.16281 | 0.99176 | -0.15723 | 8.2325

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50772 | 0.12916

## res_load
| p_mw | q_mvar
0 | 0.072269 | 0.018112
1 | 0.00050273 | 0.00012599
2 | 0.0024803 | 0.00062163
3 | 0.0047451 | 0.0011892
4 | 0.002387 | 0.00059824
5 | 0.0036763 | 0.00092137
6 | 0.0087076 | 0.0021823
7 | 0.039655 | 0.0099385
8 | 0.0013289 | 0.00033304
9 | 0.031684 | 0.0079408
10 | 0.0087276 | 0.0021873
11 | 0.0025242 | 0.00063263
12 | 0.008657 | 0.0021697
13 | 0.034523 | 0.0086524
14 | 0.010089 | 0.0025287
15 | 0.049688 | 0.012453
16 | 0.0097682 | 0.0024481
17 | 0.003202 | 0.0008025
18 | 0.061056 | 0.015302
19 | 0.008965 | 0.0022468
20 | 0.0063172 | 0.0015832
21 | 0.0067695 | 0.0016966
22 | 0.0024246 | 0.00060767
23 | 0.0038613 | 0.00096774
24 | 0.0054695 | 0.0013708
25 | 0.0038318 | 0.00096034
26 | 0.0082758 | 0.0020741
27 | 0.010856 | 0.0027207
28 | 0.001257 | 0.00031503
29 | 0.0057827 | 0.0014493
30 | 0.02036 | 0.0051027
31 | 0.0086324 | 0.0021635
32 | 0.0013648 | 0.00034204
33 | 0.014358 | 0.0035984
34 | 0.012728 | 0.0031899
35 | 0.00061635 | 0.00015447
36 | 0.002028 | 0.00050826
37 | 0.001768 | 0.00044311
38 | 0.00052377 | 0.00013127
39 | 0.0016248 | 0.00040723
40 | 0.0083425 | 0.0020908
41 | 0.0082082 | 0.0020572

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1