## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-96_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-96_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-96_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-96_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-96_0_5_node_33 | 0.4 | n |  | TRUE
5 | bus_LV_261-96_0_5_node_62 | 0.4 | n |  | TRUE
6 | bus_LV_261-96_0_5_node_32 | 0.4 | n |  | TRUE
7 | bus_LV_261-96_0_5_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_261-96_0_5_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_261-96_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_261-96_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_261-96_0_5_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_261-96_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_261-96_0_5_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_261-96_0_5_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_261-96_0_5_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_261-96_0_5_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_261-96_0_5_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_261-96_0_5_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_261-96_0_5_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_261-96_0_5_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_261-96_0_5_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_261-96_0_5_node_39 | 0.4 | n |  | TRUE
23 | bus_LV_261-96_0_5_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_261-96_0_5_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_261-96_0_5_node_131 | 0.4 | n |  | TRUE
26 | bus_LV_261-96_0_5_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_261-96_0_5_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_261-96_0_5_node_135 | 0.4 | n |  | TRUE
29 | bus_LV_261-96_0_5_node_63 | 0.4 | n |  | TRUE
30 | bus_LV_261-96_0_5_node_59 | 0.4 | n |  | TRUE
31 | bus_LV_261-96_0_5_node_58 | 0.4 | n |  | TRUE
32 | bus_LV_261-96_0_5_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_261-96_0_5_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_261-96_0_5_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_261-96_0_5_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_261-96_0_5_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_261-96_0_5_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_261-96_0_5_node_61 | 0.4 | n |  | TRUE
39 | bus_LV_261-96_0_5_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_261-96_0_5_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_261-96_0_5_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_261-96_0_5_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_261-96_0_5_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_261-96_0_5_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_261-96_0_5_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_261-96_0_5_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_261-96_0_5_node_132 | 0.4 | n |  | TRUE
48 | bus_LV_261-96_0_5_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_261-96_0_5_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_261-96_0_5_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_261-96_0_5_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_261-96_0_5_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_261-96_0_5_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_261-96_0_5_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_261-96_0_5_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_261-96_0_5_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_261-96_0_5_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_261-96_0_5_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_261-96_0_5_node_53 | 0.4 | n |  | TRUE
60 | bus_LV_261-96_0_5_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_261-96_0_5_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_261-96_0_5_node_56 | 0.4 | n |  | TRUE
63 | bus_LV_261-96_0_5_node_57 | 0.4 | n |  | TRUE
64 | bus_LV_261-96_0_5_node_78 | 0.4 | n |  | TRUE
65 | bus_LV_261-96_0_5_node_77 | 0.4 | n |  | TRUE
66 | bus_LV_261-96_0_5_node_60 | 0.4 | n |  | TRUE
67 | bus_LV_261-96_0_5_node_64 | 0.4 | n |  | TRUE
68 | bus_LV_261-96_0_5_node_65 | 0.4 | n |  | TRUE
69 | bus_LV_261-96_0_5_node_66 | 0.4 | n |  | TRUE
70 | bus_LV_261-96_0_5_node_67 | 0.4 | n |  | TRUE
71 | bus_LV_261-96_0_5_node_68 | 0.4 | n |  | TRUE
72 | bus_LV_261-96_0_5_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_261-96_0_5_node_70 | 0.4 | n |  | TRUE
74 | bus_LV_261-96_0_5_node_79 | 0.4 | n |  | TRUE
75 | bus_LV_261-96_0_5_node_119 | 0.4 | n |  | TRUE
76 | bus_LV_261-96_0_5_node_80 | 0.4 | n |  | TRUE
77 | bus_LV_261-96_0_5_node_104 | 0.4 | n |  | TRUE
78 | bus_LV_261-96_0_5_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_261-96_0_5_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_261-96_0_5_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_261-96_0_5_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_261-96_0_5_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_261-96_0_5_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_261-96_0_5_node_99 | 0.4 | n |  | TRUE
85 | bus_LV_261-96_0_5_node_103 | 0.4 | n |  | TRUE
86 | bus_LV_261-96_0_5_node_81 | 0.4 | n |  | TRUE
87 | bus_LV_261-96_0_5_node_107 | 0.4 | n |  | TRUE
88 | bus_LV_261-96_0_5_node_106 | 0.4 | n |  | TRUE
89 | bus_LV_261-96_0_5_node_82 | 0.4 | n |  | TRUE
90 | bus_LV_261-96_0_5_node_83 | 0.4 | n |  | TRUE
91 | bus_LV_261-96_0_5_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_261-96_0_5_node_86 | 0.4 | n |  | TRUE
93 | bus_LV_261-96_0_5_node_85 | 0.4 | n |  | TRUE
94 | bus_LV_261-96_0_5_node_87 | 0.4 | n |  | TRUE
95 | bus_LV_261-96_0_5_node_88 | 0.4 | n |  | TRUE
96 | bus_LV_261-96_0_5_node_89 | 0.4 | n |  | TRUE
97 | bus_LV_261-96_0_5_node_118 | 0.4 | n |  | TRUE
98 | bus_LV_261-96_0_5_node_102 | 0.4 | n |  | TRUE
99 | bus_LV_261-96_0_5_node_105 | 0.4 | n |  | TRUE
100 | bus_LV_261-96_0_5_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_261-96_0_5_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_261-96_0_5_node_120 | 0.4 | n |  | TRUE
103 | bus_LV_261-96_0_5_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_261-96_0_5_node_97 | 0.4 | n |  | TRUE
105 | bus_LV_261-96_0_5_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_261-96_0_5_node_93 | 0.4 | n |  | TRUE
107 | bus_LV_261-96_0_5_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_261-96_0_5_node_100 | 0.4 | n |  | TRUE
109 | bus_LV_261-96_0_5_node_121 | 0.4 | n |  | TRUE
110 | bus_LV_261-96_0_5_node_101 | 0.4 | n |  | TRUE
111 | bus_LV_261-96_0_5_node_130 | 0.4 | n |  | TRUE
112 | bus_LV_261-96_0_5_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_261-96_0_5_node_109 | 0.4 | n |  | TRUE
114 | bus_LV_261-96_0_5_node_111 | 0.4 | n |  | TRUE
115 | bus_LV_261-96_0_5_node_112 | 0.4 | n |  | TRUE
116 | bus_LV_261-96_0_5_node_114 | 0.4 | n |  | TRUE
117 | bus_LV_261-96_0_5_node_113 | 0.4 | n |  | TRUE
118 | bus_LV_261-96_0_5_node_115 | 0.4 | n |  | TRUE
119 | bus_LV_261-96_0_5_node_116 | 0.4 | n |  | TRUE
120 | bus_LV_261-96_0_5_node_117 | 0.4 | n |  | TRUE
121 | bus_LV_261-96_0_5_node_122 | 0.4 | n |  | TRUE
122 | bus_LV_261-96_0_5_node_123 | 0.4 | n |  | TRUE
123 | bus_LV_261-96_0_5_node_124 | 0.4 | n |  | TRUE
124 | bus_LV_261-96_0_5_node_125 | 0.4 | n |  | TRUE
125 | bus_LV_261-96_0_5_node_126 | 0.4 | n |  | TRUE
126 | bus_LV_261-96_0_5_node_127 | 0.4 | n |  | TRUE
127 | bus_LV_261-96_0_5_node_128 | 0.4 | n |  | TRUE
128 | bus_LV_261-96_0_5_node_129 | 0.4 | n |  | TRUE
129 | bus_LV_261-96_0_5_node_134 | 0.4 | n |  | TRUE
130 | bus_LV_261-96_0_5_node_133 | 0.4 | n |  | TRUE
131 | bus_MV_494_0_node_97 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-96_0_5_load_0 | 0 | 0.0018538 | 0.0004646 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-96_0_5_load_1 | 1 | 0.0016755 | 0.00041993 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-96_0_5_load_33 | 4 | 0.0057563 | 0.0014427 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-96_0_5_load_32 | 6 | 0.0057458 | 0.00144 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-96_0_5_load_18 | 7 | 0.0083234 | 0.002086 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-96_0_5_load_11 | 12 | 0.00071422 | 0.000179 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-96_0_5_load_14 | 14 | 0.00077875 | 0.00019517 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-96_0_5_load_13 | 16 | 0.0012475 | 0.00031265 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-96_0_5_load_17 | 17 | 0.0026919 | 0.00067465 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-96_0_5_load_12 | 19 | 0.023912 | 0.005993 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-96_0_5_load_39 | 22 | 0.0054205 | 0.0013585 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-96_0_5_load_34 | 24 | 0.0037664 | 0.00094395 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-96_0_5_load_131 | 25 | 0.0023744 | 0.00059509 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-96_0_5_load_36 | 26 | 0.0034247 | 0.00085831 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-96_0_5_load_35 | 27 | 0.0026122 | 0.00065468 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-96_0_5_load_135 | 28 | 0.0003991 | 0.00010003 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-96_0_5_load_58 | 31 | 0.0056133 | 0.0014068 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-96_0_5_load_19 | 32 | 0.0080118 | 0.0020079 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-96_0_5_load_21 | 34 | 0.0073165 | 0.0018337 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-96_0_5_load_22 | 35 | 0.0060084 | 0.0015058 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-96_0_5_load_23 | 36 | 0.012187 | 0.0030544 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-96_0_5_load_24 | 37 | 0.02276 | 0.0057042 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-96_0_5_load_61 | 38 | 0.0022643 | 0.00056749 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-96_0_5_load_25 | 39 | 0.01655 | 0.0041478 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-96_0_5_load_27 | 41 | 0.021012 | 0.005266 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-96_0_5_load_37 | 43 | 0.02804 | 0.0070274 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-96_0_5_load_31 | 45 | 0.014721 | 0.0036894 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-96_0_5_load_42 | 48 | 0.010413 | 0.0026097 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-96_0_5_load_43 | 49 | 0.0094948 | 0.0023796 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-96_0_5_load_44 | 50 | 0.002906 | 0.00072831 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-96_0_5_load_45 | 51 | 0.0067903 | 0.0017018 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-96_0_5_load_48 | 54 | 0.0034483 | 0.00086422 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-96_0_5_load_49 | 55 | 0.01813 | 0.0045439 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-96_0_5_load_50 | 56 | 0.0080447 | 0.0020162 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-96_0_5_load_51 | 57 | 0.0067457 | 0.0016906 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-96_0_5_load_54 | 58 | 0.0044689 | 0.00112 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-96_0_5_load_53 | 59 | 0.0062177 | 0.0015583 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-96_0_5_load_52 | 60 | 0.0098644 | 0.0024722 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-96_0_5_load_56 | 62 | 0.0069621 | 0.0017449 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-96_0_5_load_57 | 63 | 0.0065916 | 0.001652 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-96_0_5_load_78 | 64 | 0.013256 | 0.0033222 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-96_0_5_load_77 | 65 | 0.0060388 | 0.0015135 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-96_0_5_load_60 | 66 | 0.0033868 | 0.00084882 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-96_0_5_load_64 | 67 | 0.0034453 | 0.00086348 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-96_0_5_load_65 | 68 | 0.0013901 | 0.00034838 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-96_0_5_load_66 | 69 | 0.0082575 | 0.0020695 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-96_0_5_load_67 | 70 | 0.0013418 | 0.00033629 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-96_0_5_load_68 | 71 | 0.0075344 | 0.0018883 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-96_0_5_load_69 | 72 | 0.0012683 | 0.00031788 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-96_0_5_load_70 | 73 | 0.0014875 | 0.00037279 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-96_0_5_load_79 | 74 | 0.0019731 | 0.0004945 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-96_0_5_load_119 | 75 | 0.0078503 | 0.0019675 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-96_0_5_load_80 | 76 | 0.0044689 | 0.00112 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-96_0_5_load_104 | 77 | 0.0013775 | 0.00034524 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-96_0_5_load_71 | 78 | 0.011276 | 0.0028261 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-96_0_5_load_72 | 79 | 0.0092562 | 0.0023198 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-96_0_5_load_73 | 80 | 0.0048359 | 0.001212 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-96_0_5_load_74 | 81 | 0.0018068 | 0.00045284 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-96_0_5_load_75 | 82 | 0.0038939 | 0.00097591 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-96_0_5_load_76 | 83 | 0.0064465 | 0.0016156 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-96_0_5_load_99 | 84 | 0.0057328 | 0.0014368 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-96_0_5_load_81 | 86 | 0.001943 | 0.00048697 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-96_0_5_load_107 | 87 | 0.0037462 | 0.00093888 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-96_0_5_load_106 | 88 | 0.0027325 | 0.00068482 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-96_0_5_load_82 | 89 | 0.0073397 | 0.0018395 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-96_0_5_load_83 | 90 | 0.0074848 | 0.0018759 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-96_0_5_load_88 | 95 | 0.0053351 | 0.0013371 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-96_0_5_load_89 | 96 | 0.0053373 | 0.0013376 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-96_0_5_load_118 | 97 | 0.0025905 | 0.00064924 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-96_0_5_load_102 | 98 | 0.004044 | 0.0010135 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-96_0_5_load_105 | 99 | 0.0056474 | 0.0014154 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-96_0_5_load_96 | 100 | 0.0090627 | 0.0022713 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-96_0_5_load_90 | 101 | 0.0010631 | 0.00026645 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-96_0_5_load_120 | 102 | 0.0025701 | 0.00064412 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-96_0_5_load_98 | 103 | 0.00049709 | 0.00012458 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-96_0_5_load_97 | 104 | 0.0090627 | 0.0022713 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-96_0_5_load_91 | 105 | 0.00066025 | 0.00016548 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-96_0_5_load_95 | 107 | 0.00067401 | 0.00016892 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-96_0_5_load_100 | 108 | 0.00093647 | 0.0002347 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-96_0_5_load_121 | 109 | 0.00062413 | 0.00015642 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-96_0_5_load_101 | 110 | 0.0007789 | 0.00019521 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-96_0_5_load_130 | 111 | 0.00092528 | 0.0002319 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-96_0_5_load_108 | 112 | 0.0034328 | 0.00086035 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-96_0_5_load_109 | 113 | 0.012327 | 0.0030894 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-96_0_5_load_111 | 114 | 0.0038829 | 0.00097314 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-96_0_5_load_112 | 115 | 0.0031119 | 0.00077991 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-96_0_5_load_114 | 116 | 0.0020103 | 0.00050383 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-96_0_5_load_113 | 117 | 0.0068934 | 0.0017277 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-96_0_5_load_115 | 118 | 0.0024389 | 0.00061124 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-96_0_5_load_116 | 119 | 0.0019788 | 0.00049594 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-96_0_5_load_117 | 120 | 0.0025724 | 0.0006447 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-96_0_5_load_122 | 121 | 0.0025896 | 0.00064902 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-96_0_5_load_123 | 122 | 0.0041616 | 0.001043 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-96_0_5_load_124 | 123 | 0.011003 | 0.0027577 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-96_0_5_load_126 | 125 | 0.010711 | 0.0026845 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-96_0_5_load_128 | 127 | 0.0071809 | 0.0017997 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-96_0_5_load_134 | 129 | 0.0075146 | 0.0018833 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-96_0_5_load_133 | 130 | 0.007447 | 0.0018664 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 66 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-96_0_5_line_0 |  | 0 | 1 | 0.0027344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-96_0_5_line_1 |  | 0 | 2 | 0.019854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-96_0_5_line_2 |  | 2 | 3 | 0.007869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-96_0_5_line_3 |  | 3 | 11 | 0.005903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-96_0_5_line_4 |  | 3 | 12 | 0.0068966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-96_0_5_line_5 |  | 4 | 5 | 0.021923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_261-96_0_5_line_6 |  | 4 | 6 | 0.025949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-96_0_5_line_7 |  | 4 | 7 | 0.07595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_261-96_0_5_line_8 |  | 5 | 38 | 0.034261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_261-96_0_5_line_9 |  | 5 | 30 | 0.025359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_261-96_0_5_line_10 |  | 6 | 24 | 0.021592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-96_0_5_line_11 |  | 6 | 25 | 0.031683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-96_0_5_line_12 |  | 7 | 32 | 0.01411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-96_0_5_line_13 |  | 7 | 33 | 0.0050995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_261-96_0_5_line_14 |  | 8 | 9 | 0.017996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-96_0_5_line_15 |  | 8 | 10 | 0.10776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-96_0_5_line_16 |  | 9 | 16 | 0.011902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-96_0_5_line_17 |  | 10 | 19 | 0.038071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-96_0_5_line_18 |  | 11 | 17 | 0.028071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-96_0_5_line_19 |  | 12 | 20 | 0.013737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-96_0_5_line_20 |  | 13 | 14 | 0.059147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-96_0_5_line_21 |  | 13 | 15 | 0.019942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-96_0_5_line_22 |  | 13 | 16 | 0.011218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-96_0_5_line_23 |  | 15 | 17 | 0.01759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-96_0_5_line_24 |  | 15 | 18 | 0.014849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-96_0_5_line_25 |  | 18 | 22 | 0.029022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-96_0_5_line_26 |  | 18 | 23 | 0.026359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-96_0_5_line_27 |  | 20 | 21 | 0.02221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-96_0_5_line_28 |  | 21 | 28 | 0.00552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-96_0_5_line_29 |  | 23 | 43 | 3.2821e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-96_0_5_line_30 |  | 23 | 40 | 0.017883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-96_0_5_line_31 |  | 24 | 29 | 0.014011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-96_0_5_line_32 |  | 25 | 47 | 0.020156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-96_0_5_line_33 |  | 26 | 27 | 0.019645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-96_0_5_line_34 |  | 27 | 29 | 0.0068777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-96_0_5_line_35 |  | 30 | 31 | 0.069357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_261-96_0_5_line_36 |  | 31 | 59 | 0.045868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_261-96_0_5_line_37 |  | 32 | 34 | 0.022915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-96_0_5_line_38 |  | 33 | 35 | 0.031674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_261-96_0_5_line_39 |  | 34 | 36 | 0.0019486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-96_0_5_line_40 |  | 35 | 37 | 0.013545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_261-96_0_5_line_41 |  | 37 | 39 | 0.0009392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-96_0_5_line_42 |  | 38 | 66 | 0.022882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_261-96_0_5_line_43 |  | 39 | 40 | 0.042557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-96_0_5_line_44 |  | 40 | 41 | 0.028769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-96_0_5_line_45 |  | 41 | 42 | 0.020974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-96_0_5_line_46 |  | 42 | 46 | 0.028131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-96_0_5_line_47 |  | 43 | 44 | 0.014124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-96_0_5_line_48 |  | 44 | 45 | 0.031646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-96_0_5_line_49 |  | 46 | 48 | 0.007868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-96_0_5_line_50 |  | 47 | 130 | 0.021046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-96_0_5_line_51 |  | 47 | 128 | 0.037029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-96_0_5_line_52 |  | 49 | 50 | 0.019305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_261-96_0_5_line_53 |  | 49 | 51 | 0.022598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_261-96_0_5_line_54 |  | 50 | 52 | 0.0075821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_261-96_0_5_line_55 |  | 51 | 53 | 0.0089901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_261-96_0_5_line_56 |  | 52 | 54 | 0.020368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_261-96_0_5_line_57 |  | 52 | 55 | 0.0055335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-96_0_5_line_58 |  | 53 | 56 | 0.0082277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_261-96_0_5_line_59 |  | 53 | 57 | 0.018272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-96_0_5_line_60 |  | 54 | 58 | 0.001031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_261-96_0_5_line_61 |  | 56 | 59 | 0.0073779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_261-96_0_5_line_62 |  | 57 | 60 | 0.017934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-96_0_5_line_63 |  | 58 | 61 | 0.014274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_261-96_0_5_line_64 |  | 61 | 62 | 0.0089776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_261-96_0_5_line_65 |  | 62 | 63 | 0.024448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_261-96_0_5_line_66 |  | 63 | 64 | 0.0070949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_261-96_0_5_line_67 |  | 64 | 65 | 0.0011612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_261-96_0_5_line_68 |  | 65 | 82 | 0.0077469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_261-96_0_5_line_69 |  | 67 | 68 | 0.0072467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_261-96_0_5_line_70 |  | 67 | 69 | 0.0036134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_261-96_0_5_line_71 |  | 68 | 70 | 6.4093e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_261-96_0_5_line_72 |  | 69 | 71 | 0.016641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_261-96_0_5_line_73 |  | 70 | 72 | 0.01688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_261-96_0_5_line_74 |  | 71 | 73 | 0.012537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_261-96_0_5_line_75 |  | 72 | 74 | 0.0052592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_261-96_0_5_line_76 |  | 73 | 75 | 0.0057404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_261-96_0_5_line_77 |  | 74 | 76 | 0.0010189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_261-96_0_5_line_78 |  | 75 | 77 | 0.001866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_261-96_0_5_line_79 |  | 76 | 86 | 0.0048811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_261-96_0_5_line_80 |  | 77 | 85 | 0.049985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_261-96_0_5_line_81 |  | 78 | 79 | 0.014793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_261-96_0_5_line_82 |  | 78 | 80 | 0.014414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_261-96_0_5_line_83 |  | 79 | 81 | 0.0023255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_261-96_0_5_line_84 |  | 80 | 82 | 0.0075961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_261-96_0_5_line_85 |  | 81 | 83 | 0.011357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_261-96_0_5_line_86 |  | 83 | 84 | 0.011741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_261-96_0_5_line_87 |  | 84 | 85 | 0.024726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_261-96_0_5_line_88 |  | 86 | 87 | 0.01049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_261-96_0_5_line_89 |  | 87 | 88 | 0.0099538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_261-96_0_5_line_90 |  | 88 | 99 | 0.0019035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_261-96_0_5_line_91 |  | 89 | 90 | 0.031728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
92 | LV_261-96_0_5_line_92 |  | 89 | 91 | 0.015843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_261-96_0_5_line_93 |  | 91 | 92 | 0.038589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
94 | LV_261-96_0_5_line_94 |  | 92 | 96 | 0.01055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_261-96_0_5_line_95 |  | 93 | 94 | 0.003536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_261-96_0_5_line_96 |  | 93 | 95 | 0.015221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_261-96_0_5_line_97 |  | 94 | 97 | 0.035966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_261-96_0_5_line_98 |  | 94 | 98 | 0.021423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_261-96_0_5_line_99 |  | 95 | 99 | 0.011474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_261-96_0_5_line_100 |  | 96 | 100 | 0.029757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_261-96_0_5_line_101 |  | 96 | 101 | 0.032804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-96_0_5_line_102 |  | 97 | 102 | 8.1852e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_261-96_0_5_line_103 |  | 98 | 103 | 0.021849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_261-96_0_5_line_104 |  | 100 | 104 | 0.029298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_261-96_0_5_line_105 |  | 101 | 105 | 0.018312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-96_0_5_line_106 |  | 102 | 121 | 0.00033843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_261-96_0_5_line_107 |  | 103 | 110 | 0.019052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-96_0_5_line_108 |  | 103 | 104 | 0.015072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_261-96_0_5_line_109 |  | 106 | 107 | 0.027633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-96_0_5_line_110 |  | 106 | 108 | 0.017455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-96_0_5_line_111 |  | 107 | 109 | 0.0017974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-96_0_5_line_112 |  | 108 | 110 | 0.0095484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-96_0_5_line_113 |  | 109 | 111 | 0.013558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-96_0_5_line_114 |  | 112 | 113 | 0.016483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-96_0_5_line_115 |  | 113 | 114 | 0.029787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
116 | LV_261-96_0_5_line_116 |  | 114 | 115 | 0.0016254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_261-96_0_5_line_117 |  | 115 | 116 | 0.02628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_261-96_0_5_line_118 |  | 116 | 117 | 0.0068883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
119 | LV_261-96_0_5_line_119 |  | 117 | 118 | 0.00071043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_261-96_0_5_line_120 |  | 118 | 119 | 0.0011076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
121 | LV_261-96_0_5_line_121 |  | 119 | 120 | 0.022953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
122 | LV_261-96_0_5_line_122 |  | 120 | 121 | 8.1053e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_261-96_0_5_line_123 |  | 122 | 123 | 0.002157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-96_0_5_line_124 |  | 122 | 124 | 0.034112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-96_0_5_line_125 |  | 124 | 125 | 0.038588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-96_0_5_line_126 |  | 124 | 126 | 0.018937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-96_0_5_line_127 |  | 126 | 127 | 0.015378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-96_0_5_line_128 |  | 126 | 128 | 0.00601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-96_0_5_line_129 |  | 128 | 129 | 0.029212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-96_0_5_trafo_60 | 0.63 MVA 20/0.4 kV | 131 | 66 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2684835.5791 | 1244971.4224 | 2684834.149 | 1244973.753
1 | 2684845.9626 | 1244954.5002 | 2684835.5791 | 1244971.4224
2 | 2684850.0789 | 1244947.7875 | 2684845.9626 | 1244954.5002
3 | 2684850.0789 | 1244947.7875 | 2684855.1668 | 1244950.8069
4 | 2684850.0789 | 1244947.7875 | 2684844.3549 | 1244943.9407
5 | 2685013.6133 | 1245031.779 | 2685001.9432 | 1245050.3376
6 | 2684991.7141 | 1245074.1857 | 2684998.0116 | 1245059.5092 | 2685001.9432 | 1245050.3376
7 | 2685001.9432 | 1245050.3376 | 2684928.9779 | 1245029.2554
8 | 2685013.6133 | 1245031.779 | 2685034.3972 | 1245038.9488 | 2685043.1269 | 1245047.5791
9 | 2685024.1233 | 1245008.6905 | 2685013.6133 | 1245031.779
10 | 2684983.1999 | 1245094.0281 | 2684991.7141 | 1245074.1857
11 | 2685022.5601 | 1245081.4188 | 2684991.7141 | 1245074.1857
12 | 2684931.3551 | 1245016.7121 | 2684933.3527 | 1245021.8 | 2684928.9779 | 1245029.2554
13 | 2684926.397 | 1245033.6535 | 2684928.9779 | 1245029.2554
14 | 2684810.4227 | 1244978.2873 | 2684808.0369 | 1244980.2546 | 2684801.3886 | 1244988.5879 | 2684799.3027 | 1244992.3053
15 | 2684768.7256 | 1245045.3294 | 2684766.1721 | 1245041.5791 | 2684764.4803 | 1245038.8752 | 2684762.4067 | 1245035.3874 | 2684774.6541 | 1245015.4478 | 2684770.3732 | 1245007.2584 | 2684769.4298 | 1245005.5881 | 2684768.6046 | 1245004.1086 | 2684765.4679 | 1244999.9274 | 2684773.865 | 1244988.7169 | 2684783.438 | 1244987.7641 | 2684798.403 | 1244984.9426 | 2684800.5825 | 1244983.6617 | 2684802.4894 | 1244981.8988 | 2684806.9068 | 1244976.8471 | 2684810.4227 | 1244978.2873
16 | 2684799.3027 | 1244992.3053 | 2684803.2316 | 1244994.463 | 2684806.5934 | 1244989.7743 | 2684807.528 | 1244988.4148
17 | 2684768.7256 | 1245045.3294 | 2684772.6645 | 1245043.0841 | 2684779.9505 | 1245040.8754 | 2684788.4973 | 1245039.8079 | 2684798.5995 | 1245036.183 | 2684802.184 | 1245030.6675
18 | 2684855.1668 | 1244950.8069 | 2684852.6229 | 1244954.8402 | 2684840.2057 | 1244974.5585
19 | 2684832.9536 | 1244936.2786 | 2684844.3549 | 1244943.9407
20 | 2684813.7814 | 1244979.1026 | 2684810.1405 | 1244975.3033 | 2684787.4553 | 1244940.409 | 2684787.6237 | 1244938.1431 | 2684790.2795 | 1244935.2678 | 2684794.2895 | 1244930.6996
21 | 2684813.7814 | 1244979.1026 | 2684822.8765 | 1244984.6144 | 2684830.8327 | 1244989.4428
22 | 2684813.7814 | 1244979.1026 | 2684811.3473 | 1244982.8594 | 2684807.528 | 1244988.4148
23 | 2684830.8327 | 1244989.4428 | 2684840.2057 | 1244974.5585
24 | 2684843.5613 | 1244997.1527 | 2684830.8327 | 1244989.4428
25 | 2684843.5613 | 1244997.1527 | 2684851.4547 | 1244985.2457 | 2684859.3966 | 1244972.8323
26 | 2684843.5613 | 1244997.1527 | 2684868.164 | 1245006.8005
27 | 2684832.9536 | 1244936.2786 | 2684839.4632 | 1244922.3281 | 2684846.275 | 1244922.1143
28 | 2684846.275 | 1244922.1143 | 2684851.447 | 1244924.0432
29 | 2684868.1816 | 1245006.7729 | 2684868.164 | 1245006.8005
30 | 2684857.6871 | 1245020.2272 | 2684859.9109 | 1245016.9121 | 2684861.7839 | 1245016.9834 | 2684868.164 | 1245006.8005
31 | 2684981.6672 | 1245107.955 | 2684983.1999 | 1245094.0281
32 | 2685040.1342 | 1245091.0026 | 2685037.7912 | 1245088.923 | 2685030.3573 | 1245084.5799 | 2685022.5601 | 1245081.4188
33 | 2684967.9243 | 1245129.435 | 2684975.7154 | 1245111.4015
34 | 2684981.6672 | 1245107.955 | 2684975.7154 | 1245111.4015
35 | 2685024.1233 | 1245008.6905 | 2685028.1954 | 1245010.3389 | 2685059.1345 | 1245022.8583 | 2685069.1136 | 1245028.8835 | 2685078.5656 | 1245033.7226 | 2685085.2654 | 1245034.9863 | 2685087.491 | 1245036.1126
36 | 2685115.7802 | 1245014.4849 | 2685099.7597 | 1245042.3218 | 2685087.491 | 1245036.1126
37 | 2684931.3551 | 1245016.7121 | 2684931.3551 | 1245016.7121 | 2684934.3809 | 1245010.6954 | 2684939.1906 | 1244999.8897 | 2684940.9616 | 1244995.9141
38 | 2684926.397 | 1245033.6535 | 2684918.7743 | 1245028.7631 | 2684906.3374 | 1245047.6545
39 | 2684940.9616 | 1244995.9141 | 2684941.7545 | 1244994.1341
40 | 2684906.3374 | 1245047.6545 | 2684906.3374 | 1245047.6545 | 2684894.8527 | 1245040.4731
41 | 2684894.0564 | 1245039.9752 | 2684894.8527 | 1245040.4731
42 | 2685059.3468 | 1245046.1776 | 2685050.5808 | 1245054.9481 | 2685043.1269 | 1245047.5791
43 | 2684857.6871 | 1245020.2272 | 2684879.921 | 1245033.8108 | 2684884.8277 | 1245036.8054 | 2684887.119 | 1245035.6373 | 2684894.0564 | 1245039.9752
44 | 2684857.6871 | 1245020.2272 | 2684842.1125 | 1245044.4162
45 | 2684830.8658 | 1245062.1188 | 2684833.752 | 1245057.4011 | 2684842.1125 | 1245044.4162
46 | 2684854.3865 | 1245077.6555 | 2684852.0809 | 1245076.1325 | 2684830.8658 | 1245062.1188
47 | 2684872.5264 | 1244994.5095 | 2684873.7917 | 1244997.9746 | 2684868.1816 | 1245006.7729
48 | 2684872.5264 | 1244994.5095 | 2684877.6812 | 1244989.6797 | 2684890.6301 | 1244968.7844
49 | 2684854.3865 | 1245077.6555 | 2684860.9744 | 1245081.9862
50 | 2685029.7925 | 1245106.0432 | 2685032.3135 | 1245106.7798 | 2685034.3029 | 1245106.1079 | 2685035.9495 | 1245104.0522 | 2685040.1342 | 1245091.0026
51 | 2685040.1342 | 1245091.0026 | 2685043.4922 | 1245093.964 | 2685048.2258 | 1245099.5359 | 2685063.534 | 1245119.6591
52 | 2685142.1245 | 1244983.7828 | 2685148.3327 | 1244972.4452 | 2685154.0485 | 1244969.614
53 | 2685142.1245 | 1244983.7828 | 2685131.2709 | 1245003.604
54 | 2685161.6 | 1244968.933 | 2685154.0485 | 1244969.614
55 | 2685126.9531 | 1245011.4893 | 2685131.2709 | 1245003.604
56 | 2685161.6 | 1244968.933 | 2685171.4305 | 1244951.0948
57 | 2685161.6 | 1244968.933 | 2685159.1184 | 1244973.8788
58 | 2685126.9531 | 1245011.4893 | 2685119.4603 | 1245008.0904
59 | 2685126.9531 | 1245011.4893 | 2685125.7971 | 1245015.6869 | 2685123.0347 | 1245017.5597 | 2685120.8591 | 1245020.6641 | 2685120.2557 | 1245027.4271
60 | 2685171.9281 | 1244950.1919 | 2685171.4305 | 1244951.0948
61 | 2685119.4603 | 1245008.0904 | 2685115.7802 | 1245014.4849
62 | 2685110.7196 | 1245042.1344 | 2685116.3765 | 1245036.5559 | 2685118.7629 | 1245032.4538 | 2685120.2557 | 1245027.4271
63 | 2685178.8174 | 1244937.6906 | 2685171.9281 | 1244950.1919
64 | 2685178.8174 | 1244937.6906 | 2685186.79 | 1244941.818
65 | 2685186.79 | 1244941.818 | 2685208.5007 | 1244953.0578
66 | 2685214.8013 | 1244956.3197 | 2685208.5007 | 1244953.0578
67 | 2685214.8013 | 1244956.3197 | 2685215.8325 | 1244956.8535
68 | 2685215.8325 | 1244956.8535 | 2685222.7121 | 1244960.4151
69 | 2685257.3876 | 1245079.5823 | 2685253.9587 | 1245085.9664
70 | 2685257.3876 | 1245079.5823 | 2685259.0973 | 1245076.399
71 | 2685253.9587 | 1245085.9664 | 2685253.9284 | 1245086.0229
72 | 2685266.9713 | 1245061.7386 | 2685259.0973 | 1245076.399
73 | 2685245.9414 | 1245100.8938 | 2685253.9284 | 1245086.0229
74 | 2685266.9713 | 1245061.7386 | 2685272.9033 | 1245050.6939
75 | 2685245.9414 | 1245100.8938 | 2685243.4529 | 1245105.5271
76 | 2685275.6194 | 1245045.6368 | 2685272.9033 | 1245050.6939
77 | 2685242.9708 | 1245106.4247 | 2685243.4529 | 1245105.5271
78 | 2685275.6194 | 1245045.6368 | 2685276.5024 | 1245043.9929
79 | 2685242.9708 | 1245106.4247 | 2685240.6612 | 1245110.7248
80 | 2685300.1535 | 1244999.9573 | 2685276.5024 | 1245043.9929
81 | 2685242.2588 | 1244970.5321 | 2685255.4464 | 1244977.2347
82 | 2685242.2588 | 1244970.5321 | 2685241.9985 | 1244970.3998 | 2685229.4578 | 1244963.9074
83 | 2685255.4464 | 1244977.2347 | 2685257.5195 | 1244978.2884
84 | 2685222.7121 | 1244960.4151 | 2685229.4578 | 1244963.9074
85 | 2685267.6441 | 1244983.4343 | 2685257.5195 | 1244978.2884
86 | 2685267.6441 | 1244983.4343 | 2685278.1111 | 1244988.7542
87 | 2685300.1535 | 1244999.9573 | 2685278.1111 | 1244988.7542
88 | 2685235.6979 | 1245119.966 | 2685240.6612 | 1245110.7248
89 | 2685230.9881 | 1245128.735 | 2685235.6979 | 1245119.966
90 | 2685230.0874 | 1245130.412 | 2685230.9881 | 1245128.735
91 | 2685309.1327 | 1245136.5088 | 2685278.2363 | 1245143.7242
92 | 2685324.5603 | 1245132.906 | 2685309.1327 | 1245136.5088
93 | 2685324.5603 | 1245132.906 | 2685327.3637 | 1245149.7142 | 2685319.6236 | 1245165.0919 | 2685320.204 | 1245169.3923
94 | 2685320.204 | 1245169.3923 | 2685311.2031 | 1245170.5193 | 2685309.8836 | 1245171.1864
95 | 2685221.5867 | 1245156.5544 | 2685225.0366 | 1245155.7367
96 | 2685225.0366 | 1245155.7367 | 2685224.6584 | 1245140.5201
97 | 2685221.5867 | 1245156.5544 | 2685216.9252 | 1245158.5889 | 2685214.9356 | 1245159.7946 | 2685212.8828 | 1245161.7221 | 2685206.2118 | 1245173.1902 | 2685200.6296 | 1245180.4042 | 2685198.5351 | 1245183.0173
98 | 2685221.5867 | 1245156.5544 | 2685230.7923 | 1245175.8991
99 | 2685230.0874 | 1245130.412 | 2685224.6584 | 1245140.5201 | 2685224.6584 | 1245140.5201
100 | 2685282.7625 | 1245183.2719 | 2685292.7061 | 1245179.8713 | 2685309.8836 | 1245171.1864
101 | 2685309.8836 | 1245171.1864 | 2685316.1593 | 1245203.3844
102 | 2685198.5351 | 1245183.0173 | 2685198.4839 | 1245183.0812
103 | 2685240.1807 | 1245195.628 | 2685230.7923 | 1245175.8991
104 | 2685282.7625 | 1245183.2719 | 2685266.0288 | 1245188.9946 | 2685254.78 | 1245191.8814
105 | 2685316.1593 | 1245203.3844 | 2685300.4611 | 1245212.8125
106 | 2685198.4839 | 1245183.0812 | 2685198.2723 | 1245183.3453
107 | 2685240.1807 | 1245195.628 | 2685248.7188 | 1245212.66
108 | 2685240.1807 | 1245195.628 | 2685254.78 | 1245191.8814
109 | 2685264.1636 | 1245234.6124 | 2685243.2961 | 1245252.7261
110 | 2685252.9978 | 1245221.1958 | 2685264.1636 | 1245234.6124
111 | 2685241.9388 | 1245253.9043 | 2685243.2961 | 1245252.7261
112 | 2685252.9978 | 1245221.1958 | 2685248.7188 | 1245212.66
113 | 2685231.7002 | 1245262.7918 | 2685241.9388 | 1245253.9043
114 | 2685121.1107 | 1245254.97 | 2685134.7585 | 1245245.7267
115 | 2685134.7585 | 1245245.7267 | 2685138.4209 | 1245243.2462 | 2685153.3427 | 1245231.8298 | 2685158.1506 | 1245227.3434
116 | 2685159.3389 | 1245226.2345 | 2685158.1506 | 1245227.3434
117 | 2685177.9368 | 1245207.7051 | 2685172.3225 | 1245214.0892 | 2685163.9046 | 1245221.9742 | 2685159.3389 | 1245226.2345
118 | 2685182.4857 | 1245202.5325 | 2685177.9368 | 1245207.7051
119 | 2685182.9548 | 1245201.999 | 2685182.4857 | 1245202.5325
120 | 2685182.9548 | 1245201.999 | 2685183.6863 | 1245201.1673
121 | 2685183.6863 | 1245201.1673 | 2685187.0873 | 1245197.3 | 2685198.2216 | 1245183.4085
122 | 2685198.2723 | 1245183.3453 | 2685198.2216 | 1245183.4085
123 | 2685099.8532 | 1245124.7726 | 2685101.2503 | 1245126.416
124 | 2685076.4606 | 1245140.9156 | 2685079.6104 | 1245141.0053 | 2685090.95 | 1245141.724 | 2685093.5894 | 1245141.0502 | 2685094.9743 | 1245139.8581 | 2685101.2763 | 1245128.2844 | 2685101.2503 | 1245126.416
125 | 2685076.4606 | 1245140.9156 | 2685078.3806 | 1245145.0795 | 2685082.691 | 1245155.3933 | 2685083.4076 | 1245158.6393 | 2685082.7076 | 1245161.6092 | 2685075.2442 | 1245173.0217 | 2685073.9253 | 1245173.303 | 2685072.7212 | 1245172.4295
126 | 2685067.1756 | 1245124.4481 | 2685069.3189 | 1245127.2698 | 2685075.3396 | 1245138.4644 | 2685076.4606 | 1245140.9156
127 | 2685057.801 | 1245135.2883 | 2685058.9602 | 1245135.6052 | 2685061.1081 | 1245134.424 | 2685063.53 | 1245131.5233 | 2685065.2988 | 1245128.3241 | 2685067.1756 | 1245124.4481
128 | 2685063.534 | 1245119.6591 | 2685067.1756 | 1245124.4481
129 | 2685074.6987 | 1245094.6563 | 2685075.753 | 1245095.4387 | 2685076.4372 | 1245097.261 | 2685073.7033 | 1245103.9934 | 2685068.8672 | 1245112.408 | 2685063.534 | 1245119.6591

## bus_geodata
| x | y | coords
0 | 2684835.5791 | 1244971.4224
1 | 2684834.149 | 1244973.753
2 | 2684845.9626 | 1244954.5002
3 | 2684850.0789 | 1244947.7875
4 | 2685001.9432 | 1245050.3376
5 | 2685013.6133 | 1245031.779
6 | 2684991.7141 | 1245074.1857
7 | 2684928.9779 | 1245029.2554
8 | 2684810.4227 | 1244978.2873
9 | 2684799.3027 | 1244992.3053
10 | 2684768.7256 | 1245045.3294
11 | 2684855.1668 | 1244950.8069
12 | 2684844.3549 | 1244943.9407
13 | 2684813.7814 | 1244979.1026
14 | 2684794.2895 | 1244930.6996
15 | 2684830.8327 | 1244989.4428
16 | 2684807.528 | 1244988.4148
17 | 2684840.2057 | 1244974.5585
18 | 2684843.5613 | 1244997.1527
19 | 2684802.184 | 1245030.6675
20 | 2684832.9536 | 1244936.2786
21 | 2684846.275 | 1244922.1143
22 | 2684859.3966 | 1244972.8323
23 | 2684868.164 | 1245006.8005
24 | 2684983.1999 | 1245094.0281
25 | 2685022.5601 | 1245081.4188
26 | 2684967.9243 | 1245129.435
27 | 2684975.7154 | 1245111.4015
28 | 2684851.447 | 1244924.0432
29 | 2684981.6672 | 1245107.955
30 | 2685024.1233 | 1245008.6905
31 | 2685087.491 | 1245036.1126
32 | 2684931.3551 | 1245016.7121
33 | 2684926.397 | 1245033.6535
34 | 2684940.9616 | 1244995.9141
35 | 2684906.3375 | 1245047.6545
36 | 2684941.7545 | 1244994.1341
37 | 2684894.8527 | 1245040.4731
38 | 2685043.1269 | 1245047.5791
39 | 2684894.0564 | 1245039.9752
40 | 2684857.6871 | 1245020.2272
41 | 2684842.1125 | 1245044.4162
42 | 2684830.8658 | 1245062.1188
43 | 2684868.1816 | 1245006.7729
44 | 2684872.5264 | 1244994.5095
45 | 2684890.6301 | 1244968.7844
46 | 2684854.3865 | 1245077.6555
47 | 2685040.1342 | 1245091.0026
48 | 2684860.9744 | 1245081.9862
49 | 2685142.1245 | 1244983.7828
50 | 2685154.0485 | 1244969.614
51 | 2685131.2709 | 1245003.604
52 | 2685161.6 | 1244968.933
53 | 2685126.9531 | 1245011.4893
54 | 2685171.4305 | 1244951.0948
55 | 2685159.1184 | 1244973.8788
56 | 2685119.4603 | 1245008.0904
57 | 2685120.2557 | 1245027.4271
58 | 2685171.9281 | 1244950.1919
59 | 2685115.7802 | 1245014.4849
60 | 2685110.7196 | 1245042.1344
61 | 2685178.8174 | 1244937.6906
62 | 2685186.79 | 1244941.818
63 | 2685208.5007 | 1244953.0578
64 | 2685214.8013 | 1244956.3197
65 | 2685215.8325 | 1244956.8535
66 | 2685059.3468 | 1245046.1776
67 | 2685257.3876 | 1245079.5823
68 | 2685253.9587 | 1245085.9665
69 | 2685259.0973 | 1245076.399
70 | 2685253.9284 | 1245086.0229
71 | 2685266.9713 | 1245061.7386
72 | 2685245.9414 | 1245100.8938
73 | 2685272.9033 | 1245050.6939
74 | 2685243.4529 | 1245105.5271
75 | 2685275.6194 | 1245045.6368
76 | 2685242.9708 | 1245106.4247
77 | 2685276.5024 | 1245043.9929
78 | 2685242.2588 | 1244970.5321
79 | 2685255.4464 | 1244977.2347
80 | 2685229.4578 | 1244963.9074
81 | 2685257.5195 | 1244978.2884
82 | 2685222.7121 | 1244960.4151
83 | 2685267.6441 | 1244983.4343
84 | 2685278.1111 | 1244988.7542
85 | 2685300.1535 | 1244999.9573
86 | 2685240.6612 | 1245110.7248
87 | 2685235.6979 | 1245119.966
88 | 2685230.9881 | 1245128.735
89 | 2685309.1327 | 1245136.5088
90 | 2685278.2363 | 1245143.7242
91 | 2685324.5603 | 1245132.906
92 | 2685320.204 | 1245169.3923
93 | 2685225.0366 | 1245155.7367
94 | 2685221.5867 | 1245156.5544
95 | 2685224.6584 | 1245140.5201
96 | 2685309.8836 | 1245171.1864
97 | 2685198.5351 | 1245183.0173
98 | 2685230.7923 | 1245175.8991
99 | 2685230.0874 | 1245130.412
100 | 2685282.7625 | 1245183.2719
101 | 2685316.1593 | 1245203.3844
102 | 2685198.4839 | 1245183.0812
103 | 2685240.1807 | 1245195.628
104 | 2685254.78 | 1245191.8814
105 | 2685300.4611 | 1245212.8125
106 | 2685264.1636 | 1245234.6124
107 | 2685243.2961 | 1245252.7261
108 | 2685252.9978 | 1245221.1958
109 | 2685241.9388 | 1245253.9043
110 | 2685248.7188 | 1245212.66
111 | 2685231.7002 | 1245262.7918
112 | 2685121.1107 | 1245254.97
113 | 2685134.7585 | 1245245.7267
114 | 2685158.1506 | 1245227.3434
115 | 2685159.3389 | 1245226.2345
116 | 2685177.9368 | 1245207.7051
117 | 2685182.4857 | 1245202.5325
118 | 2685182.9548 | 1245201.999
119 | 2685183.6863 | 1245201.1673
120 | 2685198.2216 | 1245183.4085
121 | 2685198.2723 | 1245183.3453
122 | 2685101.2503 | 1245126.416
123 | 2685099.8532 | 1245124.7725
124 | 2685076.4606 | 1245140.9156
125 | 2685072.7212 | 1245172.4295
126 | 2685067.1756 | 1245124.4481
127 | 2685057.801 | 1245135.2883
128 | 2685063.534 | 1245119.6591
129 | 2685074.6987 | 1245094.6563
130 | 2685029.7925 | 1245106.0432
131 | 2685059.6966 | 1245045.8276

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98039 | -0.3771 | 0.0018538 | 0.0004646
1 | 0.98039 | -0.37718 | 0.0016755 | 0.00041993
2 | 0.98045 | -0.37583 | 0 | 0
3 | 0.98048 | -0.37533 | 0 | 0
4 | 0.9928 | -0.1367 | 0.0057563 | 0.0014427
5 | 0.99387 | -0.11612 | 0 | 0
6 | 0.99123 | -0.16701 | 0.0057458 | 0.00144
7 | 0.99008 | -0.18897 | 0.0083234 | 0.002086
8 | 0.97934 | -0.39762 | 0 | 0
9 | 0.97974 | -0.3898 | 0 | 0
10 | 0.97694 | -0.44456 | 0 | 0
11 | 0.98051 | -0.37483 | 0 | 0
12 | 0.98047 | -0.37547 | 0.00071422 | 0.000179
13 | 0.98026 | -0.37951 | 0 | 0
14 | 0.98022 | -0.38034 | 0.00077875 | 0.00019517
15 | 0.98074 | -0.37013 | 0 | 0
16 | 0.98 | -0.38463 | 0.0012475 | 0.00031265
17 | 0.98063 | -0.37247 | 0.0026919 | 0.00067465
18 | 0.9812 | -0.36117 | 0 | 0
19 | 0.9761 | -0.4612 | 0.023912 | 0.005993
20 | 0.98047 | -0.37557 | 0 | 0
21 | 0.98046 | -0.37573 | 0 | 0
22 | 0.98106 | -0.36402 | 0.0054205 | 0.0013585
23 | 0.98215 | -0.34272 | 0 | 0
24 | 0.99103 | -0.17077 | 0.0037664 | 0.00094395
25 | 0.98976 | -0.19538 | 0.0023744 | 0.00059509
26 | 0.99085 | -0.1742 | 0.0034247 | 0.00085831
27 | 0.99092 | -0.17301 | 0.0026122 | 0.00065468
28 | 0.98046 | -0.37577 | 0.0003991 | 0.00010003
29 | 0.99095 | -0.17227 | 0 | 0
30 | 0.99239 | -0.14414 | 0 | 0
31 | 0.98836 | -0.2212 | 0.0056133 | 0.0014068
32 | 0.98972 | -0.19588 | 0.0080118 | 0.0020079
33 | 0.98993 | -0.19184 | 0 | 0
34 | 0.98931 | -0.20384 | 0.0073165 | 0.0018337
35 | 0.989 | -0.20969 | 0.0060084 | 0.0015058
36 | 0.98929 | -0.20426 | 0.012187 | 0.0030544
37 | 0.98805 | -0.22807 | 0.02276 | 0.0057042
38 | 0.99754 | -0.046434 | 0.0022643 | 0.00056749
39 | 0.98794 | -0.23025 | 0.01655 | 0.0041478
40 | 0.9835 | -0.31643 | 0 | 0
41 | 0.98266 | -0.33274 | 0.021012 | 0.005266
42 | 0.98246 | -0.33668 | 0 | 0
43 | 0.98215 | -0.34275 | 0.02804 | 0.0070274
44 | 0.98196 | -0.3465 | 0 | 0
45 | 0.98153 | -0.35493 | 0.014721 | 0.0036894
46 | 0.98219 | -0.34197 | 0 | 0
47 | 0.98887 | -0.21262 | 0 | 0
48 | 0.98212 | -0.34345 | 0.010413 | 0.0026097
49 | 0.98329 | -0.31905 | 0.0094948 | 0.0023796
50 | 0.98236 | -0.33715 | 0.002906 | 0.00072831
51 | 0.98442 | -0.29713 | 0.0067903 | 0.0017018
52 | 0.98199 | -0.34419 | 0 | 0
53 | 0.98488 | -0.28821 | 0 | 0
54 | 0.98109 | -0.36179 | 0.0034483 | 0.00086422
55 | 0.9819 | -0.34601 | 0.01813 | 0.0045439
56 | 0.98533 | -0.27955 | 0.0080447 | 0.0020162
57 | 0.98461 | -0.29366 | 0.0067457 | 0.0016906
58 | 0.98104 | -0.36267 | 0.0044689 | 0.00112
59 | 0.98575 | -0.27159 | 0.0062177 | 0.0015583
60 | 0.98444 | -0.29684 | 0.0098644 | 0.0024722
61 | 0.98043 | -0.37462 | 0 | 0
62 | 0.98004 | -0.38214 | 0.0069621 | 0.0017449
63 | 0.97902 | -0.40202 | 0.0065916 | 0.001652
64 | 0.97874 | -0.40763 | 0.013256 | 0.0033222
65 | 0.97869 | -0.4085 | 0.0060388 | 0.0015135
66 | 1 | 0 | -0.59274 | -0.15218
67 | 0.97314 | -0.51746 | 0.0034453 | 0.00086348
68 | 0.97297 | -0.52078 | 0.0013901 | 0.00034838
69 | 0.97323 | -0.51575 | 0.0082575 | 0.0020695
70 | 0.97297 | -0.52081 | 0.0013418 | 0.00033629
71 | 0.97365 | -0.50739 | 0.0075344 | 0.0018883
72 | 0.97258 | -0.5284 | 0.0012683 | 0.00031788
73 | 0.97399 | -0.50075 | 0.0014875 | 0.00037279
74 | 0.97247 | -0.53075 | 0.0019731 | 0.0004945
75 | 0.97414 | -0.49769 | 0.0078503 | 0.0019675
76 | 0.97244 | -0.53119 | 0.0044689 | 0.00112
77 | 0.9742 | -0.49663 | 0.0013775 | 0.00034524
78 | 0.97762 | -0.4294 | 0.011276 | 0.0028261
79 | 0.97713 | -0.43901 | 0.0092562 | 0.0023198
80 | 0.97813 | -0.41945 | 0.0048359 | 0.001212
81 | 0.97706 | -0.44044 | 0.0018068 | 0.00045284
82 | 0.97841 | -0.41408 | 0.0038939 | 0.00097591
83 | 0.9767 | -0.44737 | 0.0064465 | 0.0016156
84 | 0.97635 | -0.45426 | 0.0057328 | 0.0014368
85 | 0.97564 | -0.46826 | 0 | 0
86 | 0.97234 | -0.53325 | 0.001943 | 0.00048697
87 | 0.97212 | -0.5376 | 0.0037462 | 0.00093888
88 | 0.97192 | -0.54159 | 0.0027325 | 0.00068482
89 | 0.97037 | -0.57216 | 0.0073397 | 0.0018395
90 | 0.97026 | -0.57436 | 0.0074848 | 0.0018759
91 | 0.97042 | -0.57129 | 0 | 0
92 | 0.97052 | -0.56917 | 0 | 0
93 | 0.97139 | -0.55192 | 0 | 0
94 | 0.97133 | -0.55316 | 0 | 0
95 | 0.97166 | -0.54658 | 0.0053351 | 0.0013371
96 | 0.97055 | -0.56859 | 0.0053373 | 0.0013376
97 | 0.97102 | -0.55933 | 0.0025905 | 0.00064924
98 | 0.97114 | -0.557 | 0.004044 | 0.0010135
99 | 0.97188 | -0.54233 | 0.0056474 | 0.0014154
100 | 0.97067 | -0.56618 | 0.0090627 | 0.0022713
101 | 0.9705 | -0.56964 | 0.0010631 | 0.00026645
102 | 0.97102 | -0.55934 | 0.0025701 | 0.00064412
103 | 0.97096 | -0.56059 | 0.00049709 | 0.00012458
104 | 0.97084 | -0.56282 | 0.0090627 | 0.0022713
105 | 0.97049 | -0.56986 | 0.00066025 | 0.00016548
106 | 0.97082 | -0.56326 | 0 | 0
107 | 0.97076 | -0.56439 | 0.00067401 | 0.00016892
108 | 0.97086 | -0.56254 | 0.00093647 | 0.0002347
109 | 0.97076 | -0.56444 | 0.00062413 | 0.00015642
110 | 0.97089 | -0.56198 | 0.0007789 | 0.00019521
111 | 0.97075 | -0.56468 | 0.00092528 | 0.0002319
112 | 0.97043 | -0.57104 | 0.0034328 | 0.00086035
113 | 0.97048 | -0.56999 | 0.012327 | 0.0030894
114 | 0.9707 | -0.56565 | 0.0038829 | 0.00097314
115 | 0.97071 | -0.56553 | 0.0031119 | 0.00077991
116 | 0.97082 | -0.56332 | 0.0020103 | 0.00050383
117 | 0.97085 | -0.56269 | 0.0068934 | 0.0017277
118 | 0.97085 | -0.56261 | 0.0024389 | 0.00061124
119 | 0.97086 | -0.56247 | 0.0019788 | 0.00049594
120 | 0.97102 | -0.5594 | 0.0025724 | 0.0006447
121 | 0.97102 | -0.55939 | 0.0025896 | 0.00064902
122 | 0.98638 | -0.26102 | 0.0041616 | 0.001043
123 | 0.98636 | -0.26145 | 0.011003 | 0.0027577
124 | 0.98686 | -0.25176 | 0 | 0
125 | 0.98648 | -0.25916 | 0.010711 | 0.0026845
126 | 0.98731 | -0.24299 | 0 | 0
127 | 0.9872 | -0.24497 | 0.0071809 | 0.0017997
128 | 0.98749 | -0.23944 | 0 | 0
129 | 0.98729 | -0.24336 | 0.0075146 | 0.0018833
130 | 0.98873 | -0.21542 | 0.007447 | 0.0018664
131 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0016755 | 0.0004199 | -0.0016755 | -0.00041993 | 6.6317e-09 | -3.0236e-08 | 0.0025431 | 0.0025431 | 0.0025431 | 0.98039 | -0.3771 | 0.98039 | -0.37718 | 0.69865
1 | -0.0035293 | -0.0008845 | 0.0035295 | 0.00088439 | 2.1363e-07 | -1.1364e-07 | 0.0053567 | 0.0053567 | 0.0053567 | 0.98039 | -0.3771 | 0.98045 | -0.37583 | 1.4716
2 | -0.0035295 | -0.00088439 | 0.0035296 | 0.00088434 | 8.4671e-08 | -4.5053e-08 | 0.0053567 | 0.0053566 | 0.0053567 | 0.98045 | -0.37583 | 0.98048 | -0.37533 | 1.4716
3 | -0.004643 | -0.0011628 | 0.0046431 | 0.0011628 | 1.099e-07 | -4.1157e-09 | 0.0070461 | 0.007046 | 0.0070461 | 0.98048 | -0.37533 | 0.98051 | -0.37483 | 1.9357
4 | 0.0011133 | 0.00027842 | -0.0011133 | -0.00027851 | 7.3817e-09 | -8.2255e-08 | 0.0016894 | 0.0016895 | 0.0016895 | 0.98048 | -0.37533 | 0.98047 | -0.37547 | 0.46414
5 | -0.2676 | -0.067774 | 0.26787 | 0.067942 | 0.00026484 | 0.00016808 | 0.40134 | 0.40134 | 0.40134 | 0.9928 | -0.1367 | 0.99387 | -0.11612 | 22.0515
6 | 0.066231 | 0.016707 | -0.066135 | -0.016646 | 9.5965e-05 | 6.1083e-05 | 0.099307 | 0.099307 | 0.099307 | 0.9928 | -0.1367 | 0.99123 | -0.16701 | 27.282
7 | 0.19562 | 0.049624 | -0.19513 | -0.049315 | 0.00049037 | 0.00030894 | 0.2934 | 0.29341 | 0.29341 | 0.9928 | -0.1367 | 0.99008 | -0.18897 | 16.1212
8 | -0.58552 | -0.1495 | 0.5875 | 0.15076 | 0.0019791 | 0.0012644 | 0.87762 | 0.87762 | 0.87762 | 0.99387 | -0.11612 | 0.99754 | -0.046434 | 48.2208
9 | 0.31765 | 0.081556 | -0.31722 | -0.081282 | 0.00043144 | 0.00027448 | 0.47628 | 0.47628 | 0.47628 | 0.99387 | -0.11612 | 0.99239 | -0.14414 | 26.1693
10 | 0.0098059 | 0.0024578 | -0.0098041 | -0.0024569 | 1.7546e-06 | 8.4466e-07 | 0.014721 | 0.014721 | 0.014721 | 0.99123 | -0.16701 | 0.99103 | -0.17077 | 4.0441
11 | 0.050584 | 0.012748 | -0.050515 | -0.012705 | 6.8554e-05 | 4.3467e-05 | 0.075961 | 0.075961 | 0.075961 | 0.99123 | -0.16701 | 0.98976 | -0.19538 | 20.8683
12 | 0.027532 | 0.0069062 | -0.027523 | -0.0069006 | 9.0609e-06 | 5.6176e-06 | 0.041381 | 0.041381 | 0.041381 | 0.99008 | -0.18897 | 0.98972 | -0.19588 | 11.3685
13 | 0.15927 | 0.040323 | -0.15925 | -0.040309 | 2.1941e-05 | 1.3714e-05 | 0.23952 | 0.23952 | 0.23952 | 0.99008 | -0.18897 | 0.98993 | -0.19184 | 13.1602
14 | -0.023985 | -0.0060377 | 0.023994 | 0.0060432 | 8.9674e-06 | 5.5126e-06 | 0.036453 | 0.036453 | 0.036453 | 0.97934 | -0.39762 | 0.97974 | -0.3898 | 10.0145
15 | 0.023985 | 0.0060377 | -0.023931 | -0.0060047 | 5.3695e-05 | 3.3012e-05 | 0.036453 | 0.036453 | 0.036453 | 0.97934 | -0.39762 | 0.97694 | -0.44456 | 10.0146
16 | -0.023994 | -0.0060432 | 0.024 | 0.0060469 | 5.9305e-06 | 3.6456e-06 | 0.036453 | 0.036453 | 0.036453 | 0.97974 | -0.3898 | 0.98 | -0.38463 | 10.0144
17 | 0.023931 | 0.0060047 | -0.023912 | -0.005993 | 1.8972e-05 | 1.1665e-05 | 0.036453 | 0.036453 | 0.036453 | 0.97694 | -0.44456 | 0.9761 | -0.4612 | 10.0146
18 | -0.0046431 | -0.0011628 | 0.0046436 | 0.0011627 | 5.226e-07 | -1.9632e-08 | 0.007046 | 0.0070459 | 0.007046 | 0.98051 | -0.37483 | 0.98063 | -0.37247 | 1.9357
19 | 0.00039911 | 9.9506e-05 | -0.00039911 | -9.9678e-05 | 1.889e-09 | -1.7204e-07 | 0.00060552 | 0.00060559 | 0.00060559 | 0.98047 | -0.37547 | 0.98047 | -0.37557 | 0.16637
20 | 0.00077878 | 0.00019445 | -0.00077875 | -0.00019517 | 3.0991e-08 | -7.2578e-07 | 0.0011819 | 0.0011822 | 0.0011822 | 0.98026 | -0.37951 | 0.98022 | -0.38034 | 0.32477
21 | -0.026032 | -0.0065578 | 0.026044 | 0.006565 | 1.1685e-05 | 7.2266e-06 | 0.039529 | 0.039528 | 0.039529 | 0.98026 | -0.37951 | 0.98074 | -0.37013 | 10.8595
22 | 0.025254 | 0.0063633 | -0.025247 | -0.0063595 | 6.1859e-06 | 3.8176e-06 | 0.038347 | 0.038347 | 0.038347 | 0.98026 | -0.37951 | 0.98 | -0.38463 | 10.5348
23 | 0.0073363 | 0.0018377 | -0.0073355 | -0.0018374 | 8.172e-07 | 3.0107e-07 | 0.011131 | 0.011131 | 0.011131 | 0.98074 | -0.37013 | 0.98063 | -0.37247 | 3.0579
24 | -0.03338 | -0.0084027 | 0.033395 | 0.0084116 | 1.429e-05 | 8.9583e-06 | 0.050659 | 0.050659 | 0.050659 | 0.98074 | -0.37013 | 0.9812 | -0.36117 | 13.9173
25 | 0.0054212 | 0.0013586 | -0.0054205 | -0.0013585 | 7.3563e-07 | 1.0428e-07 | 0.0082214 | 0.0082215 | 0.0082215 | 0.9812 | -0.36117 | 0.98106 | -0.36402 | 2.2587
26 | -0.038816 | -0.0097703 | 0.03885 | 0.0097919 | 3.4269e-05 | 2.1599e-05 | 0.05888 | 0.05888 | 0.05888 | 0.9812 | -0.36117 | 0.98215 | -0.34272 | 16.1759
27 | 0.00039911 | 9.9678e-05 | -0.00039911 | -9.9956e-05 | 3.0549e-09 | -2.7815e-07 | 0.00060559 | 0.00060569 | 0.00060569 | 0.98047 | -0.37557 | 0.98046 | -0.37573 | 0.1664
28 | 0.00039911 | 9.9956e-05 | -0.0003991 | -0.00010003 | 7.5942e-10 | -6.913e-08 | 0.00060569 | 0.00060571 | 0.00060571 | 0.98046 | -0.37573 | 0.98046 | -0.37577 | 0.1664
29 | 0.042769 | 0.010722 | -0.042769 | -0.010722 | 5.1681e-08 | 3.266e-08 | 0.064799 | 0.064799 | 0.064799 | 0.98215 | -0.34272 | 0.98215 | -0.34275 | 17.8019
30 | -0.081619 | -0.020514 | 0.081722 | 0.020579 | 0.00010258 | 6.5424e-05 | 0.12368 | 0.12368 | 0.12368 | 0.98215 | -0.34272 | 0.9835 | -0.31643 | 33.9777
31 | 0.0060377 | 0.001513 | -0.0060373 | -0.0015129 | 4.318e-07 | 9.5835e-08 | 0.0090655 | 0.0090655 | 0.0090655 | 0.99103 | -0.17077 | 0.99095 | -0.17227 | 2.4905
32 | 0.048141 | 0.01211 | -0.048101 | -0.012085 | 3.961e-05 | 2.5091e-05 | 0.072391 | 0.072391 | 0.072391 | 0.98976 | -0.19538 | 0.98887 | -0.21262 | 19.8876
33 | -0.0034247 | -0.00085831 | 0.0034249 | 0.00085818 | 1.9485e-07 | -1.2834e-07 | 0.005143 | 0.0051429 | 0.005143 | 0.99085 | -0.1742 | 0.99092 | -0.17301 | 1.4129
34 | -0.0060371 | -0.0015129 | 0.0060373 | 0.0015129 | 2.1196e-07 | 4.7055e-08 | 0.0090656 | 0.0090655 | 0.0090656 | 0.99092 | -0.17301 | 0.99095 | -0.17227 | 2.4905
35 | 0.31722 | 0.081282 | -0.31604 | -0.080531 | 0.00118 | 0.00075074 | 0.47628 | 0.47628 | 0.47628 | 0.99239 | -0.14414 | 0.98836 | -0.2212 | 26.1694
36 | 0.31043 | 0.079124 | -0.30967 | -0.078645 | 0.00075293 | 0.00047894 | 0.46783 | 0.46783 | 0.46783 | 0.98836 | -0.2212 | 0.98575 | -0.27159 | 25.7051
37 | 0.019511 | 0.0048927 | -0.019504 | -0.0048882 | 7.3951e-06 | 4.4385e-06 | 0.029336 | 0.029336 | 0.029336 | 0.98972 | -0.19588 | 0.98931 | -0.20384 | 8.0593
38 | 0.15925 | 0.040309 | -0.15911 | -0.040224 | 0.00013628 | 8.5186e-05 | 0.23952 | 0.23952 | 0.23952 | 0.98993 | -0.19184 | 0.989 | -0.20969 | 13.1602
39 | 0.012188 | 0.0030546 | -0.012187 | -0.0030544 | 2.4555e-07 | 1.3213e-07 | 0.018331 | 0.018331 | 0.018331 | 0.98931 | -0.20384 | 0.98929 | -0.20426 | 5.036
40 | 0.1531 | 0.038718 | -0.15297 | -0.038632 | 0.00013491 | 8.5994e-05 | 0.23048 | 0.23048 | 0.23048 | 0.989 | -0.20969 | 0.98805 | -0.22807 | 31.6588
41 | 0.13021 | 0.032928 | -0.13019 | -0.03292 | 1.3558e-05 | 8.6648e-06 | 0.1962 | 0.1962 | 0.1962 | 0.98805 | -0.22807 | 0.98794 | -0.23025 | 53.9009
42 | -0.58976 | -0.15133 | 0.59109 | 0.15218 | 0.001332 | 0.00085097 | 0.88099 | 0.88099 | 0.88099 | 0.99754 | -0.046434 | 1 | 0 | 48.4063
43 | 0.11364 | 0.028772 | -0.11318 | -0.028473 | 0.00046814 | 0.00029907 | 0.17127 | 0.17127 | 0.17127 | 0.98794 | -0.23025 | 0.9835 | -0.31643 | 47.0528
44 | 0.031454 | 0.0078937 | -0.03143 | -0.0078784 | 2.4438e-05 | 1.5275e-05 | 0.047594 | 0.047594 | 0.047594 | 0.9835 | -0.31643 | 0.98266 | -0.33274 | 13.0752
45 | 0.010418 | 0.0026124 | -0.010416 | -0.0026114 | 1.9576e-06 | 9.8722e-07 | 0.015776 | 0.015776 | 0.015776 | 0.98266 | -0.33274 | 0.98246 | -0.33668 | 4.3342
46 | 0.010416 | 0.0026114 | -0.010414 | -0.0026101 | 2.6256e-06 | 1.3243e-06 | 0.015776 | 0.015777 | 0.015777 | 0.98246 | -0.33668 | 0.98219 | -0.34197 | 4.3342
47 | 0.014729 | 0.0036943 | -0.014727 | -0.0036928 | 2.6378e-06 | 1.5095e-06 | 0.022317 | 0.022317 | 0.022317 | 0.98215 | -0.34275 | 0.98196 | -0.3465 | 6.131
48 | 0.014727 | 0.0036928 | -0.014721 | -0.0036894 | 5.9105e-06 | 3.3826e-06 | 0.022317 | 0.022317 | 0.022317 | 0.98196 | -0.3465 | 0.98153 | -0.35493 | 6.1311
49 | 0.010414 | 0.0026101 | -0.010413 | -0.0026097 | 7.3438e-07 | 3.7043e-07 | 0.015777 | 0.015777 | 0.015777 | 0.98219 | -0.34197 | 0.98212 | -0.34345 | 4.3342
50 | 0.007448 | 0.0018668 | -0.007447 | -0.0018664 | 9.9134e-07 | 3.645e-07 | 0.011207 | 0.011208 | 0.011208 | 0.98887 | -0.21262 | 0.98873 | -0.21542 | 3.079
51 | 0.040653 | 0.010218 | -0.040601 | -0.010185 | 5.1981e-05 | 3.2793e-05 | 0.061184 | 0.061184 | 0.061184 | 0.98887 | -0.21262 | 0.98749 | -0.23944 | 16.8087
52 | 0.26187 | 0.066414 | -0.26164 | -0.066269 | 0.00022769 | 0.0001445 | 0.39656 | 0.39656 | 0.39656 | 0.98329 | -0.31905 | 0.98236 | -0.33715 | 21.7892
53 | -0.27136 | -0.068793 | 0.27165 | 0.068975 | 0.0002862 | 0.00018173 | 0.41093 | 0.41093 | 0.41093 | 0.98329 | -0.31905 | 0.98442 | -0.29713 | 22.5786
54 | 0.25873 | 0.065541 | -0.25864 | -0.065485 | 8.7454e-05 | 5.5491e-05 | 0.39216 | 0.39216 | 0.39216 | 0.98236 | -0.33715 | 0.98199 | -0.34419 | 21.5473
55 | -0.27844 | -0.070677 | 0.27856 | 0.070753 | 0.00011962 | 7.5983e-05 | 0.42119 | 0.42119 | 0.42119 | 0.98442 | -0.29713 | 0.98488 | -0.28821 | 23.1426
56 | 0.24051 | 0.06094 | -0.24031 | -0.060812 | 0.00020316 | 0.00012874 | 0.36469 | 0.36469 | 0.36469 | 0.98199 | -0.34419 | 0.98109 | -0.36179 | 20.0377
57 | 0.018132 | 0.0045448 | -0.01813 | -0.0045439 | 1.5665e-06 | 9.3255e-07 | 0.027476 | 0.027476 | 0.027476 | 0.98199 | -0.34419 | 0.9819 | -0.34601 | 7.5482
58 | -0.29517 | -0.074919 | 0.2953 | 0.074997 | 0.00012291 | 7.8139e-05 | 0.4463 | 0.4463 | 0.4463 | 0.98488 | -0.28821 | 0.98533 | -0.27955 | 24.5219
59 | 0.016616 | 0.0041661 | -0.016612 | -0.0041636 | 4.3185e-06 | 2.5314e-06 | 0.025105 | 0.025105 | 0.025105 | 0.98488 | -0.28821 | 0.98461 | -0.29366 | 6.8969
60 | 0.23686 | 0.059947 | -0.23685 | -0.059941 | 9.9909e-06 | 6.3291e-06 | 0.35946 | 0.35946 | 0.35946 | 0.98109 | -0.36179 | 0.98104 | -0.36267 | 19.7504
61 | -0.30334 | -0.077013 | 0.30346 | 0.077087 | 0.0001163 | 7.3961e-05 | 0.45845 | 0.45845 | 0.45845 | 0.98533 | -0.27955 | 0.98575 | -0.27159 | 25.1894
62 | 0.0098659 | 0.002473 | -0.0098644 | -0.0024722 | 1.4952e-06 | 7.2884e-07 | 0.01491 | 0.01491 | 0.01491 | 0.98461 | -0.29366 | 0.98444 | -0.29684 | 4.0962
63 | 0.23238 | 0.058821 | -0.23225 | -0.058737 | 0.00013316 | 8.432e-05 | 0.35268 | 0.35268 | 0.35268 | 0.98104 | -0.36267 | 0.98043 | -0.37462 | 19.3779
64 | 0.23225 | 0.058737 | -0.23216 | -0.058684 | 8.3749e-05 | 5.3033e-05 | 0.35268 | 0.35268 | 0.35268 | 0.98043 | -0.37462 | 0.98004 | -0.38214 | 19.378
65 | 0.2252 | 0.056939 | -0.22499 | -0.056803 | 0.0002146 | 0.0001358 | 0.34211 | 0.34211 | 0.34211 | 0.98004 | -0.38214 | 0.97902 | -0.40202 | 18.7972
66 | 0.2184 | 0.055151 | -0.21834 | -0.055114 | 5.8684e-05 | 3.7112e-05 | 0.33209 | 0.33209 | 0.33209 | 0.97902 | -0.40202 | 0.97874 | -0.40763 | 18.2467
67 | 0.20508 | 0.051792 | -0.20507 | -0.051786 | 8.4744e-06 | 5.3507e-06 | 0.31194 | 0.31194 | 0.31194 | 0.97874 | -0.40763 | 0.97869 | -0.4085 | 17.1394
68 | 0.19903 | 0.050273 | -0.19898 | -0.050239 | 5.3257e-05 | 3.3598e-05 | 0.30276 | 0.30276 | 0.30276 | 0.97869 | -0.4085 | 0.97841 | -0.41408 | 16.6349
69 | 0.12498 | 0.031394 | -0.12496 | -0.031382 | 1.9856e-05 | 1.2257e-05 | 0.19114 | 0.19114 | 0.19114 | 0.97314 | -0.51746 | 0.97297 | -0.52078 | 10.5019
70 | -0.12843 | -0.032257 | 0.12844 | 0.032264 | 1.0454e-05 | 6.466e-06 | 0.1964 | 0.1964 | 0.1964 | 0.97314 | -0.51746 | 0.97323 | -0.51575 | 10.7914
71 | 0.12357 | 0.031033 | -0.12357 | -0.031033 | 1.7172e-07 | 1.0592e-07 | 0.18901 | 0.18901 | 0.18901 | 0.97297 | -0.52078 | 0.97297 | -0.52081 | 10.3851
72 | -0.1367 | -0.034333 | 0.13675 | 0.034367 | 5.4532e-05 | 3.3866e-05 | 0.20903 | 0.20903 | 0.20903 | 0.97323 | -0.51575 | 0.97365 | -0.50739 | 11.4851
73 | 0.12223 | 0.030697 | -0.12219 | -0.03067 | 4.4251e-05 | 2.7273e-05 | 0.18696 | 0.18696 | 0.18696 | 0.97297 | -0.52081 | 0.97258 | -0.5284 | 10.2724
74 | -0.14428 | -0.036256 | 0.14433 | 0.036284 | 4.5734e-05 | 2.849e-05 | 0.22054 | 0.22054 | 0.22054 | 0.97365 | -0.50739 | 0.97399 | -0.50075 | 12.1177
75 | 0.12092 | 0.030352 | -0.1209 | -0.030343 | 1.3502e-05 | 8.3152e-06 | 0.18502 | 0.18502 | 0.18502 | 0.97258 | -0.5284 | 0.97247 | -0.53075 | 10.1658
76 | -0.14582 | -0.036657 | 0.14584 | 0.03667 | 2.1374e-05 | 1.3322e-05 | 0.22282 | 0.22282 | 0.22282 | 0.97399 | -0.50075 | 0.97414 | -0.49769 | 12.2426
77 | 0.11893 | 0.029849 | -0.11893 | -0.029847 | 2.5313e-06 | 1.5568e-06 | 0.182 | 0.182 | 0.182 | 0.97247 | -0.53075 | 0.97244 | -0.53119 | 9.9999
78 | -0.15369 | -0.038638 | 0.1537 | 0.038642 | 7.7161e-06 | 4.8221e-06 | 0.23481 | 0.23481 | 0.23481 | 0.97414 | -0.49769 | 0.9742 | -0.49663 | 12.9015
79 | 0.11446 | 0.028727 | -0.11445 | -0.02872 | 1.1232e-05 | 6.8856e-06 | 0.17516 | 0.17516 | 0.17516 | 0.97244 | -0.53119 | 0.97234 | -0.53325 | 9.6242
80 | -0.15508 | -0.038988 | 0.15529 | 0.039119 | 0.00021041 | 0.00013155 | 0.23691 | 0.23691 | 0.23691 | 0.9742 | -0.49663 | 0.97564 | -0.46826 | 13.0171
81 | 0.17883 | 0.045137 | -0.17875 | -0.045085 | 8.2273e-05 | 5.1728e-05 | 0.27231 | 0.27231 | 0.27231 | 0.97762 | -0.4294 | 0.97713 | -0.43901 | 14.9623
82 | -0.19011 | -0.047963 | 0.1902 | 0.04802 | 9.0587e-05 | 5.7071e-05 | 0.28948 | 0.28948 | 0.28948 | 0.97762 | -0.4294 | 0.97813 | -0.41945 | 15.9054
83 | 0.1695 | 0.042765 | -0.16948 | -0.042758 | 1.1629e-05 | 7.2972e-06 | 0.25822 | 0.25822 | 0.25822 | 0.97713 | -0.43901 | 0.97706 | -0.44044 | 14.1878
84 | -0.19504 | -0.049232 | 0.19509 | 0.049263 | 5.0197e-05 | 3.1649e-05 | 0.29683 | 0.29683 | 0.29683 | 0.97813 | -0.41945 | 0.97841 | -0.41408 | 16.3096
85 | 0.16768 | 0.042305 | -0.16762 | -0.04227 | 5.5591e-05 | 3.4867e-05 | 0.25547 | 0.25547 | 0.25547 | 0.97706 | -0.44044 | 0.9767 | -0.44737 | 14.0367
86 | 0.16118 | 0.040654 | -0.16112 | -0.040621 | 5.3137e-05 | 3.3273e-05 | 0.24565 | 0.24565 | 0.24565 | 0.9767 | -0.44737 | 0.97635 | -0.45426 | 13.497
87 | 0.15539 | 0.039184 | -0.15529 | -0.039119 | 0.00010408 | 6.5068e-05 | 0.23691 | 0.23691 | 0.23691 | 0.97635 | -0.45426 | 0.97564 | -0.46826 | 13.017
88 | 0.11251 | 0.028234 | -0.11248 | -0.028219 | 2.3325e-05 | 1.4278e-05 | 0.17219 | 0.17219 | 0.17219 | 0.97234 | -0.53325 | 0.97212 | -0.5376 | 9.4608
89 | 0.10874 | 0.02728 | -0.10872 | -0.027268 | 2.0684e-05 | 1.2621e-05 | 0.16645 | 0.16645 | 0.16645 | 0.97212 | -0.5376 | 0.97192 | -0.54159 | 9.1458
90 | 0.10598 | 0.026583 | -0.10598 | -0.026581 | 3.7592e-06 | 2.2879e-06 | 0.16227 | 0.16227 | 0.16227 | 0.97192 | -0.54159 | 0.97188 | -0.54233 | 8.9159
91 | 0.0074856 | 0.0018756 | -0.0074848 | -0.0018759 | 7.8385e-07 | -2.8214e-07 | 0.011479 | 0.011479 | 0.011479 | 0.97037 | -0.57216 | 0.97026 | -0.57436 | 1.5768
92 | -0.014825 | -0.0037151 | 0.014826 | 0.0037145 | 6.1408e-07 | -5.8559e-07 | 0.022734 | 0.022733 | 0.022734 | 0.97037 | -0.57216 | 0.97042 | -0.57129 | 1.2491
93 | -0.014826 | -0.0037145 | 0.014827 | 0.0037131 | 1.4957e-06 | -1.4268e-06 | 0.022733 | 0.022732 | 0.022733 | 0.97042 | -0.57129 | 0.97052 | -0.56917 | 1.2491
94 | -0.014827 | -0.0037131 | 0.014828 | 0.0037127 | 4.0888e-07 | -3.9017e-07 | 0.022732 | 0.022732 | 0.022732 | 0.97052 | -0.56917 | 0.97055 | -0.56859 | 1.249
95 | 0.094953 | 0.023801 | -0.094947 | -0.023798 | 5.6107e-06 | 3.372e-06 | 0.14545 | 0.14545 | 0.14545 | 0.97139 | -0.55192 | 0.97133 | -0.55316 | 7.9919
96 | -0.094953 | -0.023801 | 0.094977 | 0.023816 | 2.4152e-05 | 1.4515e-05 | 0.14545 | 0.14545 | 0.14545 | 0.97139 | -0.55192 | 0.97166 | -0.54658 | 7.9919
97 | 0.046424 | 0.011638 | -0.046411 | -0.011632 | 1.3644e-05 | 6.5071e-06 | 0.07112 | 0.071121 | 0.071121 | 0.97133 | -0.55316 | 0.97102 | -0.55933 | 3.9078
98 | 0.048523 | 0.01216 | -0.048514 | -0.012155 | 8.878e-06 | 4.3563e-06 | 0.074333 | 0.074333 | 0.074333 | 0.97133 | -0.55316 | 0.97114 | -0.557 | 4.0843
99 | -0.10031 | -0.025153 | 0.10033 | 0.025165 | 2.0309e-05 | 1.2287e-05 | 0.15362 | 0.15362 | 0.15362 | 0.97166 | -0.54658 | 0.97188 | -0.54233 | 8.4408
100 | -0.021889 | -0.0054817 | 0.021891 | 0.0054815 | 2.5132e-06 | -2.3051e-07 | 0.033557 | 0.033557 | 0.033557 | 0.97055 | -0.56859 | 0.97067 | -0.56618 | 1.8438
101 | 0.0017235 | 0.00043135 | -0.0017234 | -0.0004317 | 8.5881e-08 | -3.504e-07 | 0.0026422 | 0.0026423 | 0.0026423 | 0.97055 | -0.56859 | 0.9705 | -0.56964 | 0.72591
102 | 0.04382 | 0.010983 | -0.04382 | -0.010983 | 2.7682e-08 | 1.2651e-08 | 0.067152 | 0.067152 | 0.067152 | 0.97102 | -0.55933 | 0.97102 | -0.55934 | 3.6896
103 | 0.04447 | 0.011142 | -0.044462 | -0.011138 | 7.6078e-06 | 3.5176e-06 | 0.068137 | 0.068138 | 0.068138 | 0.97114 | -0.557 | 0.97096 | -0.56059 | 3.7438
104 | -0.030954 | -0.0077528 | 0.030959 | 0.0077541 | 4.9472e-06 | 1.3551e-06 | 0.047449 | 0.047449 | 0.047449 | 0.97067 | -0.56618 | 0.97084 | -0.56282 | 2.6071
105 | 0.00066026 | 0.00016525 | -0.00066025 | -0.00016548 | 7.037e-09 | -2.2177e-07 | 0.0010123 | 0.0010123 | 0.0010123 | 0.9705 | -0.56964 | 0.97049 | -0.56986 | 0.27812
106 | 0.04125 | 0.010338 | -0.04125 | -0.010338 | 1.0143e-07 | 4.3981e-08 | 0.063213 | 0.063213 | 0.063213 | 0.97102 | -0.55934 | 0.97102 | -0.55939 | 3.4732
107 | 0.0039393 | 0.00098641 | -0.0039391 | -0.00098648 | 2.6038e-07 | -6.8986e-08 | 0.0060368 | 0.0060369 | 0.0060369 | 0.97096 | -0.56059 | 0.97089 | -0.56198 | 1.6585
108 | 0.040026 | 0.010027 | -0.040021 | -0.010025 | 4.2532e-06 | 1.7901e-06 | 0.061339 | 0.061339 | 0.061339 | 0.97096 | -0.56059 | 0.97084 | -0.56282 | 3.3703
109 | 0.0022236 | 0.0005568 | -0.0022234 | -0.00055706 | 1.2035e-07 | -2.6463e-07 | 0.003408 | 0.0034081 | 0.0034081 | 0.97082 | -0.56326 | 0.97076 | -0.56439 | 0.93628
110 | -0.0022236 | -0.0005568 | 0.0022236 | 0.00055663 | 7.602e-08 | -1.6718e-07 | 0.003408 | 0.0034079 | 0.003408 | 0.97082 | -0.56326 | 0.97086 | -0.56254 | 0.93625
111 | 0.0015494 | 0.00038814 | -0.0015494 | -0.00038816 | 3.8018e-09 | -1.9789e-08 | 0.0023749 | 0.0023749 | 0.0023749 | 0.97076 | -0.56439 | 0.97076 | -0.56444 | 0.65246
112 | -0.0031601 | -0.00079133 | 0.0031602 | 0.00079127 | 8.3988e-08 | -6.4324e-08 | 0.0048432 | 0.0048431 | 0.0048432 | 0.97086 | -0.56254 | 0.97089 | -0.56198 | 1.3305
113 | 0.00092529 | 0.00023174 | -0.00092528 | -0.0002319 | 1.0227e-08 | -1.6107e-07 | 0.0014183 | 0.0014183 | 0.0014183 | 0.97076 | -0.56444 | 0.97075 | -0.56468 | 0.38965
114 | -0.0034328 | -0.00086035 | 0.003433 | 0.00086026 | 1.7126e-07 | -9.4051e-08 | 0.0052638 | 0.0052637 | 0.0052638 | 0.97043 | -0.57104 | 0.97048 | -0.56999 | 1.4461
115 | -0.01576 | -0.0039496 | 0.015763 | 0.003951 | 3.2612e-06 | 1.3509e-06 | 0.024164 | 0.024164 | 0.024164 | 0.97048 | -0.56999 | 0.9707 | -0.56565 | 3.3192
116 | -0.019646 | -0.0049241 | 0.019646 | 0.0049241 | 1.1056e-07 | -2.9703e-08 | 0.030116 | 0.030116 | 0.030116 | 0.9707 | -0.56565 | 0.97071 | -0.56553 | 1.6547
117 | -0.022758 | -0.005704 | 0.02276 | 0.0057039 | 2.3988e-06 | -8.9337e-08 | 0.034886 | 0.034886 | 0.034886 | 0.97071 | -0.56553 | 0.97082 | -0.56332 | 1.9168
118 | -0.024771 | -0.0062078 | 0.024771 | 0.0062078 | 7.447e-07 | 5.0734e-08 | 0.037967 | 0.037967 | 0.037967 | 0.97082 | -0.56332 | 0.97085 | -0.56269 | 2.0861
119 | -0.031665 | -0.0079355 | 0.031665 | 0.0079355 | 1.255e-07 | 3.6396e-08 | 0.048532 | 0.048532 | 0.048532 | 0.97085 | -0.56269 | 0.97085 | -0.56261 | 2.6666
120 | -0.034104 | -0.0085467 | 0.034104 | 0.0085468 | 2.2696e-07 | 7.6774e-08 | 0.05227 | 0.05227 | 0.05227 | 0.97085 | -0.56261 | 0.97086 | -0.56247 | 2.872
121 | -0.036083 | -0.0090428 | 0.036088 | 0.0090447 | 5.265e-06 | 1.9502e-06 | 0.055303 | 0.055303 | 0.055303 | 0.97086 | -0.56247 | 0.97102 | -0.5594 | 3.0386
122 | -0.038661 | -0.0096894 | 0.038661 | 0.0096894 | 2.133e-08 | 8.6533e-09 | 0.059245 | 0.059245 | 0.059245 | 0.97102 | -0.5594 | 0.97102 | -0.55939 | 3.2552
123 | 0.011004 | 0.0027578 | -0.011003 | -0.0027577 | 2.2288e-07 | 1.1511e-07 | 0.016599 | 0.0166 | 0.0166 | 0.98638 | -0.26102 | 0.98636 | -0.26145 | 4.5603
124 | -0.015165 | -0.0038008 | 0.015172 | 0.0038046 | 6.695e-06 | 3.8491e-06 | 0.022877 | 0.022877 | 0.022877 | 0.98638 | -0.26102 | 0.98686 | -0.25176 | 6.285
125 | 0.010715 | 0.0026865 | -0.010711 | -0.0026845 | 3.7776e-06 | 1.9248e-06 | 0.016157 | 0.016157 | 0.016157 | 0.98686 | -0.25176 | 0.98648 | -0.25916 | 4.4388
126 | -0.025887 | -0.0064911 | 0.025898 | 0.0064978 | 1.082e-05 | 6.6829e-06 | 0.039035 | 0.039034 | 0.039035 | 0.98686 | -0.25176 | 0.98731 | -0.24299 | 10.7238
127 | 0.0071816 | 0.0017999 | -0.0071809 | -0.0017997 | 6.7559e-07 | 2.3574e-07 | 0.010824 | 0.010824 | 0.010824 | 0.98731 | -0.24299 | 0.9872 | -0.24497 | 2.9736
128 | -0.033079 | -0.0082977 | 0.033085 | 0.0083012 | 5.6024e-06 | 3.5087e-06 | 0.049858 | 0.049858 | 0.049858 | 0.98731 | -0.24299 | 0.98749 | -0.23944 | 13.6973
129 | 0.007516 | 0.0018839 | -0.0075146 | -0.0018833 | 1.4051e-06 | 5.2566e-07 | 0.011326 | 0.011326 | 0.011326 | 0.98749 | -0.23944 | 0.98729 | -0.24336 | 3.1115

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59613 | 0.15303

## res_load
| p_mw | q_mvar
0 | 0.0018538 | 0.0004646
1 | 0.0016755 | 0.00041993
2 | 0.0057563 | 0.0014427
3 | 0.0057458 | 0.00144
4 | 0.0083234 | 0.002086
5 | 0.00071422 | 0.000179
6 | 0.00077875 | 0.00019517
7 | 0.0012475 | 0.00031265
8 | 0.0026919 | 0.00067465
9 | 0.023912 | 0.005993
10 | 0.0054205 | 0.0013585
11 | 0.0037664 | 0.00094395
12 | 0.0023744 | 0.00059509
13 | 0.0034247 | 0.00085831
14 | 0.0026122 | 0.00065468
15 | 0.0003991 | 0.00010003
16 | 0.0056133 | 0.0014068
17 | 0.0080118 | 0.0020079
18 | 0.0073165 | 0.0018337
19 | 0.0060084 | 0.0015058
20 | 0.012187 | 0.0030544
21 | 0.02276 | 0.0057042
22 | 0.0022643 | 0.00056749
23 | 0.01655 | 0.0041478
24 | 0.021012 | 0.005266
25 | 0.02804 | 0.0070274
26 | 0.014721 | 0.0036894
27 | 0.010413 | 0.0026097
28 | 0.0094948 | 0.0023796
29 | 0.002906 | 0.00072831
30 | 0.0067903 | 0.0017018
31 | 0.0034483 | 0.00086422
32 | 0.01813 | 0.0045439
33 | 0.0080447 | 0.0020162
34 | 0.0067457 | 0.0016906
35 | 0.0044689 | 0.00112
36 | 0.0062177 | 0.0015583
37 | 0.0098644 | 0.0024722
38 | 0.0069621 | 0.0017449
39 | 0.0065916 | 0.001652
40 | 0.013256 | 0.0033222
41 | 0.0060388 | 0.0015135
42 | 0.0033868 | 0.00084882
43 | 0.0034453 | 0.00086348
44 | 0.0013901 | 0.00034838
45 | 0.0082575 | 0.0020695
46 | 0.0013418 | 0.00033629
47 | 0.0075344 | 0.0018883
48 | 0.0012683 | 0.00031788
49 | 0.0014875 | 0.00037279
50 | 0.0019731 | 0.0004945
51 | 0.0078503 | 0.0019675
52 | 0.0044689 | 0.00112
53 | 0.0013775 | 0.00034524
54 | 0.011276 | 0.0028261
55 | 0.0092562 | 0.0023198
56 | 0.0048359 | 0.001212
57 | 0.0018068 | 0.00045284
58 | 0.0038939 | 0.00097591
59 | 0.0064465 | 0.0016156
60 | 0.0057328 | 0.0014368
61 | 0.001943 | 0.00048697
62 | 0.0037462 | 0.00093888
63 | 0.0027325 | 0.00068482
64 | 0.0073397 | 0.0018395
65 | 0.0074848 | 0.0018759
66 | 0.0053351 | 0.0013371
67 | 0.0053373 | 0.0013376
68 | 0.0025905 | 0.00064924
69 | 0.004044 | 0.0010135
70 | 0.0056474 | 0.0014154
71 | 0.0090627 | 0.0022713
72 | 0.0010631 | 0.00026645
73 | 0.0025701 | 0.00064412
74 | 0.00049709 | 0.00012458
75 | 0.0090627 | 0.0022713
76 | 0.00066025 | 0.00016548
77 | 0.00067401 | 0.00016892
78 | 0.00093647 | 0.0002347
79 | 0.00062413 | 0.00015642
80 | 0.0007789 | 0.00019521
81 | 0.00092528 | 0.0002319
82 | 0.0034328 | 0.00086035
83 | 0.012327 | 0.0030894
84 | 0.0038829 | 0.00097314
85 | 0.0031119 | 0.00077991
86 | 0.0020103 | 0.00050383
87 | 0.0068934 | 0.0017277
88 | 0.0024389 | 0.00061124
89 | 0.0019788 | 0.00049594
90 | 0.0025724 | 0.0006447
91 | 0.0025896 | 0.00064902
92 | 0.0041616 | 0.001043
93 | 0.011003 | 0.0027577
94 | 0.010711 | 0.0026845
95 | 0.0071809 | 0.0017997
96 | 0.0075146 | 0.0018833
97 | 0.007447 | 0.0018664

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1