## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_27-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_27-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_27-6_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_27-6_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_27-6_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_27-6_0_4_node_33 | 0.4 | n |  | TRUE
6 | bus_LV_27-6_0_4_node_64 | 0.4 | n |  | TRUE
7 | bus_LV_27-6_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_27-6_0_4_node_112 | 0.4 | n |  | TRUE
9 | bus_LV_27-6_0_4_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_27-6_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_27-6_0_4_node_144 | 0.4 | n |  | TRUE
12 | bus_LV_27-6_0_4_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_27-6_0_4_node_145 | 0.4 | n |  | TRUE
14 | bus_LV_27-6_0_4_node_142 | 0.4 | n |  | TRUE
15 | bus_LV_27-6_0_4_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_27-6_0_4_node_157 | 0.4 | n |  | TRUE
17 | bus_LV_27-6_0_4_node_158 | 0.4 | n |  | TRUE
18 | bus_LV_27-6_0_4_node_156 | 0.4 | n |  | TRUE
19 | bus_LV_27-6_0_4_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_27-6_0_4_node_170 | 0.4 | n |  | TRUE
21 | bus_LV_27-6_0_4_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_27-6_0_4_node_161 | 0.4 | n |  | TRUE
23 | bus_LV_27-6_0_4_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_27-6_0_4_node_95 | 0.4 | n |  | TRUE
25 | bus_LV_27-6_0_4_node_79 | 0.4 | n |  | TRUE
26 | bus_LV_27-6_0_4_node_168 | 0.4 | n |  | TRUE
27 | bus_LV_27-6_0_4_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_27-6_0_4_node_72 | 0.4 | n |  | TRUE
29 | bus_LV_27-6_0_4_node_191 | 0.4 | n |  | TRUE
30 | bus_LV_27-6_0_4_node_65 | 0.4 | n |  | TRUE
31 | bus_LV_27-6_0_4_node_207 | 0.4 | n |  | TRUE
32 | bus_LV_27-6_0_4_node_113 | 0.4 | n |  | TRUE
33 | bus_LV_27-6_0_4_node_11 | 0.4 | n |  | TRUE
34 | bus_LV_27-6_0_4_node_6 | 0.4 | n |  | TRUE
35 | bus_LV_27-6_0_4_node_7 | 0.4 | n |  | TRUE
36 | bus_LV_27-6_0_4_node_8 | 0.4 | n |  | TRUE
37 | bus_LV_27-6_0_4_node_9 | 0.4 | n |  | TRUE
38 | bus_LV_27-6_0_4_node_13 | 0.4 | n |  | TRUE
39 | bus_LV_27-6_0_4_node_121 | 0.4 | n |  | TRUE
40 | bus_LV_27-6_0_4_node_122 | 0.4 | n |  | TRUE
41 | bus_LV_27-6_0_4_node_160 | 0.4 | n |  | TRUE
42 | bus_LV_27-6_0_4_node_77 | 0.4 | n |  | TRUE
43 | bus_LV_27-6_0_4_node_163 | 0.4 | n |  | TRUE
44 | bus_LV_27-6_0_4_node_162 | 0.4 | n |  | TRUE
45 | bus_LV_27-6_0_4_node_146 | 0.4 | n |  | TRUE
46 | bus_LV_27-6_0_4_node_143 | 0.4 | n |  | TRUE
47 | bus_LV_27-6_0_4_node_185 | 0.4 | n |  | TRUE
48 | bus_LV_27-6_0_4_node_69 | 0.4 | n |  | TRUE
49 | bus_LV_27-6_0_4_node_66 | 0.4 | n |  | TRUE
50 | bus_LV_27-6_0_4_node_73 | 0.4 | n |  | TRUE
51 | bus_LV_27-6_0_4_node_74 | 0.4 | n |  | TRUE
52 | bus_LV_27-6_0_4_node_67 | 0.4 | n |  | TRUE
53 | bus_LV_27-6_0_4_node_68 | 0.4 | n |  | TRUE
54 | bus_LV_27-6_0_4_node_70 | 0.4 | n |  | TRUE
55 | bus_LV_27-6_0_4_node_71 | 0.4 | n |  | TRUE
56 | bus_LV_27-6_0_4_node_194 | 0.4 | n |  | TRUE
57 | bus_LV_27-6_0_4_node_132 | 0.4 | n |  | TRUE
58 | bus_LV_27-6_0_4_node_193 | 0.4 | n |  | TRUE
59 | bus_LV_27-6_0_4_node_197 | 0.4 | n |  | TRUE
60 | bus_LV_27-6_0_4_node_134 | 0.4 | n |  | TRUE
61 | bus_LV_27-6_0_4_node_135 | 0.4 | n |  | TRUE
62 | bus_LV_27-6_0_4_node_130 | 0.4 | n |  | TRUE
63 | bus_LV_27-6_0_4_node_192 | 0.4 | n |  | TRUE
64 | bus_LV_27-6_0_4_node_183 | 0.4 | n |  | TRUE
65 | bus_LV_27-6_0_4_node_75 | 0.4 | n |  | TRUE
66 | bus_LV_27-6_0_4_node_190 | 0.4 | n |  | TRUE
67 | bus_LV_27-6_0_4_node_184 | 0.4 | n |  | TRUE
68 | bus_LV_27-6_0_4_node_76 | 0.4 | n |  | TRUE
69 | bus_LV_27-6_0_4_node_78 | 0.4 | n |  | TRUE
70 | bus_LV_27-6_0_4_node_80 | 0.4 | n |  | TRUE
71 | bus_LV_27-6_0_4_node_89 | 0.4 | n |  | TRUE
72 | bus_LV_27-6_0_4_node_87 | 0.4 | n |  | TRUE
73 | bus_LV_27-6_0_4_node_111 | 0.4 | n |  | TRUE
74 | bus_LV_27-6_0_4_node_115 | 0.4 | n |  | TRUE
75 | bus_LV_27-6_0_4_node_117 | 0.4 | n |  | TRUE
76 | bus_LV_27-6_0_4_node_116 | 0.4 | n |  | TRUE
77 | bus_LV_27-6_0_4_node_114 | 0.4 | n |  | TRUE
78 | bus_LV_27-6_0_4_node_118 | 0.4 | n |  | TRUE
79 | bus_LV_27-6_0_4_node_138 | 0.4 | n |  | TRUE
80 | bus_LV_27-6_0_4_node_136 | 0.4 | n |  | TRUE
81 | bus_LV_27-6_0_4_node_119 | 0.4 | n |  | TRUE
82 | bus_LV_27-6_0_4_node_137 | 0.4 | n |  | TRUE
83 | bus_LV_27-6_0_4_node_127 | 0.4 | n |  | TRUE
84 | bus_LV_27-6_0_4_node_128 | 0.4 | n |  | TRUE
85 | bus_LV_27-6_0_4_node_129 | 0.4 | n |  | TRUE
86 | bus_LV_27-6_0_4_node_149 | 0.4 | n |  | TRUE
87 | bus_LV_27-6_0_4_node_150 | 0.4 | n |  | TRUE
88 | bus_LV_27-6_0_4_node_131 | 0.4 | n |  | TRUE
89 | bus_LV_27-6_0_4_node_133 | 0.4 | n |  | TRUE
90 | bus_LV_27-6_0_4_node_195 | 0.4 | n |  | TRUE
91 | bus_LV_27-6_0_4_node_196 | 0.4 | n |  | TRUE
92 | bus_LV_27-6_0_4_node_147 | 0.4 | n |  | TRUE
93 | bus_LV_27-6_0_4_node_148 | 0.4 | n |  | TRUE
94 | bus_LV_27-6_0_4_node_180 | 0.4 | n |  | TRUE
95 | bus_LV_27-6_0_4_node_181 | 0.4 | n |  | TRUE
96 | bus_LV_27-6_0_4_node_186 | 0.4 | n |  | TRUE
97 | bus_LV_27-6_0_4_node_182 | 0.4 | n |  | TRUE
98 | bus_LV_27-6_0_4_node_198 | 0.4 | n |  | TRUE
99 | bus_LV_27-6_0_4_node_151 | 0.4 | n |  | TRUE
100 | bus_LV_27-6_0_4_node_152 | 0.4 | n |  | TRUE
101 | bus_LV_27-6_0_4_node_153 | 0.4 | n |  | TRUE
102 | bus_LV_27-6_0_4_node_154 | 0.4 | n |  | TRUE
103 | bus_LV_27-6_0_4_node_155 | 0.4 | n |  | TRUE
104 | bus_LV_27-6_0_4_node_169 | 0.4 | n |  | TRUE
105 | bus_LV_27-6_0_4_node_166 | 0.4 | n |  | TRUE
106 | bus_LV_27-6_0_4_node_159 | 0.4 | n |  | TRUE
107 | bus_LV_27-6_0_4_node_172 | 0.4 | n |  | TRUE
108 | bus_LV_27-6_0_4_node_164 | 0.4 | n |  | TRUE
109 | bus_LV_27-6_0_4_node_165 | 0.4 | n |  | TRUE
110 | bus_LV_27-6_0_4_node_167 | 0.4 | n |  | TRUE
111 | bus_LV_27-6_0_4_node_204 | 0.4 | n |  | TRUE
112 | bus_LV_27-6_0_4_node_199 | 0.4 | n |  | TRUE
113 | bus_LV_27-6_0_4_node_205 | 0.4 | n |  | TRUE
114 | bus_LV_27-6_0_4_node_203 | 0.4 | n |  | TRUE
115 | bus_LV_27-6_0_4_node_202 | 0.4 | n |  | TRUE
116 | bus_LV_27-6_0_4_node_200 | 0.4 | n |  | TRUE
117 | bus_LV_27-6_0_4_node_201 | 0.4 | n |  | TRUE
118 | bus_LV_27-6_0_4_node_206 | 0.4 | n |  | TRUE
119 | bus_MV_554_0_node_165 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_27-6_0_4_load_0 | 0 | 0.011359 | 0.0028469 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_27-6_0_4_load_2 | 2 | 0.0017527 | 0.00043926 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_27-6_0_4_load_64 | 6 | 0.0021833 | 0.00054719 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_27-6_0_4_load_112 | 8 | 0.0011579 | 0.00029021 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_27-6_0_4_load_10 | 10 | 0.0024054 | 0.00060284 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_27-6_0_4_load_144 | 11 | 0.0044008 | 0.0011029 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_27-6_0_4_load_145 | 13 | 0.019227 | 0.0048186 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_27-6_0_4_load_142 | 14 | 0.019333 | 0.0048453 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_27-6_0_4_load_157 | 16 | 0.0046939 | 0.0011764 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_27-6_0_4_load_158 | 17 | 0.00093806 | 0.0002351 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_27-6_0_4_load_156 | 18 | 0.0016977 | 0.00042549 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_27-6_0_4_load_170 | 20 | 0.0069289 | 0.0017365 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_27-6_0_4_load_161 | 22 | 0.004002 | 0.001003 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_27-6_0_4_load_79 | 25 | 0.0034307 | 0.00085982 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_27-6_0_4_load_168 | 26 | 0.0017956 | 0.00045003 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_27-6_0_4_load_191 | 29 | 0.0061394 | 0.0015387 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_27-6_0_4_load_65 | 30 | 0.0021901 | 0.00054889 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_27-6_0_4_load_207 | 31 | 0.0065494 | 0.0016414 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_27-6_0_4_load_113 | 32 | 0.0057499 | 0.0014411 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_27-6_0_4_load_11 | 33 | 0.0023748 | 0.00059518 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_27-6_0_4_load_6 | 34 | 0.0065493 | 0.0016414 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_27-6_0_4_load_7 | 35 | 0.0013092 | 0.00032811 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_27-6_0_4_load_8 | 36 | 0.0041755 | 0.0010465 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_27-6_0_4_load_13 | 38 | 0.00081378 | 0.00020395 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_27-6_0_4_load_121 | 39 | 0.00081327 | 0.00020383 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_27-6_0_4_load_122 | 40 | 0.00081324 | 0.00020382 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_27-6_0_4_load_160 | 41 | 0.001727 | 0.00043281 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_27-6_0_4_load_77 | 42 | 0.0031791 | 0.00079675 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_27-6_0_4_load_163 | 43 | 0.0025238 | 0.00063253 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_27-6_0_4_load_162 | 44 | 0.0047113 | 0.0011808 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_27-6_0_4_load_146 | 45 | 0.01576 | 0.0039498 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_27-6_0_4_load_143 | 46 | 0.019365 | 0.0048533 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_27-6_0_4_load_185 | 47 | 0.0065429 | 0.0016398 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_27-6_0_4_load_66 | 49 | 0.0021842 | 0.00054741 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_27-6_0_4_load_73 | 50 | 0.0059602 | 0.0014938 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_27-6_0_4_load_74 | 51 | 0.0022475 | 0.00056327 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_27-6_0_4_load_67 | 52 | 0.0014314 | 0.00035874 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_27-6_0_4_load_68 | 53 | 0.0014331 | 0.00035918 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_27-6_0_4_load_71 | 55 | 0.0039764 | 0.00099658 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_27-6_0_4_load_194 | 56 | 0.0014335 | 0.00035926 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_27-6_0_4_load_193 | 58 | 0.001432 | 0.0003589 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_27-6_0_4_load_197 | 59 | 0.0014312 | 0.0003587 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_27-6_0_4_load_134 | 60 | 0.0014322 | 0.00035893 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_27-6_0_4_load_135 | 61 | 0.0014328 | 0.0003591 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_27-6_0_4_load_130 | 62 | 0.002468 | 0.00061854 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_27-6_0_4_load_192 | 63 | 0.0014325 | 0.00035901 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_27-6_0_4_load_75 | 65 | 0.0022545 | 0.00056504 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_27-6_0_4_load_190 | 66 | 0.0022475 | 0.00056328 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_27-6_0_4_load_184 | 67 | 0.0061383 | 0.0015384 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_27-6_0_4_load_76 | 68 | 0.0048147 | 0.0012067 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_27-6_0_4_load_78 | 69 | 0.0026399 | 0.00066163 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_27-6_0_4_load_80 | 70 | 0.0021249 | 0.00053255 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_27-6_0_4_load_89 | 71 | 0.0019221 | 0.00048172 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_27-6_0_4_load_87 | 72 | 0.0023781 | 0.00059602 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_27-6_0_4_load_111 | 73 | 0.0020435 | 0.00051215 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_27-6_0_4_load_117 | 75 | 0.0019759 | 0.00049521 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_27-6_0_4_load_116 | 76 | 0.0018388 | 0.00046085 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_27-6_0_4_load_114 | 77 | 0.001574 | 0.00039448 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_27-6_0_4_load_118 | 78 | 0.0012657 | 0.00031722 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_27-6_0_4_load_138 | 79 | 0.0016382 | 0.00041058 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_27-6_0_4_load_136 | 80 | 0.0020351 | 0.00051005 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_27-6_0_4_load_119 | 81 | 0.0012836 | 0.0003217 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_27-6_0_4_load_137 | 82 | 0.00081318 | 0.0002038 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_27-6_0_4_load_127 | 83 | 0.0024228 | 0.00060722 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_27-6_0_4_load_128 | 84 | 0.0012738 | 0.00031925 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_27-6_0_4_load_129 | 85 | 0.0012748 | 0.00031951 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_27-6_0_4_load_149 | 86 | 0.0030868 | 0.00077363 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_27-6_0_4_load_131 | 88 | 0.0022005 | 0.00055149 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_27-6_0_4_load_133 | 89 | 0.0022037 | 0.0005523 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_27-6_0_4_load_195 | 90 | 0.0014331 | 0.00035917 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_27-6_0_4_load_196 | 91 | 0.0022017 | 0.00055179 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_27-6_0_4_load_147 | 92 | 0.0039736 | 0.00099588 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_27-6_0_4_load_148 | 93 | 0.0039722 | 0.00099554 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_27-6_0_4_load_181 | 95 | 0.00095131 | 0.00023842 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_27-6_0_4_load_186 | 96 | 0.0016731 | 0.00041932 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_27-6_0_4_load_182 | 97 | 0.0041219 | 0.001033 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_27-6_0_4_load_198 | 98 | 0.0012754 | 0.00031965 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_27-6_0_4_load_151 | 99 | 0.004121 | 0.0010328 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_27-6_0_4_load_152 | 100 | 0.0016835 | 0.00042192 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_27-6_0_4_load_153 | 101 | 0.0017503 | 0.00043866 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_27-6_0_4_load_155 | 103 | 0.0024293 | 0.00060884 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_27-6_0_4_load_169 | 104 | 0.00050045 | 0.00012543 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_27-6_0_4_load_166 | 105 | 0.0012512 | 0.00031359 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_27-6_0_4_load_159 | 106 | 0.0017121 | 0.00042908 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_27-6_0_4_load_172 | 107 | 0.00033696 | 8.445e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_27-6_0_4_load_164 | 108 | 0.00081789 | 0.00020498 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_27-6_0_4_load_165 | 109 | 0.00081789 | 0.00020498 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_27-6_0_4_load_167 | 110 | 0.002064 | 0.00051729 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_27-6_0_4_load_204 | 111 | 0.001673 | 0.0004193 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_27-6_0_4_load_199 | 112 | 0.0012745 | 0.00031941 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_27-6_0_4_load_205 | 113 | 0.0016746 | 0.00041968 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_27-6_0_4_load_203 | 114 | 0.0012744 | 0.0003194 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_27-6_0_4_load_202 | 115 | 0.0012744 | 0.0003194 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_27-6_0_4_load_200 | 116 | 0.0012742 | 0.00031933 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_27-6_0_4_load_201 | 117 | 0.0012751 | 0.00031958 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_27-6_0_4_load_206 | 118 | 0.001673 | 0.0004193 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_27-6_0_4_line_0 |  | 0 | 1 | 0.065043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_27-6_0_4_line_1 |  | 0 | 2 | 0.02825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_27-6_0_4_line_2 |  | 1 | 3 | 0.025468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_27-6_0_4_line_3 |  | 1 | 4 | 0.036993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_27-6_0_4_line_4 |  | 3 | 5 | 0.00844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_27-6_0_4_line_5 |  | 3 | 6 | 0.061956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_27-6_0_4_line_6 |  | 4 | 7 | 0.022322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_27-6_0_4_line_7 |  | 4 | 8 | 0.010115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_27-6_0_4_line_8 |  | 5 | 11 | 0.010354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_27-6_0_4_line_9 |  | 6 | 30 | 4.2179e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_27-6_0_4_line_10 |  | 7 | 9 | 0.004027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_27-6_0_4_line_11 |  | 7 | 10 | 0.0086851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_27-6_0_4_line_12 |  | 8 | 24 | 0.009689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_27-6_0_4_line_13 |  | 9 | 31 | 0.011783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_27-6_0_4_line_14 |  | 10 | 33 | 0.03079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_27-6_0_4_line_15 |  | 11 | 46 | 0.022507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_27-6_0_4_line_16 |  | 12 | 13 | 0.00074599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_27-6_0_4_line_17 |  | 12 | 14 | 0.034951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_27-6_0_4_line_18 |  | 13 | 45 | 0.04211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_27-6_0_4_line_19 |  | 14 | 46 | 0.052906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_27-6_0_4_line_20 |  | 15 | 16 | 0.015365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_27-6_0_4_line_21 |  | 15 | 17 | 0.024266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_27-6_0_4_line_22 |  | 15 | 18 | 0.014877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_27-6_0_4_line_23 |  | 16 | 44 | 0.011222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_27-6_0_4_line_24 |  | 19 | 20 | 0.027299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_27-6_0_4_line_25 |  | 19 | 21 | 0.022449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_27-6_0_4_line_26 |  | 19 | 22 | 0.012669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_27-6_0_4_line_27 |  | 21 | 26 | 0.019057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_27-6_0_4_line_28 |  | 21 | 23 | 0.013703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_27-6_0_4_line_29 |  | 22 | 41 | 0.024838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_27-6_0_4_line_30 |  | 23 | 24 | 0.028619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_27-6_0_4_line_31 |  | 23 | 25 | 0.055907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_27-6_0_4_line_32 |  | 24 | 32 | 0.011509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_27-6_0_4_line_33 |  | 25 | 42 | 0.018233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_27-6_0_4_line_34 |  | 26 | 43 | 0.026944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_27-6_0_4_line_35 |  | 27 | 28 | 0.06095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_27-6_0_4_line_36 |  | 27 | 29 | 0.063548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_27-6_0_4_line_37 |  | 28 | 47 | 0.025234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_27-6_0_4_line_38 |  | 28 | 48 | 0.02656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_27-6_0_4_line_39 |  | 30 | 49 | 3.7284e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_27-6_0_4_line_40 |  | 33 | 37 | 0.011513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_27-6_0_4_line_41 |  | 34 | 35 | 0.019749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_27-6_0_4_line_42 |  | 34 | 36 | 0.00036179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_27-6_0_4_line_43 |  | 36 | 37 | 0.026677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_27-6_0_4_line_44 |  | 37 | 38 | 0.013212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_27-6_0_4_line_45 |  | 38 | 39 | 0.0072312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_27-6_0_4_line_46 |  | 39 | 40 | 0.014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_27-6_0_4_line_47 |  | 40 | 82 | 0.0072308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_27-6_0_4_line_48 |  | 41 | 106 | 0.017843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_27-6_0_4_line_49 |  | 42 | 68 | 0.01413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_27-6_0_4_line_50 |  | 43 | 44 | 0.11099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_27-6_0_4_line_51 |  | 45 | 92 | 0.03357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_27-6_0_4_line_52 |  | 47 | 64 | 0.03528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_27-6_0_4_line_53 |  | 48 | 54 | 0.028707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_27-6_0_4_line_54 |  | 48 | 55 | 0.016765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_27-6_0_4_line_55 |  | 48 | 52 | 0.012452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_27-6_0_4_line_56 |  | 49 | 50 | 0.028748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_27-6_0_4_line_57 |  | 50 | 51 | 0.03932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_27-6_0_4_line_58 |  | 51 | 65 | 4.0697e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_27-6_0_4_line_59 |  | 52 | 53 | 0.010815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_27-6_0_4_line_60 |  | 54 | 56 | 0.013577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_27-6_0_4_line_61 |  | 54 | 57 | 0.029744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_27-6_0_4_line_62 |  | 54 | 58 | 0.012494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_27-6_0_4_line_63 |  | 56 | 59 | 0.010728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_27-6_0_4_line_64 |  | 57 | 60 | 0.013489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_27-6_0_4_line_65 |  | 57 | 61 | 0.012698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_27-6_0_4_line_66 |  | 57 | 62 | 0.020276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_27-6_0_4_line_67 |  | 58 | 63 | 0.010805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_27-6_0_4_line_68 |  | 60 | 90 | 0.010815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_27-6_0_4_line_69 |  | 61 | 91 | 0.010726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_27-6_0_4_line_70 |  | 62 | 88 | 0.021545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_27-6_0_4_line_71 |  | 64 | 67 | 0.0050497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_27-6_0_4_line_72 |  | 64 | 97 | 0.023205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_27-6_0_4_line_73 |  | 65 | 66 | 3.9617e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_27-6_0_4_line_74 |  | 66 | 67 | 0.02875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_27-6_0_4_line_75 |  | 68 | 69 | 0.012915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_27-6_0_4_line_76 |  | 69 | 70 | 0.0034797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_27-6_0_4_line_77 |  | 70 | 71 | 0.018079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_27-6_0_4_line_78 |  | 71 | 72 | 0.0089321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_27-6_0_4_line_79 |  | 73 | 74 | 0.009025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_27-6_0_4_line_80 |  | 73 | 75 | 0.01495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_27-6_0_4_line_81 |  | 74 | 76 | 0.0061872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_27-6_0_4_line_82 |  | 74 | 77 | 0.020221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_27-6_0_4_line_83 |  | 75 | 78 | 0.014283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_27-6_0_4_line_84 |  | 76 | 79 | 0.016954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_27-6_0_4_line_85 |  | 78 | 81 | 0.0076968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_27-6_0_4_line_86 |  | 79 | 80 | 0.01742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_27-6_0_4_line_87 |  | 80 | 82 | 0.01615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_27-6_0_4_line_88 |  | 83 | 84 | 0.011569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_27-6_0_4_line_89 |  | 84 | 85 | 0.0035832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_27-6_0_4_line_90 |  | 85 | 86 | 0.017768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_27-6_0_4_line_91 |  | 86 | 87 | 0.0052975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_27-6_0_4_line_92 |  | 87 | 94 | 0.025824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_27-6_0_4_line_93 |  | 87 | 95 | 0.010931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_27-6_0_4_line_94 |  | 88 | 89 | 0.010812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_27-6_0_4_line_95 |  | 92 | 93 | 0.01583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_27-6_0_4_line_96 |  | 94 | 96 | 0.011703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_27-6_0_4_line_97 |  | 94 | 97 | 0.0043318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_27-6_0_4_line_98 |  | 95 | 98 | 0.0010702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_27-6_0_4_line_99 |  | 96 | 111 | 0.0074439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_27-6_0_4_line_100 |  | 98 | 112 | 0.0074425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_27-6_0_4_line_101 |  | 99 | 100 | 0.016952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_27-6_0_4_line_102 |  | 99 | 101 | 0.0020109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_27-6_0_4_line_103 |  | 100 | 102 | 0.025232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_27-6_0_4_line_104 |  | 101 | 103 | 0.015239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_27-6_0_4_line_105 |  | 102 | 104 | 0.030773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_27-6_0_4_line_106 |  | 102 | 105 | 0.01243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_27-6_0_4_line_107 |  | 103 | 106 | 0.020183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_27-6_0_4_line_108 |  | 104 | 107 | 0.0081779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_27-6_0_4_line_109 |  | 105 | 108 | 0.0013641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_27-6_0_4_line_110 |  | 108 | 109 | 0.012647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_27-6_0_4_line_111 |  | 109 | 110 | 0.020156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_27-6_0_4_line_112 |  | 111 | 113 | 0.013916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_27-6_0_4_line_113 |  | 112 | 114 | 0.015028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_27-6_0_4_line_114 |  | 113 | 118 | 0.0074429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_27-6_0_4_line_115 |  | 114 | 115 | 2.8366e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_27-6_0_4_line_116 |  | 115 | 116 | 0.0069234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_27-6_0_4_line_117 |  | 116 | 117 | 0.0005177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_27-6_0_4_trafo_1 | 0.63 MVA 20/0.4 kV | 119 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2689922.6546 | 1282959.744 | 2689929.6462 | 1282958.1937 | 2689961.7065 | 1282955.8142 | 2689968.3915 | 1282954.1814 | 2689973.8829 | 1282951.5519 | 2689985.1191 | 1282945.4975
1 | 2690009.9885 | 1282932.0973 | 2689985.1191 | 1282945.4975
2 | 2689910.1138 | 1282938.2007 | 2689916.4579 | 1282944.1471 | 2689919.1086 | 1282950.037 | 2689921.93 | 1282957.531 | 2689922.6546 | 1282959.744
3 | 2689922.6546 | 1282959.744 | 2689929.8863 | 1282981.8068 | 2689931.3997 | 1282984.977 | 2689932.8058 | 1282986.8112 | 2689925.5989 | 1282990.1708
4 | 2689910.1138 | 1282938.2007 | 2689907.1258 | 1282930.3039
5 | 2689910.1138 | 1282938.2007 | 2689914.3949 | 1282930.248 | 2689920.1565 | 1282924.6755 | 2689960.1427 | 1282904.2338
6 | 2689925.5989 | 1282990.1708 | 2689932.8058 | 1282986.8112 | 2689934.8991 | 1282988.3889 | 2689938.8486 | 1282989.8616 | 2689946.3815 | 1282989.7431
7 | 2689925.5989 | 1282990.1708 | 2689915.5592 | 1282991.4035
8 | 2689907.1258 | 1282930.3039 | 2689905.9277 | 1282927.1384 | 2689903.9879 | 1282923.8615 | 2689901.418 | 1282922.0207
9 | 2689960.1427 | 1282904.2338 | 2689960.1803 | 1282904.2146
10 | 2689946.7633 | 1282993.7524 | 2689946.3815 | 1282989.7431
11 | 2689946.3815 | 1282989.7431 | 2689947.4945 | 1282989.6266 | 2689955.0184 | 1282988.8288
12 | 2689905.9424 | 1282992.5842 | 2689915.5592 | 1282991.4035
13 | 2689948.3052 | 1283005.3749 | 2689947.7611 | 1283004.1321 | 2689946.7633 | 1282993.7524
14 | 2689955.0184 | 1282988.8288 | 2689985.637 | 1282985.5819
15 | 2689884.5073 | 1282934.374 | 2689888.394 | 1282929.1839 | 2689892.4406 | 1282924.2969 | 2689895.1198 | 1282922.4139 | 2689898.0142 | 1282921.6908 | 2689901.418 | 1282922.0207
16 | 2689805.33 | 1282966.2113 | 2689806.0699 | 1282966.1168
17 | 2689806.0699 | 1282966.1168 | 2689830.8983 | 1282963.3148 | 2689840.7333 | 1282961.7099
18 | 2689763.293 | 1282968.0103 | 2689797.5161 | 1282967.2096 | 2689805.33 | 1282966.2113
19 | 2689840.7333 | 1282961.7099 | 2689843.6119 | 1282961.2401 | 2689855.3064 | 1282957.5485 | 2689864.7642 | 1282952.3326 | 2689873.8375 | 1282946.2323 | 2689880.8518 | 1282939.2554 | 2689884.5073 | 1282934.374
20 | 2689734.1944 | 1282990.0319 | 2689749.5592 | 1282989.9674
21 | 2689734.1944 | 1282990.0319 | 2689734.2737 | 1282991.2341 | 2689733.99 | 1283005.4199 | 2689730.5445 | 1283009.3041 | 2689726.9411 | 1283010.0513
22 | 2689734.1944 | 1282990.0319 | 2689719.3183 | 1282990.1826
23 | 2689760.7808 | 1282989.9204 | 2689749.5592 | 1282989.9674
24 | 2689927.2827 | 1283039.2279 | 2689932.7522 | 1283043.9265 | 2689947.3728 | 1283057.7027
25 | 2689909.7784 | 1283025.1042 | 2689927.2827 | 1283039.2279
26 | 2689927.2827 | 1283039.2279 | 2689924.0533 | 1283041.2471 | 2689915.3622 | 1283042.9716
27 | 2689909.7784 | 1283025.1042 | 2689896.8087 | 1283015.4314 | 2689894.3068 | 1283014.0107
28 | 2689909.7784 | 1283025.1042 | 2689914.3531 | 1283019.5581 | 2689918.4919 | 1283014.528
29 | 2689891.7857 | 1283035.1552 | 2689915.3622 | 1283042.9716
30 | 2689905.9424 | 1282992.5842 | 2689916.6397 | 1282999.6201 | 2689916.9782 | 1283004.4962 | 2689917.5109 | 1283011.8996 | 2689916.9479 | 1283013.3701 | 2689918.4919 | 1283014.528
31 | 2689918.4919 | 1283014.528 | 2689931.7162 | 1283025.7172 | 2689958.7151 | 1283053.2819
32 | 2689905.9424 | 1282992.5842 | 2689894.5124 | 1282991.2421
33 | 2689971.7375 | 1283066.038 | 2689965.0446 | 1283059.7441 | 2689958.7151 | 1283053.2819
34 | 2689870.1261 | 1283002.2781 | 2689881.5337 | 1283006.7576 | 2689894.3068 | 1283014.0107
35 | 2690156.4425 | 1282797.741 | 2690149.4646 | 1282802.3049 | 2690143.4493 | 1282803.8253 | 2690103.3222 | 1282827.4101
36 | 2690156.4425 | 1282797.741 | 2690123.146 | 1282784.1757 | 2690096.5368 | 1282776.87
37 | 2690103.3222 | 1282827.4101 | 2690081.499 | 1282840.0793
38 | 2690116.7952 | 1282850.3248 | 2690103.3222 | 1282827.4101
39 | 2689960.1803 | 1282904.2146 | 2689960.2135 | 1282904.1977
40 | 2689997.086 | 1282984.3678 | 2689985.637 | 1282985.5819
41 | 2689999.6643 | 1283011.2835 | 2690001.5476 | 1283030.943
42 | 2689999.6643 | 1283011.2835 | 2689999.6298 | 1283010.9234
43 | 2689997.086 | 1282984.3678 | 2689999.6298 | 1283010.9234
44 | 2689997.086 | 1282984.3678 | 2690010.2246 | 1282982.9737
45 | 2690017.4155 | 1282982.2107 | 2690010.2246 | 1282982.9737
46 | 2690017.4155 | 1282982.2107 | 2690031.3374 | 1282980.7335
47 | 2690038.5278 | 1282979.9705 | 2690031.3374 | 1282980.7335
48 | 2689874.638 | 1283030.8144 | 2689878.7934 | 1283030.8478 | 2689891.7857 | 1283035.1552
49 | 2689982.0308 | 1283075.7177 | 2689971.7375 | 1283066.038
50 | 2689760.7808 | 1282989.9204 | 2689783.4082 | 1282989.8255 | 2689816.4984 | 1282989.8073 | 2689830.0279 | 1282991.337 | 2689847.8813 | 1282994.901 | 2689862.9116 | 1282999.4452 | 2689870.1261 | 1283002.2781
51 | 2689763.293 | 1282968.0103 | 2689752.6141 | 1282968.2601 | 2689741.7727 | 1282970.6638 | 2689729.9901 | 1282970.4843
52 | 2690050.9875 | 1282857.7923 | 2690081.499 | 1282840.0793
53 | 2690116.7952 | 1282850.3248 | 2690131.3585 | 1282875.0911
54 | 2690116.7952 | 1282850.3248 | 2690102.2722 | 1282858.7011
55 | 2690116.7952 | 1282850.3248 | 2690128.2694 | 1282845.488
56 | 2689960.2135 | 1282904.1977 | 2689985.8105 | 1282891.112
57 | 2690020.8205 | 1282873.2143 | 2689985.8105 | 1282891.112
58 | 2690020.8205 | 1282873.2143 | 2690020.8567 | 1282873.1957
59 | 2690138.2354 | 1282841.287 | 2690128.2694 | 1282845.488
60 | 2690131.3585 | 1282875.0911 | 2690119.6219 | 1282881.9165
61 | 2690131.3585 | 1282875.0911 | 2690145.8124 | 1282901.1125
62 | 2690131.3585 | 1282875.0911 | 2690143.0041 | 1282870.5659
63 | 2690119.6219 | 1282881.9165 | 2690110.3478 | 1282887.3098
64 | 2690145.8124 | 1282901.1125 | 2690158.2128 | 1282895.8036
65 | 2690145.8124 | 1282901.1125 | 2690134.813 | 1282907.4568
66 | 2690145.8124 | 1282901.1125 | 2690151.1912 | 1282920.6624
67 | 2690153.075 | 1282866.6526 | 2690143.0041 | 1282870.5659
68 | 2690168.1554 | 1282891.547 | 2690158.2128 | 1282895.8036
69 | 2690134.813 | 1282907.4568 | 2690125.5221 | 1282912.8157
70 | 2690166.5524 | 1282925.1025 | 2690153.2881 | 1282928.2837 | 2690151.1912 | 1282920.6624
71 | 2690050.9875 | 1282857.7923 | 2690046.4913 | 1282860.0909
72 | 2690050.9875 | 1282857.7923 | 2690062.8631 | 1282877.7288
73 | 2690020.8567 | 1282873.1957 | 2690020.892 | 1282873.1777
74 | 2690046.4913 | 1282860.0909 | 2690020.892 | 1282873.1777
75 | 2689991.4389 | 1283084.565 | 2689982.0308 | 1283075.7177
76 | 2689991.4389 | 1283084.565 | 2689993.9738 | 1283086.9488
77 | 2690007.1438 | 1283099.3337 | 2689993.9738 | 1283086.9488
78 | 2690007.1438 | 1283099.3337 | 2690013.6507 | 1283105.4527
79 | 2690094.923 | 1282973.9866 | 2690103.9253 | 1282973.0345
80 | 2690103.9253 | 1282973.0345 | 2690118.8026 | 1282971.5589
81 | 2690094.923 | 1282973.9866 | 2690088.7703 | 1282974.6394
82 | 2690094.923 | 1282973.9866 | 2690095.1088 | 1282977.0588 | 2690095.5631 | 1282980.7356 | 2690097.654 | 1282994.0102
83 | 2690118.8026 | 1282971.5589 | 2690133.0155 | 1282970.1492
84 | 2690071.911 | 1282976.4283 | 2690088.7703 | 1282974.6394
85 | 2690140.6747 | 1282969.3896 | 2690133.0155 | 1282970.1492
86 | 2690071.911 | 1282976.4283 | 2690054.5881 | 1282978.2664
87 | 2690038.5278 | 1282979.9705 | 2690054.5881 | 1282978.2664
88 | 2690091.8756 | 1282926.5898 | 2690097.4801 | 1282936.7111
89 | 2690091.8756 | 1282926.5898 | 2690090.5269 | 1282924.154 | 2690090.1181 | 1282923.4676
90 | 2690081.0267 | 1282908.2012 | 2690090.1181 | 1282923.4676
91 | 2690078.3161 | 1282903.6496 | 2690081.0267 | 1282908.2012
92 | 2690065.08 | 1282881.4504 | 2690078.3161 | 1282903.6496
93 | 2690078.3161 | 1282903.6496 | 2690068.541 | 1282908.5411
94 | 2690177.0666 | 1282922.5809 | 2690166.5524 | 1282925.1025
95 | 2689729.9901 | 1282970.4843 | 2689714.1617 | 1282970.2432
96 | 2690065.08 | 1282881.4504 | 2690054.6289 | 1282886.7157
97 | 2690065.08 | 1282881.4504 | 2690062.8631 | 1282877.7288
98 | 2690068.541 | 1282908.5411 | 2690067.5839 | 1282909.02
99 | 2690047.981 | 1282890.065 | 2690054.6289 | 1282886.7157
100 | 2690060.9282 | 1282912.3505 | 2690067.5839 | 1282909.02
101 | 2689837.2058 | 1283030.5132 | 2689835.5951 | 1283030.5002 | 2689820.4405 | 1283032.8888
102 | 2689837.2058 | 1283030.5132 | 2689839.2166 | 1283030.5293
103 | 2689795.5163 | 1283036.8173 | 2689820.4405 | 1283032.8888
104 | 2689839.2166 | 1283030.5293 | 2689854.4554 | 1283030.652
105 | 2689795.5163 | 1283036.8173 | 2689765.1182 | 1283041.6051
106 | 2689795.5163 | 1283036.8173 | 2689795.0845 | 1283024.3944
107 | 2689874.638 | 1283030.8144 | 2689854.4554 | 1283030.652
108 | 2689757.0399 | 1283042.8775 | 2689765.1182 | 1283041.6051
109 | 2689795.0845 | 1283024.3944 | 2689795.0371 | 1283023.0311
110 | 2689794.5977 | 1283010.3915 | 2689794.5977 | 1283010.3915 | 2689795.0371 | 1283023.0311
111 | 2689794.5977 | 1283010.3915 | 2689804.4995 | 1283010.0198 | 2689805.8332 | 1283008.7279 | 2689814.2161 | 1283008.3653
112 | 2690047.981 | 1282890.065 | 2690035.5533 | 1282896.3262
113 | 2690047.4888 | 1282919.0755 | 2690060.9282 | 1282912.3505
114 | 2690028.9064 | 1282899.675 | 2690035.5533 | 1282896.3262
115 | 2690047.4635 | 1282919.0882 | 2690047.4888 | 1282919.0755
116 | 2690041.272 | 1282922.1864 | 2690047.4635 | 1282919.0882
117 | 2690040.8091 | 1282922.4181 | 2690041.272 | 1282922.1864

## bus_geodata
| x | y | coords
0 | 2689985.1191 | 1282945.4975
1 | 2689922.6546 | 1282959.744
2 | 2690009.9885 | 1282932.0973
3 | 2689910.1138 | 1282938.2007
4 | 2689925.5989 | 1282990.1708
5 | 2689907.1258 | 1282930.3039
6 | 2689960.1427 | 1282904.2338
7 | 2689946.3815 | 1282989.7431
8 | 2689915.5592 | 1282991.4035
9 | 2689946.7633 | 1282993.7524
10 | 2689955.0184 | 1282988.8288
11 | 2689901.418 | 1282922.0207
12 | 2689806.0699 | 1282966.1168
13 | 2689805.33 | 1282966.2113
14 | 2689840.7333 | 1282961.7099
15 | 2689734.1944 | 1282990.0319
16 | 2689749.5591 | 1282989.9674
17 | 2689726.9411 | 1283010.0513
18 | 2689719.3183 | 1282990.1826
19 | 2689927.2827 | 1283039.2279
20 | 2689947.3728 | 1283057.7027
21 | 2689909.7784 | 1283025.1042
22 | 2689915.3622 | 1283042.9716
23 | 2689918.4919 | 1283014.528
24 | 2689905.9424 | 1282992.5842
25 | 2689958.7151 | 1283053.2819
26 | 2689894.3068 | 1283014.0107
27 | 2690156.4425 | 1282797.741
28 | 2690103.3222 | 1282827.4101
29 | 2690096.5368 | 1282776.87
30 | 2689960.1803 | 1282904.2146
31 | 2689948.3052 | 1283005.3749
32 | 2689894.5124 | 1282991.2421
33 | 2689985.637 | 1282985.5819
34 | 2689999.6643 | 1283011.2835
35 | 2690001.5476 | 1283030.943
36 | 2689999.6298 | 1283010.9234
37 | 2689997.086 | 1282984.3678
38 | 2690010.2246 | 1282982.9737
39 | 2690017.4155 | 1282982.2107
40 | 2690031.3374 | 1282980.7335
41 | 2689891.7857 | 1283035.1552
42 | 2689971.7375 | 1283066.038
43 | 2689870.1261 | 1283002.2781
44 | 2689760.7808 | 1282989.9204
45 | 2689763.293 | 1282968.0103
46 | 2689884.5073 | 1282934.374
47 | 2690081.499 | 1282840.0793
48 | 2690116.7952 | 1282850.3248
49 | 2689960.2135 | 1282904.1977
50 | 2689985.8105 | 1282891.112
51 | 2690020.8205 | 1282873.2143
52 | 2690128.2694 | 1282845.488
53 | 2690138.2354 | 1282841.287
54 | 2690131.3585 | 1282875.0911
55 | 2690102.2722 | 1282858.7011
56 | 2690119.6219 | 1282881.9165
57 | 2690145.8124 | 1282901.1125
58 | 2690143.0041 | 1282870.5659
59 | 2690110.3478 | 1282887.3098
60 | 2690158.2128 | 1282895.8036
61 | 2690134.813 | 1282907.4568
62 | 2690151.1912 | 1282920.6624
63 | 2690153.075 | 1282866.6526
64 | 2690050.9875 | 1282857.7923
65 | 2690020.8567 | 1282873.1957
66 | 2690020.892 | 1282873.1777
67 | 2690046.4913 | 1282860.0909
68 | 2689982.0308 | 1283075.7177
69 | 2689991.4389 | 1283084.565
70 | 2689993.9738 | 1283086.9488
71 | 2690007.1438 | 1283099.3337
72 | 2690013.6507 | 1283105.4527
73 | 2690103.9253 | 1282973.0345
74 | 2690094.923 | 1282973.9866
75 | 2690118.8026 | 1282971.5589
76 | 2690088.7703 | 1282974.6394
77 | 2690097.654 | 1282994.0102
78 | 2690133.0155 | 1282970.1492
79 | 2690071.911 | 1282976.4283
80 | 2690054.5881 | 1282978.2664
81 | 2690140.6747 | 1282969.3896
82 | 2690038.5278 | 1282979.9705
83 | 2690097.4801 | 1282936.7111
84 | 2690091.8756 | 1282926.5898
85 | 2690090.1181 | 1282923.4676
86 | 2690081.0267 | 1282908.2012
87 | 2690078.3161 | 1282903.6496
88 | 2690166.5524 | 1282925.1025
89 | 2690177.0666 | 1282922.5809
90 | 2690168.1554 | 1282891.547
91 | 2690125.5221 | 1282912.8157
92 | 2689729.9902 | 1282970.4843
93 | 2689714.1617 | 1282970.2432
94 | 2690065.08 | 1282881.4504
95 | 2690068.541 | 1282908.5411
96 | 2690054.6289 | 1282886.7157
97 | 2690062.8631 | 1282877.7288
98 | 2690067.5839 | 1282909.02
99 | 2689837.2058 | 1283030.5132
100 | 2689820.4405 | 1283032.8888
101 | 2689839.2166 | 1283030.5293
102 | 2689795.5163 | 1283036.8173
103 | 2689854.4554 | 1283030.652
104 | 2689765.1182 | 1283041.6051
105 | 2689795.0845 | 1283024.3944
106 | 2689874.638 | 1283030.8144
107 | 2689757.0399 | 1283042.8775
108 | 2689795.0371 | 1283023.0311
109 | 2689794.5977 | 1283010.3915
110 | 2689814.2161 | 1283008.3653
111 | 2690047.981 | 1282890.065
112 | 2690060.9282 | 1282912.3505
113 | 2690035.5533 | 1282896.3262
114 | 2690047.4888 | 1282919.0755
115 | 2690047.4635 | 1282919.0882
116 | 2690041.272 | 1282922.1864
117 | 2690040.8091 | 1282922.4181
118 | 2690028.9064 | 1282899.675
119 | 2689910.1138 | 1282938.2007

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99923 | -0.014878 | 0.011359 | 0.0028469
1 | 1 | 0 | -0.30924 | -0.078143
2 | 0.99918 | -0.015743 | 0.0017527 | 0.00043926
3 | 0.99792 | -0.039493 | 0 | 0
4 | 0.99614 | -0.073922 | 0 | 0
5 | 0.99726 | -0.05221 | 0 | 0
6 | 0.9927 | -0.13926 | 0.0021833 | 0.00054719
7 | 0.99532 | -0.089728 | 0 | 0
8 | 0.99545 | -0.087065 | 0.0011579 | 0.00029021
9 | 0.99529 | -0.090193 | 0 | 0
10 | 0.99505 | -0.094884 | 0.0024054 | 0.00060284
11 | 0.99644 | -0.067835 | 0.0044008 | 0.0011029
12 | 0.99037 | -0.18498 | 0 | 0
13 | 0.99034 | -0.18554 | 0.019227 | 0.0048186
14 | 0.99175 | -0.15835 | 0.019333 | 0.0048453
15 | 0.99049 | -0.18295 | 0 | 0
16 | 0.99053 | -0.18223 | 0.0046939 | 0.0011764
17 | 0.99047 | -0.18336 | 0.00093806 | 0.0002351
18 | 0.99047 | -0.1834 | 0.0016977 | 0.00042549
19 | 0.99185 | -0.15657 | 0 | 0
20 | 0.99168 | -0.15992 | 0.0069289 | 0.0017365
21 | 0.99247 | -0.14458 | 0 | 0
22 | 0.99158 | -0.16178 | 0.004002 | 0.001003
23 | 0.99306 | -0.13331 | 0 | 0
24 | 0.99481 | -0.099474 | 0 | 0
25 | 0.99201 | -0.15358 | 0.0034307 | 0.00085982
26 | 0.99219 | -0.1501 | 0.0017956 | 0.00045003
27 | 0.983 | -0.32718 | 0 | 0
28 | 0.98335 | -0.32043 | 0 | 0
29 | 0.98264 | -0.33422 | 0.0061394 | 0.0015387
30 | 0.9927 | -0.13933 | 0.0021901 | 0.00054889
31 | 0.99522 | -0.09155 | 0.0065494 | 0.0016414
32 | 0.99475 | -0.10064 | 0.0057499 | 0.0014411
33 | 0.99417 | -0.11188 | 0.0023748 | 0.00059518
34 | 0.99357 | -0.12347 | 0.0065493 | 0.0016414
35 | 0.99355 | -0.12393 | 0.0013092 | 0.00032811
36 | 0.99357 | -0.12342 | 0.0041755 | 0.0010465
37 | 0.99387 | -0.11776 | 0 | 0
38 | 0.99366 | -0.1217 | 0.00081378 | 0.00020395
39 | 0.99356 | -0.12376 | 0.00081327 | 0.00020383
40 | 0.99336 | -0.12754 | 0.00081324 | 0.00020382
41 | 0.99115 | -0.17025 | 0.001727 | 0.00043281
42 | 0.99172 | -0.15909 | 0.0031791 | 0.00079675
43 | 0.99183 | -0.15706 | 0.0025238 | 0.00063253
44 | 0.99061 | -0.18077 | 0.0047113 | 0.0011808
45 | 0.98943 | -0.2033 | 0.01576 | 0.0039498
46 | 0.99476 | -0.10014 | 0.019365 | 0.0048533
47 | 0.98409 | -0.30584 | 0.0065429 | 0.0016398
48 | 0.98271 | -0.33286 | 0 | 0
49 | 0.99269 | -0.13939 | 0.0021842 | 0.00054741
50 | 0.99044 | -0.18269 | 0.0059602 | 0.0014938
51 | 0.98758 | -0.23804 | 0.0022475 | 0.00056327
52 | 0.98268 | -0.33351 | 0.0014314 | 0.00035874
53 | 0.98266 | -0.33379 | 0.0014331 | 0.00035918
54 | 0.9822 | -0.34277 | 0 | 0
55 | 0.98265 | -0.33407 | 0.0039764 | 0.00099658
56 | 0.98217 | -0.34347 | 0.0014335 | 0.00035926
57 | 0.98184 | -0.34996 | 0 | 0
58 | 0.98217 | -0.34341 | 0.001432 | 0.0003589
59 | 0.98215 | -0.34375 | 0.0014312 | 0.0003587
60 | 0.9818 | -0.35066 | 0.0014322 | 0.00035893
61 | 0.98179 | -0.35079 | 0.0014328 | 0.0003591
62 | 0.98171 | -0.35248 | 0.002468 | 0.00061854
63 | 0.98216 | -0.34369 | 0.0014325 | 0.00035901
64 | 0.98535 | -0.28134 | 0 | 0
65 | 0.98758 | -0.2381 | 0.0022545 | 0.00056504
66 | 0.98757 | -0.23815 | 0.0022475 | 0.00056328
67 | 0.98566 | -0.27535 | 0.0061383 | 0.0015384
68 | 0.99154 | -0.16257 | 0.0048147 | 0.0012067
69 | 0.99144 | -0.16464 | 0.0026399 | 0.00066163
70 | 0.99142 | -0.16504 | 0.0021249 | 0.00053255
71 | 0.99135 | -0.16642 | 0.0019221 | 0.00048172
72 | 0.99133 | -0.1668 | 0.0023781 | 0.00059602
73 | 0.99262 | -0.14179 | 0.0020435 | 0.00051215
74 | 0.99268 | -0.14075 | 0 | 0
75 | 0.99256 | -0.14299 | 0.0019759 | 0.00049521
76 | 0.99272 | -0.13985 | 0.0018388 | 0.00046085
77 | 0.99265 | -0.14131 | 0.001574 | 0.00039448
78 | 0.99253 | -0.14364 | 0.0012657 | 0.00031722
79 | 0.99288 | -0.13686 | 0.0016382 | 0.00041058
80 | 0.99306 | -0.13328 | 0.0020351 | 0.00051005
81 | 0.99252 | -0.14381 | 0.0012836 | 0.0003217
82 | 0.99327 | -0.12938 | 0.00081318 | 0.0002038
83 | 0.98411 | -0.30545 | 0.0024228 | 0.00060722
84 | 0.98414 | -0.30495 | 0.0012738 | 0.00031925
85 | 0.98415 | -0.30471 | 0.0012748 | 0.00031951
86 | 0.98423 | -0.30312 | 0.0030868 | 0.00077363
87 | 0.98427 | -0.30235 | 0 | 0
88 | 0.98162 | -0.3542 | 0.0022005 | 0.00055149
89 | 0.9816 | -0.35463 | 0.0022037 | 0.0005523
90 | 0.98179 | -0.35094 | 0.0014331 | 0.00035917
91 | 0.98177 | -0.35122 | 0.0022017 | 0.00055179
92 | 0.98918 | -0.20805 | 0.0039736 | 0.00099588
93 | 0.98913 | -0.20917 | 0.0039722 | 0.00099554
94 | 0.98467 | -0.29461 | 0 | 0
95 | 0.98419 | -0.30404 | 0.00095131 | 0.00023842
96 | 0.9846 | -0.29602 | 0.0016731 | 0.00041932
97 | 0.98476 | -0.2928 | 0.0041219 | 0.001033
98 | 0.98418 | -0.30419 | 0.0012754 | 0.00031965
99 | 0.99036 | -0.18547 | 0.004121 | 0.0010328
100 | 0.99025 | -0.18772 | 0.0016835 | 0.00042192
101 | 0.99038 | -0.18505 | 0.0017503 | 0.00043866
102 | 0.99011 | -0.19032 | 0 | 0
103 | 0.99057 | -0.18144 | 0.0024293 | 0.00060884
104 | 0.99009 | -0.19078 | 0.00050045 | 0.00012543
105 | 0.99006 | -0.19141 | 0.0012512 | 0.00031359
106 | 0.99086 | -0.17578 | 0.0017121 | 0.00042908
107 | 0.99009 | -0.19083 | 0.00033696 | 8.445e-05
108 | 0.99005 | -0.1915 | 0.00081789 | 0.00020498
109 | 0.99002 | -0.19215 | 0.00081789 | 0.00020498
110 | 0.98998 | -0.19289 | 0.002064 | 0.00051729
111 | 0.98456 | -0.2967 | 0.001673 | 0.0004193
112 | 0.98414 | -0.30504 | 0.0012745 | 0.00031941
113 | 0.98452 | -0.29753 | 0.0016746 | 0.00041968
114 | 0.98407 | -0.30642 | 0.0012744 | 0.0003194
115 | 0.98407 | -0.30643 | 0.0012744 | 0.0003194
116 | 0.98405 | -0.30674 | 0.0012742 | 0.00031933
117 | 0.98405 | -0.30675 | 0.0012751 | 0.00031958
118 | 0.98451 | -0.29776 | 0.001673 | 0.0004193
119 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.013112 | -0.0032858 | 0.013121 | 0.0032909 | 9.2991e-06 | 5.0988e-06 | 0.019526 | 0.019525 | 0.019526 | 0.99923 | -0.014878 | 1 | 0 | 5.3642
1 | 0.0017527 | 0.00043893 | -0.0017527 | -0.00043926 | 7.2168e-08 | -3.2384e-07 | 0.00261 | 0.0026101 | 0.0026101 | 0.99923 | -0.014878 | 0.99918 | -0.015743 | 0.71706
2 | 0.17948 | 0.045726 | -0.17914 | -0.045509 | 0.00034127 | 0.00021775 | 0.26733 | 0.26733 | 0.26733 | 1 | 0 | 0.99792 | -0.039493 | 36.7217
3 | 0.11499 | 0.029125 | -0.11458 | -0.028865 | 0.00040667 | 0.00025979 | 0.17122 | 0.17122 | 0.17122 | 1 | 0 | 0.99614 | -0.073922 | 47.0375
4 | 0.086527 | 0.021876 | -0.086474 | -0.021842 | 5.2741e-05 | 3.3644e-05 | 0.12909 | 0.12909 | 0.12909 | 0.99792 | -0.039493 | 0.99726 | -0.05221 | 35.4638
5 | 0.092613 | 0.023633 | -0.092169 | -0.02335 | 0.00044404 | 0.00028338 | 0.13825 | 0.13825 | 0.13825 | 0.99792 | -0.039493 | 0.9927 | -0.13926 | 37.9797
6 | 0.040364 | 0.010148 | -0.040333 | -0.010129 | 3.0443e-05 | 1.9193e-05 | 0.060306 | 0.060306 | 0.060306 | 0.99614 | -0.073922 | 0.99532 | -0.089728 | 16.5676
7 | 0.074221 | 0.018717 | -0.074174 | -0.018688 | 4.666e-05 | 2.9731e-05 | 0.11091 | 0.11091 | 0.11091 | 0.99614 | -0.073922 | 0.99545 | -0.087065 | 30.4699
8 | 0.086474 | 0.021842 | -0.086409 | -0.021801 | 6.4699e-05 | 4.1273e-05 | 0.12909 | 0.12909 | 0.12909 | 0.99726 | -0.05221 | 0.99644 | -0.067835 | 35.4638
9 | 0.089986 | 0.022802 | -0.089985 | -0.022802 | 2.8815e-07 | 1.8387e-07 | 0.13497 | 0.13497 | 0.13497 | 0.9927 | -0.13926 | 0.9927 | -0.13933 | 37.0806
10 | 0.0065499 | 0.0016416 | -0.0065498 | -0.0016415 | 1.448e-07 | 4.0338e-08 | 0.0097923 | 0.0097923 | 0.0097923 | 0.99532 | -0.089728 | 0.99529 | -0.090193 | 2.6902
11 | 0.033783 | 0.0084873 | -0.033775 | -0.008482 | 8.3106e-06 | 5.2059e-06 | 0.050514 | 0.050514 | 0.050514 | 0.99532 | -0.089728 | 0.99505 | -0.094884 | 13.8775
12 | 0.073016 | 0.018397 | -0.072973 | -0.01837 | 4.3311e-05 | 2.7593e-05 | 0.10918 | 0.10918 | 0.10918 | 0.99545 | -0.087065 | 0.99481 | -0.099474 | 29.9944
13 | 0.0065498 | 0.0016415 | -0.0065494 | -0.0016414 | 4.237e-07 | 1.1805e-07 | 0.0097923 | 0.0097924 | 0.0097924 | 0.99529 | -0.090193 | 0.99522 | -0.09155 | 2.6902
14 | 0.03137 | 0.0078792 | -0.031344 | -0.0078633 | 2.5416e-05 | 1.5867e-05 | 0.046917 | 0.046917 | 0.046917 | 0.99505 | -0.094884 | 0.99417 | -0.11188 | 12.8893
15 | 0.082008 | 0.020698 | -0.081882 | -0.020617 | 0.00012669 | 8.0788e-05 | 0.12252 | 0.12252 | 0.12252 | 0.99644 | -0.067835 | 0.99476 | -0.10014 | 33.6584
16 | 0.042956 | 0.010774 | -0.042954 | -0.010773 | 1.1654e-06 | 7.3623e-07 | 0.064543 | 0.064543 | 0.064543 | 0.99037 | -0.18498 | 0.99034 | -0.18554 | 17.7315
17 | -0.042956 | -0.010774 | 0.04301 | 0.010808 | 5.4599e-05 | 3.4493e-05 | 0.064543 | 0.064543 | 0.064543 | 0.99037 | -0.18498 | 0.99175 | -0.15835 | 17.7315
18 | 0.023728 | 0.0059542 | -0.023708 | -0.0059419 | 2.0074e-05 | 1.2306e-05 | 0.035654 | 0.035654 | 0.035654 | 0.99034 | -0.18554 | 0.98943 | -0.2033 | 9.7952
19 | -0.062343 | -0.015653 | 0.062517 | 0.015764 | 0.00017363 | 0.00011044 | 0.09355 | 0.093549 | 0.09355 | 0.99175 | -0.15835 | 0.99476 | -0.10014 | 25.7005
20 | -0.0026358 | -0.00066012 | 0.0026359 | 0.00065998 | 9.0337e-08 | -1.3995e-07 | 0.0039596 | 0.0039596 | 0.0039596 | 0.99049 | -0.18295 | 0.99053 | -0.18223 | 1.0878
21 | 0.00093808 | 0.0002348 | -0.00093806 | -0.0002351 | 1.8071e-08 | -3.0075e-07 | 0.0014092 | 0.0014093 | 0.0014093 | 0.99049 | -0.18295 | 0.99047 | -0.18336 | 0.38716
22 | 0.0016978 | 0.00042532 | -0.0016977 | -0.00042549 | 3.6291e-08 | -1.6825e-07 | 0.0025505 | 0.0025505 | 0.0025505 | 0.99049 | -0.18295 | 0.99047 | -0.1834 | 0.7007
23 | -0.0073298 | -0.0018364 | 0.0073303 | 0.0018366 | 5.1019e-07 | 1.8207e-07 | 0.011011 | 0.011011 | 0.011011 | 0.99053 | -0.18223 | 0.99061 | -0.18077 | 3.025
24 | 0.00693 | 0.0017369 | -0.0069289 | -0.0017365 | 1.1066e-06 | 3.5592e-07 | 0.010397 | 0.010397 | 0.010397 | 0.99185 | -0.15657 | 0.99168 | -0.15992 | 2.8563
25 | -0.03017 | -0.0075691 | 0.030188 | 0.0075799 | 1.7249e-05 | 1.0749e-05 | 0.045265 | 0.045265 | 0.045265 | 0.99185 | -0.15657 | 0.99247 | -0.14458 | 12.4355
26 | 0.02324 | 0.0058322 | -0.023235 | -0.0058287 | 5.7763e-06 | 3.5334e-06 | 0.034869 | 0.034869 | 0.034869 | 0.99185 | -0.15657 | 0.99158 | -0.16178 | 9.5793
27 | 0.016384 | 0.0041124 | -0.016379 | -0.0041099 | 4.3128e-06 | 2.514e-06 | 0.024566 | 0.024567 | 0.024567 | 0.99247 | -0.14458 | 0.99219 | -0.1501 | 6.7491
28 | -0.046571 | -0.011692 | 0.046596 | 0.011708 | 2.5059e-05 | 1.5861e-05 | 0.069832 | 0.069832 | 0.069832 | 0.99247 | -0.14458 | 0.99306 | -0.13331 | 19.1845
29 | 0.019233 | 0.0048257 | -0.019225 | -0.004821 | 7.7597e-06 | 4.6459e-06 | 0.028863 | 0.028863 | 0.028863 | 0.99158 | -0.16178 | 0.99115 | -0.17025 | 7.9295
30 | -0.067114 | -0.016859 | 0.067222 | 0.016929 | 0.00010857 | 6.9111e-05 | 0.10058 | 0.10058 | 0.10058 | 0.99306 | -0.13331 | 0.99481 | -0.099474 | 27.6315
31 | 0.020517 | 0.0051513 | -0.020498 | -0.0051394 | 1.982e-05 | 1.1962e-05 | 0.030747 | 0.030747 | 0.030747 | 0.99306 | -0.13331 | 0.99201 | -0.15358 | 8.4471
32 | 0.0057503 | 0.0014411 | -0.0057499 | -0.0014411 | 3.1927e-07 | 5.4924e-08 | 0.0086011 | 0.0086012 | 0.0086012 | 0.99481 | -0.099474 | 0.99475 | -0.10064 | 2.363
33 | 0.017067 | 0.0042796 | -0.017062 | -0.0042769 | 4.4814e-06 | 2.6328e-06 | 0.025601 | 0.025601 | 0.025601 | 0.99201 | -0.15358 | 0.99172 | -0.15909 | 7.0333
34 | 0.014584 | 0.0036599 | -0.014579 | -0.0036571 | 4.8344e-06 | 2.7462e-06 | 0.021874 | 0.021874 | 0.021874 | 0.99219 | -0.1501 | 0.99183 | -0.15706 | 6.0093
35 | -0.0061415 | -0.0015392 | 0.0061435 | 0.0015397 | 1.9754e-06 | 4.913e-07 | 0.0092967 | 0.0092964 | 0.0092967 | 0.983 | -0.32718 | 0.98335 | -0.32043 | 2.554
36 | 0.0061415 | 0.0015392 | -0.0061394 | -0.0015387 | 2.0597e-06 | 5.129e-07 | 0.0092967 | 0.009297 | 0.009297 | 0.983 | -0.32718 | 0.98264 | -0.33422 | 2.5541
37 | -0.032117 | -0.0080578 | 0.032139 | 0.0080718 | 2.2353e-05 | 1.3986e-05 | 0.048602 | 0.048602 | 0.048602 | 0.98335 | -0.32043 | 0.98409 | -0.30584 | 13.3523
38 | 0.025973 | 0.0065181 | -0.025958 | -0.0065086 | 1.5388e-05 | 9.5116e-06 | 0.039306 | 0.039306 | 0.039306 | 0.98335 | -0.32043 | 0.98271 | -0.33286 | 10.7984
39 | 0.087795 | 0.022253 | -0.087795 | -0.022253 | 2.4247e-07 | 1.547e-07 | 0.13169 | 0.13169 | 0.13169 | 0.9927 | -0.13933 | 0.99269 | -0.13939 | 36.1788
40 | 0.02897 | 0.0072682 | -0.028961 | -0.0072631 | 8.1182e-06 | 5.0464e-06 | 0.043363 | 0.043363 | 0.043363 | 0.99417 | -0.11188 | 0.99387 | -0.11776 | 11.9128
41 | 0.0013092 | 0.00032787 | -0.0013092 | -0.00032811 | 2.8471e-08 | -2.3755e-07 | 0.0019606 | 0.0019607 | 0.0019607 | 0.99357 | -0.12347 | 0.99355 | -0.12393 | 0.53866
42 | -0.0078585 | -0.0019693 | 0.0078585 | 0.0019693 | 1.8793e-08 | 7.3414e-09 | 0.011769 | 0.011769 | 0.011769 | 0.99357 | -0.12347 | 0.99357 | -0.12342 | 3.2333
43 | -0.012034 | -0.0030157 | 0.012037 | 0.0030175 | 3.2493e-06 | 1.734e-06 | 0.018022 | 0.018022 | 0.018022 | 0.99357 | -0.12342 | 0.99387 | -0.11776 | 4.9512
44 | 0.016924 | 0.0042456 | -0.016921 | -0.0042438 | 3.1816e-06 | 1.865e-06 | 0.02534 | 0.02534 | 0.02534 | 0.99387 | -0.11776 | 0.99366 | -0.1217 | 6.9617
45 | 0.016107 | 0.0040398 | -0.016106 | -0.0040389 | 1.5778e-06 | 9.1616e-07 | 0.024122 | 0.024122 | 0.024122 | 0.99366 | -0.1217 | 0.99356 | -0.12376 | 6.6269
46 | 0.015292 | 0.0038351 | -0.01529 | -0.0038335 | 2.7541e-06 | 1.5813e-06 | 0.022904 | 0.022904 | 0.022904 | 0.99356 | -0.12376 | 0.99336 | -0.12754 | 6.2923
47 | 0.014476 | 0.0036297 | -0.014475 | -0.003629 | 1.2752e-06 | 7.225e-07 | 0.021686 | 0.021686 | 0.021686 | 0.99336 | -0.12754 | 0.99327 | -0.12938 | 5.9576
48 | 0.017498 | 0.0043882 | -0.017493 | -0.0043855 | 4.6179e-06 | 2.7256e-06 | 0.026271 | 0.026271 | 0.026271 | 0.99115 | -0.17025 | 0.99086 | -0.17578 | 7.2172
49 | 0.013883 | 0.0034802 | -0.013881 | -0.0034789 | 2.2993e-06 | 1.2893e-06 | 0.020831 | 0.020831 | 0.020831 | 0.99172 | -0.15909 | 0.99154 | -0.16257 | 5.7229
50 | 0.012055 | 0.0030246 | -0.012042 | -0.0030173 | 1.3617e-05 | 7.2842e-06 | 0.018087 | 0.018088 | 0.018088 | 0.99183 | -0.15706 | 0.99061 | -0.18077 | 4.9692
51 | 0.0079478 | 0.0019921 | -0.007946 | -0.0019913 | 1.7986e-06 | 7.2007e-07 | 0.011953 | 0.011953 | 0.011953 | 0.98943 | -0.2033 | 0.98918 | -0.20805 | 3.2838
52 | -0.038682 | -0.0097116 | 0.038727 | 0.0097401 | 4.527e-05 | 2.8524e-05 | 0.058496 | 0.058496 | 0.058496 | 0.98409 | -0.30584 | 0.98535 | -0.28134 | 16.0702
53 | 0.019116 | 0.0047944 | -0.019107 | -0.004789 | 9.0207e-06 | 5.4097e-06 | 0.028947 | 0.028947 | 0.028947 | 0.98271 | -0.33286 | 0.9822 | -0.34277 | 7.9526
54 | 0.0039766 | 0.00099651 | -0.0039764 | -0.00099658 | 2.2795e-07 | -6.6509e-08 | 0.0060213 | 0.0060214 | 0.0060214 | 0.98271 | -0.33286 | 0.98265 | -0.33407 | 1.6542
55 | 0.0028646 | 0.00071769 | -0.0028645 | -0.00071779 | 8.7853e-08 | -1.0153e-07 | 0.0043375 | 0.0043376 | 0.0043376 | 0.98271 | -0.33286 | 0.98268 | -0.33351 | 1.1916
56 | 0.085611 | 0.021706 | -0.085433 | -0.021592 | 0.00017778 | 0.00011341 | 0.12842 | 0.12842 | 0.12842 | 0.99269 | -0.13939 | 0.99044 | -0.18269 | 35.2793
57 | 0.079473 | 0.020099 | -0.079262 | -0.019964 | 0.00021043 | 0.00013417 | 0.11946 | 0.11946 | 0.11946 | 0.99044 | -0.18269 | 0.98758 | -0.23804 | 32.8194
58 | 0.077015 | 0.019401 | -0.077015 | -0.019401 | 2.0562e-07 | 1.3108e-07 | 0.11608 | 0.11608 | 0.11608 | 0.98758 | -0.23804 | 0.98758 | -0.2381 | 31.8891
59 | 0.0014331 | 0.00035905 | -0.0014331 | -0.00035918 | 1.91e-08 | -1.2479e-07 | 0.0021701 | 0.0021701 | 0.0021701 | 0.98268 | -0.33351 | 0.98266 | -0.33379 | 0.59619
60 | 0.0028648 | 0.00071772 | -0.0028647 | -0.00071783 | 9.59e-08 | -1.1045e-07 | 0.00434 | 0.0043401 | 0.0043401 | 0.9822 | -0.34277 | 0.98217 | -0.34347 | 1.1923
61 | 0.013378 | 0.0033536 | -0.013374 | -0.003351 | 4.5819e-06 | 2.5561e-06 | 0.020268 | 0.020268 | 0.020268 | 0.9822 | -0.34277 | 0.98184 | -0.34996 | 5.5681
62 | 0.0028646 | 0.00071768 | -0.0028645 | -0.00071778 | 8.8238e-08 | -1.0165e-07 | 0.0043397 | 0.0043398 | 0.0043398 | 0.9822 | -0.34277 | 0.98217 | -0.34341 | 1.1922
63 | 0.0014312 | 0.00035857 | -0.0014312 | -0.0003587 | 1.8916e-08 | -1.2366e-07 | 0.0021683 | 0.0021684 | 0.0021684 | 0.98217 | -0.34347 | 0.98215 | -0.34375 | 0.59571
64 | 0.0028654 | 0.00071787 | -0.0028653 | -0.00071798 | 9.5391e-08 | -1.0954e-07 | 0.0043425 | 0.0043426 | 0.0043426 | 0.98184 | -0.34996 | 0.9818 | -0.35066 | 1.193
65 | 0.0036347 | 0.00091071 | -0.0036345 | -0.00091078 | 1.4449e-07 | -6.8113e-08 | 0.0055084 | 0.0055085 | 0.0055085 | 0.98184 | -0.34996 | 0.98179 | -0.35079 | 1.5133
66 | 0.0068734 | 0.0017225 | -0.0068726 | -0.0017222 | 8.251e-07 | 2.7166e-07 | 0.010417 | 0.010417 | 0.010417 | 0.98184 | -0.34996 | 0.98171 | -0.35248 | 2.8618
67 | 0.0014325 | 0.00035888 | -0.0014325 | -0.00035901 | 1.9083e-08 | -1.2452e-07 | 0.0021702 | 0.0021702 | 0.0021702 | 0.98217 | -0.34341 | 0.98216 | -0.34369 | 0.59622
68 | 0.0014331 | 0.00035905 | -0.0014331 | -0.00035917 | 1.9134e-08 | -1.2452e-07 | 0.002172 | 0.0021721 | 0.0021721 | 0.9818 | -0.35066 | 0.98179 | -0.35094 | 0.59672
69 | 0.0022017 | 0.00055168 | -0.0022017 | -0.00055179 | 4.4786e-08 | -1.0697e-07 | 0.0033369 | 0.0033369 | 0.0033369 | 0.98179 | -0.35079 | 0.98177 | -0.35122 | 0.91674
70 | 0.0044046 | 0.0011036 | -0.0044042 | -0.0011037 | 3.6011e-07 | -4.1914e-08 | 0.0066761 | 0.0066762 | 0.0066762 | 0.98171 | -0.35248 | 0.98162 | -0.3542 | 1.8341
71 | -0.066226 | -0.01664 | 0.066245 | 0.016652 | 1.8946e-05 | 1.2061e-05 | 0.10003 | 0.10003 | 0.10003 | 0.98535 | -0.28134 | 0.98566 | -0.27535 | 27.4797
72 | 0.027499 | 0.0068999 | -0.027484 | -0.0068906 | 1.5009e-05 | 9.3105e-06 | 0.041531 | 0.041531 | 0.041531 | 0.98535 | -0.28134 | 0.98476 | -0.2928 | 11.4096
73 | 0.07476 | 0.018836 | -0.07476 | -0.018836 | 1.8863e-07 | 1.2021e-07 | 0.11268 | 0.11268 | 0.11268 | 0.98758 | -0.2381 | 0.98757 | -0.23815 | 30.9558
74 | 0.072513 | 0.018273 | -0.072384 | -0.018191 | 0.00012878 | 8.2054e-05 | 0.10929 | 0.10929 | 0.10929 | 0.98757 | -0.23815 | 0.98566 | -0.27535 | 30.0255
75 | 0.0090664 | 0.0022722 | -0.0090655 | -0.0022718 | 8.9654e-07 | 4.0723e-07 | 0.013606 | 0.013606 | 0.013606 | 0.99154 | -0.16257 | 0.99144 | -0.16464 | 3.7379
76 | 0.0064256 | 0.0016102 | -0.0064254 | -0.0016101 | 1.2136e-07 | 3.2798e-08 | 0.0096438 | 0.0096439 | 0.0096439 | 0.99144 | -0.16464 | 0.99142 | -0.16504 | 2.6494
77 | 0.0043005 | 0.0010776 | -0.0043002 | -0.0010776 | 2.8245e-07 | -5.2342e-08 | 0.0064546 | 0.0064547 | 0.0064547 | 0.99142 | -0.16504 | 0.99135 | -0.16642 | 1.7733
78 | 0.0023782 | 0.00059593 | -0.0023781 | -0.00059602 | 4.2681e-08 | -8.7846e-08 | 0.0035696 | 0.0035697 | 0.0035697 | 0.99135 | -0.16642 | 0.99133 | -0.1668 | 0.98068
79 | -0.0065691 | -0.001646 | 0.0065695 | 0.0016461 | 3.2819e-07 | 9.3374e-08 | 0.0098475 | 0.0098474 | 0.0098475 | 0.99262 | -0.14179 | 0.99268 | -0.14075 | 2.7054
80 | 0.0045256 | 0.0011339 | -0.0045254 | -0.0011339 | 2.5803e-07 | -2.8104e-08 | 0.0067841 | 0.0067842 | 0.0067842 | 0.99262 | -0.14179 | 0.99256 | -0.14299 | 1.8638
81 | -0.0081435 | -0.0020404 | 0.0081438 | 0.0020405 | 3.4573e-07 | 1.4127e-07 | 0.012207 | 0.012207 | 0.012207 | 0.99268 | -0.14075 | 0.99272 | -0.13985 | 3.3535
82 | 0.001574 | 0.00039425 | -0.001574 | -0.00039448 | 4.2213e-08 | -2.3439e-07 | 0.0023594 | 0.0023595 | 0.0023595 | 0.99268 | -0.14075 | 0.99265 | -0.14131 | 0.64821
83 | 0.0025494 | 0.0006387 | -0.0025494 | -0.00063883 | 7.8237e-08 | -1.3452e-07 | 0.0038219 | 0.003822 | 0.003822 | 0.99256 | -0.14299 | 0.99253 | -0.14364 | 1.05
84 | -0.0099827 | -0.0025014 | 0.0099841 | 0.0025021 | 1.4234e-06 | 6.9177e-07 | 0.014963 | 0.014963 | 0.014963 | 0.99272 | -0.13985 | 0.99288 | -0.13686 | 4.1107
85 | 0.0012836 | 0.00032161 | -0.0012836 | -0.0003217 | 1.0689e-08 | -9.2631e-08 | 0.0019244 | 0.0019244 | 0.0019244 | 0.99253 | -0.14364 | 0.99252 | -0.14381 | 0.52869
86 | -0.011622 | -0.0029126 | 0.011624 | 0.0029137 | 1.9819e-06 | 1.0431e-06 | 0.017418 | 0.017418 | 0.017418 | 0.99288 | -0.13686 | 0.99306 | -0.13328 | 4.7852
87 | -0.013659 | -0.0034237 | 0.013662 | 0.0034252 | 2.5371e-06 | 1.4148e-06 | 0.020468 | 0.020467 | 0.020468 | 0.99306 | -0.13328 | 0.99327 | -0.12938 | 5.623
88 | -0.0024228 | -0.00060722 | 0.0024229 | 0.00060711 | 5.8225e-08 | -1.0974e-07 | 0.0036634 | 0.0036634 | 0.0036634 | 0.98411 | -0.30545 | 0.98414 | -0.30495 | 1.0064
89 | -0.0036967 | -0.00092636 | 0.0036968 | 0.00092634 | 4.1978e-08 | -1.8664e-08 | 0.0055894 | 0.0055894 | 0.0055894 | 0.98414 | -0.30495 | 0.98415 | -0.30471 | 1.5355
90 | -0.0049716 | -0.0012459 | 0.004972 | 0.0012459 | 3.7649e-07 | 1.5156e-08 | 0.0075169 | 0.0075168 | 0.0075169 | 0.98415 | -0.30471 | 0.98423 | -0.30312 | 2.0651
91 | -0.0080588 | -0.0020195 | 0.0080591 | 0.0020196 | 2.9489e-07 | 1.214e-07 | 0.012184 | 0.012184 | 0.012184 | 0.98423 | -0.30312 | 0.98427 | -0.30235 | 3.3472
92 | -0.01666 | -0.0041752 | 0.016666 | 0.0041788 | 6.1429e-06 | 3.6031e-06 | 0.025186 | 0.025186 | 0.025186 | 0.98427 | -0.30235 | 0.98467 | -0.29461 | 6.9193
93 | 0.0086007 | 0.0021555 | -0.0086 | -0.0021552 | 6.93e-07 | 3.046e-07 | 0.013002 | 0.013003 | 0.013003 | 0.98427 | -0.30235 | 0.98419 | -0.30404 | 3.5721
94 | 0.0022038 | 0.00055219 | -0.0022037 | -0.0005523 | 4.5248e-08 | -1.0772e-07 | 0.0033406 | 0.0033406 | 0.0033406 | 0.98162 | -0.3542 | 0.9816 | -0.35463 | 0.91775
95 | 0.0039724 | 0.00099547 | -0.0039722 | -0.00099554 | 2.1198e-07 | -6.7535e-08 | 0.0059757 | 0.0059757 | 0.0059757 | 0.98918 | -0.20805 | 0.98913 | -0.20917 | 1.6417
96 | 0.0066945 | 0.0016776 | -0.006694 | -0.0016774 | 4.4913e-07 | 1.386e-07 | 0.010116 | 0.010117 | 0.010117 | 0.98467 | -0.29461 | 0.9846 | -0.29602 | 2.7793
97 | -0.02336 | -0.0058563 | 0.023362 | 0.0058576 | 2.0244e-06 | 1.2405e-06 | 0.035302 | 0.035302 | 0.035302 | 0.98467 | -0.29461 | 0.98476 | -0.2928 | 9.6985
98 | 0.0076487 | 0.0019168 | -0.0076486 | -0.0019168 | 5.367e-08 | 2.0749e-08 | 0.011564 | 0.011564 | 0.011564 | 0.98419 | -0.30404 | 0.98418 | -0.30419 | 3.177
99 | 0.0050209 | 0.0012581 | -0.0050207 | -0.0012581 | 1.6073e-07 | 8.1942e-09 | 0.007588 | 0.007588 | 0.007588 | 0.9846 | -0.29602 | 0.98456 | -0.2967 | 2.0846
100 | 0.0063732 | 0.0015971 | -0.006373 | -0.0015971 | 2.5914e-07 | 7.1277e-08 | 0.0096358 | 0.0096359 | 0.0096359 | 0.98418 | -0.30419 | 0.98414 | -0.30504 | 2.6472
101 | 0.0074739 | 0.0018722 | -0.007473 | -0.001872 | 8.016e-07 | 2.9491e-07 | 0.011229 | 0.011229 | 0.011229 | 0.99036 | -0.18547 | 0.99025 | -0.18772 | 3.0849
102 | -0.011595 | -0.0029051 | 0.011595 | 0.0029052 | 2.2885e-07 | 1.2059e-07 | 0.017421 | 0.017421 | 0.017421 | 0.99036 | -0.18547 | 0.99038 | -0.18505 | 4.7859
103 | 0.0057896 | 0.00145 | -0.0057889 | -0.0014499 | 7.161e-07 | 1.3375e-07 | 0.0086995 | 0.0086996 | 0.0086996 | 0.99025 | -0.18772 | 0.99011 | -0.19032 | 2.39
104 | -0.013345 | -0.0033438 | 0.013348 | 0.0033451 | 2.2974e-06 | 1.2742e-06 | 0.020051 | 0.02005 | 0.020051 | 0.99038 | -0.18505 | 0.99057 | -0.18144 | 5.5084
105 | 0.00083743 | 0.00020939 | -0.00083741 | -0.00020977 | 1.8276e-08 | -3.8407e-07 | 0.0012584 | 0.0012585 | 0.0012585 | 0.99011 | -0.19032 | 0.99009 | -0.19078 | 0.34575
106 | 0.0049514 | 0.0012405 | -0.0049512 | -0.0012405 | 2.5811e-07 | 5.3319e-09 | 0.0074412 | 0.0074413 | 0.0074413 | 0.99011 | -0.19032 | 0.99006 | -0.19141 | 2.0443
107 | -0.015777 | -0.0039539 | 0.015781 | 0.0039564 | 4.2511e-06 | 2.4608e-06 | 0.0237 | 0.0237 | 0.0237 | 0.99057 | -0.18144 | 0.99086 | -0.17578 | 6.5109
108 | 0.00033696 | 8.4345e-05 | -0.00033696 | -8.445e-05 | 7.8644e-10 | -1.0467e-07 | 0.00050638 | 0.00050642 | 0.00050642 | 0.99009 | -0.19078 | 0.99009 | -0.19083 | 0.13913
109 | 0.0036999 | 0.00092692 | -0.0036999 | -0.00092693 | 1.5818e-08 | -7.4187e-09 | 0.0055607 | 0.0055607 | 0.0055607 | 0.99006 | -0.19141 | 0.99005 | -0.1915 | 1.5277
110 | 0.002882 | 0.00072195 | -0.002882 | -0.00072206 | 8.8983e-08 | -1.0568e-07 | 0.0043315 | 0.0043315 | 0.0043315 | 0.99005 | -0.1915 | 0.99002 | -0.19215 | 1.19
111 | 0.0020641 | 0.00051707 | -0.002064 | -0.00051729 | 7.2746e-08 | -2.1262e-07 | 0.0031022 | 0.0031023 | 0.0031023 | 0.99002 | -0.19215 | 0.98998 | -0.19289 | 0.85229
112 | 0.0033477 | 0.00083881 | -0.0033476 | -0.0008389 | 1.3359e-07 | -9.147e-08 | 0.0050595 | 0.0050596 | 0.0050596 | 0.98456 | -0.2967 | 0.98452 | -0.29753 | 1.39
113 | 0.0050985 | 0.0012777 | -0.0050982 | -0.0012776 | 3.349e-07 | 2.3401e-08 | 0.0077089 | 0.0077089 | 0.0077089 | 0.98414 | -0.30504 | 0.98407 | -0.30642 | 2.1178
114 | 0.001673 | 0.00041921 | -0.001673 | -0.0004193 | 1.7846e-08 | -8.3223e-08 | 0.0025286 | 0.0025286 | 0.0025286 | 0.98452 | -0.29753 | 0.98451 | -0.29776 | 0.69468
115 | 0.0038237 | 0.00095824 | -0.0038237 | -0.00095824 | 3.5727e-10 | -1.3043e-10 | 0.0057819 | 0.0057819 | 0.0057819 | 0.98407 | -0.30642 | 0.98407 | -0.30643 | 1.5884
116 | 0.0025493 | 0.00063884 | -0.0025493 | -0.00063891 | 3.858e-08 | -6.3265e-08 | 0.0038548 | 0.0038549 | 0.0038549 | 0.98407 | -0.30643 | 0.98405 | -0.30674 | 1.059
117 | 0.0012751 | 0.00031957 | -0.0012751 | -0.00031958 | 7.2191e-10 | -6.1148e-09 | 0.0019282 | 0.0019282 | 0.0019282 | 0.98405 | -0.30674 | 0.98405 | -0.30675 | 0.52972

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30924 | 0.078143

## res_load
| p_mw | q_mvar
0 | 0.011359 | 0.0028469
1 | 0.0017527 | 0.00043926
2 | 0.0021833 | 0.00054719
3 | 0.0011579 | 0.00029021
4 | 0.0024054 | 0.00060284
5 | 0.0044008 | 0.0011029
6 | 0.019227 | 0.0048186
7 | 0.019333 | 0.0048453
8 | 0.0046939 | 0.0011764
9 | 0.00093806 | 0.0002351
10 | 0.0016977 | 0.00042549
11 | 0.0069289 | 0.0017365
12 | 0.004002 | 0.001003
13 | 0.0034307 | 0.00085982
14 | 0.0017956 | 0.00045003
15 | 0.0061394 | 0.0015387
16 | 0.0021901 | 0.00054889
17 | 0.0065494 | 0.0016414
18 | 0.0057499 | 0.0014411
19 | 0.0023748 | 0.00059518
20 | 0.0065493 | 0.0016414
21 | 0.0013092 | 0.00032811
22 | 0.0041755 | 0.0010465
23 | 0.00081378 | 0.00020395
24 | 0.00081327 | 0.00020383
25 | 0.00081324 | 0.00020382
26 | 0.001727 | 0.00043281
27 | 0.0031791 | 0.00079675
28 | 0.0025238 | 0.00063253
29 | 0.0047113 | 0.0011808
30 | 0.01576 | 0.0039498
31 | 0.019365 | 0.0048533
32 | 0.0065429 | 0.0016398
33 | 0.0021842 | 0.00054741
34 | 0.0059602 | 0.0014938
35 | 0.0022475 | 0.00056327
36 | 0.0014314 | 0.00035874
37 | 0.0014331 | 0.00035918
38 | 0.0039764 | 0.00099658
39 | 0.0014335 | 0.00035926
40 | 0.001432 | 0.0003589
41 | 0.0014312 | 0.0003587
42 | 0.0014322 | 0.00035893
43 | 0.0014328 | 0.0003591
44 | 0.002468 | 0.00061854
45 | 0.0014325 | 0.00035901
46 | 0.0022545 | 0.00056504
47 | 0.0022475 | 0.00056328
48 | 0.0061383 | 0.0015384
49 | 0.0048147 | 0.0012067
50 | 0.0026399 | 0.00066163
51 | 0.0021249 | 0.00053255
52 | 0.0019221 | 0.00048172
53 | 0.0023781 | 0.00059602
54 | 0.0020435 | 0.00051215
55 | 0.0019759 | 0.00049521
56 | 0.0018388 | 0.00046085
57 | 0.001574 | 0.00039448
58 | 0.0012657 | 0.00031722
59 | 0.0016382 | 0.00041058
60 | 0.0020351 | 0.00051005
61 | 0.0012836 | 0.0003217
62 | 0.00081318 | 0.0002038
63 | 0.0024228 | 0.00060722
64 | 0.0012738 | 0.00031925
65 | 0.0012748 | 0.00031951
66 | 0.0030868 | 0.00077363
67 | 0.0022005 | 0.00055149
68 | 0.0022037 | 0.0005523
69 | 0.0014331 | 0.00035917
70 | 0.0022017 | 0.00055179
71 | 0.0039736 | 0.00099588
72 | 0.0039722 | 0.00099554
73 | 0.00095131 | 0.00023842
74 | 0.0016731 | 0.00041932
75 | 0.0041219 | 0.001033
76 | 0.0012754 | 0.00031965
77 | 0.004121 | 0.0010328
78 | 0.0016835 | 0.00042192
79 | 0.0017503 | 0.00043866
80 | 0.0024293 | 0.00060884
81 | 0.00050045 | 0.00012543
82 | 0.0012512 | 0.00031359
83 | 0.0017121 | 0.00042908
84 | 0.00033696 | 8.445e-05
85 | 0.00081789 | 0.00020498
86 | 0.00081789 | 0.00020498
87 | 0.002064 | 0.00051729
88 | 0.001673 | 0.0004193
89 | 0.0012745 | 0.00031941
90 | 0.0016746 | 0.00041968
91 | 0.0012744 | 0.0003194
92 | 0.0012744 | 0.0003194
93 | 0.0012742 | 0.00031933
94 | 0.0012751 | 0.00031958
95 | 0.001673 | 0.0004193

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1