## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-100_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-100_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-100_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-100_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-100_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-100_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2701-100_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2701-100_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2701-100_0_3_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_2701-100_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_2701-100_0_3_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_2701-100_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2701-100_0_3_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_2701-100_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2701-100_0_3_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_2701-100_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_2701-100_0_3_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_2701-100_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2701-100_0_3_node_42 | 0.4 | n |  | TRUE
19 | bus_LV_2701-100_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2701-100_0_3_node_50 | 0.4 | n |  | TRUE
21 | bus_LV_2701-100_0_3_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_2701-100_0_3_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_2701-100_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_2701-100_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2701-100_0_3_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_2701-100_0_3_node_51 | 0.4 | n |  | TRUE
27 | bus_LV_2701-100_0_3_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_2701-100_0_3_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_2701-100_0_3_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2701-100_0_3_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_2701-100_0_3_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_2701-100_0_3_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_2701-100_0_3_node_49 | 0.4 | n |  | TRUE
34 | bus_LV_2701-100_0_3_node_47 | 0.4 | n |  | TRUE
35 | bus_LV_2701-100_0_3_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_2701-100_0_3_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_2701-100_0_3_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_2701-100_0_3_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_2701-100_0_3_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_2701-100_0_3_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_2701-100_0_3_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_2701-100_0_3_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_2701-100_0_3_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_2701-100_0_3_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_2701-100_0_3_node_48 | 0.4 | n |  | TRUE
46 | bus_LV_2701-100_0_3_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_2701-100_0_3_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_2701-100_0_3_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_2701-100_0_3_node_45 | 0.4 | n |  | TRUE
50 | bus_MV_555_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-100_0_3_load_0 | 0 | 0.006141 | 0.0015391 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-100_0_3_load_1 | 1 | 0.0054133 | 0.0013567 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-100_0_3_load_3 | 3 | 0.0025782 | 0.00064615 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-100_0_3_load_5 | 5 | 0.0054131 | 0.0013566 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-100_0_3_load_6 | 6 | 0.0025873 | 0.00064844 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-100_0_3_load_12 | 9 | 0.0043876 | 0.0010996 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-100_0_3_load_13 | 10 | 0.0076563 | 0.0019188 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-100_0_3_load_7 | 11 | 0.0092925 | 0.0023289 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-100_0_3_load_17 | 14 | 0.0060827 | 0.0015245 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-100_0_3_load_14 | 15 | 0.0051802 | 0.0012983 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-100_0_3_load_35 | 16 | 0.016331 | 0.0040929 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-100_0_3_load_42 | 18 | 0.011708 | 0.0029344 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-100_0_3_load_16 | 19 | 0.042625 | 0.010683 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-100_0_3_load_50 | 20 | 0.0043732 | 0.001096 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-100_0_3_load_38 | 22 | 0.0074755 | 0.0018735 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-100_0_3_load_18 | 23 | 0.0038652 | 0.00096872 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-100_0_3_load_15 | 24 | 0.010067 | 0.002523 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-100_0_3_load_36 | 25 | 0.0048451 | 0.0012143 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-100_0_3_load_51 | 26 | 0.0054266 | 0.00136 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-100_0_3_load_31 | 27 | 0.0038705 | 0.00097004 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-100_0_3_load_32 | 28 | 0.0038626 | 0.00096806 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-100_0_3_load_19 | 29 | 0.007643 | 0.0019155 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-100_0_3_load_20 | 30 | 0.0063098 | 0.0015814 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-100_0_3_load_22 | 31 | 0.0063256 | 0.0015853 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-100_0_3_load_24 | 32 | 0.007556 | 0.0018937 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-100_0_3_load_47 | 34 | 0.0050623 | 0.0012687 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-100_0_3_load_25 | 35 | 0.030019 | 0.0075234 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-100_0_3_load_26 | 36 | 0.0071172 | 0.0017837 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-100_0_3_load_28 | 38 | 0.0070526 | 0.0017676 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-100_0_3_load_41 | 41 | 0.0171 | 0.0042856 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-100_0_3_load_40 | 43 | 0.0028078 | 0.00070369 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-100_0_3_load_46 | 46 | 0.0053018 | 0.0013288 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-100_0_3_load_43 | 47 | 0.0025473 | 0.00063843 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-100_0_3_load_44 | 48 | 0.0025845 | 0.00064773 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-100_0_3_line_0 |  | 0 | 1 | 0.001695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-100_0_3_line_1 |  | 0 | 2 | 0.016358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-100_0_3_line_2 |  | 1 | 3 | 0.028479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-100_0_3_line_3 |  | 2 | 4 | 0.023639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-100_0_3_line_4 |  | 2 | 5 | 0.024728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-100_0_3_line_5 |  | 3 | 6 | 0.00012862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-100_0_3_line_6 |  | 4 | 7 | 0.036766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2701-100_0_3_line_7 |  | 4 | 8 | 0.038131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2701-100_0_3_line_8 |  | 5 | 9 | 0.012251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-100_0_3_line_9 |  | 6 | 10 | 0.016549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-100_0_3_line_10 |  | 7 | 13 | 0.004385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2701-100_0_3_line_11 |  | 8 | 14 | 0.055093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-100_0_3_line_12 |  | 8 | 15 | 0.01555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2701-100_0_3_line_13 |  | 9 | 20 | 0.010862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-100_0_3_line_14 |  | 10 | 12 | 0.024386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-100_0_3_line_15 |  | 11 | 12 | 0.022563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-100_0_3_line_16 |  | 12 | 21 | 0.031214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-100_0_3_line_17 |  | 13 | 16 | 0.033133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2701-100_0_3_line_18 |  | 14 | 23 | 0.013303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-100_0_3_line_19 |  | 15 | 24 | 0.025206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2701-100_0_3_line_20 |  | 16 | 25 | 0.048221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_2701-100_0_3_line_21 |  | 17 | 18 | 0.018592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-100_0_3_line_22 |  | 17 | 19 | 0.044504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-100_0_3_line_23 |  | 19 | 24 | 0.011366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-100_0_3_line_24 |  | 20 | 26 | 0.012263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-100_0_3_line_25 |  | 21 | 22 | 0.021233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-100_0_3_line_26 |  | 23 | 27 | 0.011518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-100_0_3_line_27 |  | 25 | 40 | 0.038086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-100_0_3_line_28 |  | 26 | 44 | 0.023132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-100_0_3_line_29 |  | 27 | 28 | 0.010878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-100_0_3_line_30 |  | 29 | 30 | 0.012407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-100_0_3_line_31 |  | 30 | 31 | 0.010855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-100_0_3_line_32 |  | 31 | 32 | 0.012352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-100_0_3_line_33 |  | 32 | 33 | 0.025182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-100_0_3_line_34 |  | 33 | 34 | 0.021767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-100_0_3_line_35 |  | 34 | 49 | 0.011993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-100_0_3_line_36 |  | 35 | 36 | 0.082929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-100_0_3_line_37 |  | 35 | 37 | 0.09072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-100_0_3_line_38 |  | 36 | 38 | 0.029735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2701-100_0_3_line_39 |  | 37 | 39 | 0.21431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2701-100_0_3_line_40 |  | 38 | 40 | 0.064945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2701-100_0_3_line_41 |  | 39 | 41 | 0.034798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-100_0_3_line_42 |  | 41 | 42 | 0.016421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-100_0_3_line_43 |  | 42 | 43 | 0.017651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-100_0_3_line_44 |  | 44 | 45 | 0.003985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2701-100_0_3_line_45 |  | 45 | 46 | 0.013368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2701-100_0_3_line_46 |  | 46 | 48 | 0.027997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2701-100_0_3_line_47 |  | 47 | 48 | 0.00054241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2701-100_0_3_line_48 |  | 47 | 49 | 0.012688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-100_0_3_trafo_15 | 0.63 MVA 20/0.4 kV | 50 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2613757.9556 | 1266434.9998 | 2613759.6487 | 1266434.9179
1 | 2613741.6163 | 1266435.7906 | 2613757.9556 | 1266434.9998
2 | 2613759.6487 | 1266434.9179 | 2613788.0946 | 1266433.5412
3 | 2613740.6697 | 1266412.172 | 2613741.6163 | 1266435.7906
4 | 2613741.6163 | 1266435.7906 | 2613742.7166 | 1266460.4941
5 | 2613788.2231 | 1266433.535 | 2613788.0946 | 1266433.5412
6 | 2613739.2944 | 1266375.432 | 2613740.3853 | 1266404.9885 | 2613740.6697 | 1266412.172
7 | 2613740.6697 | 1266412.172 | 2613740.3853 | 1266404.9885 | 2613735.6044 | 1266405.2665 | 2613736.0709 | 1266411.8834 | 2613736.8387 | 1266431.3876
8 | 2613742.7166 | 1266460.4941 | 2613743.2618 | 1266472.7334
9 | 2613788.2231 | 1266433.535 | 2613804.7523 | 1266432.735
10 | 2613739.2944 | 1266375.432 | 2613734.8984 | 1266375.2884
11 | 2613736.8387 | 1266431.3876 | 2613739.0068 | 1266486.4375
12 | 2613736.8387 | 1266431.3876 | 2613721.3002 | 1266431.9821
13 | 2613743.7451 | 1266483.5843 | 2613743.2618 | 1266472.7334
14 | 2613803.7024 | 1266408.3711 | 2613804.7523 | 1266432.735
15 | 2613803.7024 | 1266408.3711 | 2613781.1801 | 1266409.7292
16 | 2613801.7047 | 1266377.2225 | 2613803.7024 | 1266408.3711
17 | 2613734.8984 | 1266375.2884 | 2613701.7829 | 1266374.2153
18 | 2613739.5399 | 1266499.73 | 2613739.384 | 1266496.0164 | 2613739.0068 | 1266486.4375
19 | 2613721.3002 | 1266431.9821 | 2613716.2857 | 1266432.174 | 2613701.0455 | 1266445.4132
20 | 2613701.7829 | 1266374.2153 | 2613653.5867 | 1266372.6535
21 | 2613689.4972 | 1266407.8952 | 2613670.8782 | 1266408.9308
22 | 2613689.4972 | 1266407.8952 | 2613691.0831 | 1266444.8802 | 2613692.0747 | 1266452.2988
23 | 2613692.0747 | 1266452.2988 | 2613694.7504 | 1266450.8818 | 2613701.0455 | 1266445.4132
24 | 2613743.7451 | 1266483.5843 | 2613744.2907 | 1266495.8348
25 | 2613801.7047 | 1266377.2225 | 2613780.5032 | 1266378.374
26 | 2613739.5399 | 1266499.73 | 2613740.0229 | 1266511.2381
27 | 2613615.5211 | 1266371.4219 | 2613623.7109 | 1266371.6853 | 2613653.5867 | 1266372.6535
28 | 2613745.4887 | 1266518.9354 | 2613744.8006 | 1266507.2812 | 2613744.2907 | 1266495.8348
29 | 2613740.479 | 1266522.1065 | 2613740.0229 | 1266511.2381
30 | 2613835.6914 | 1266469.4972 | 2613835.1419 | 1266457.1023
31 | 2613835.6914 | 1266469.4972 | 2613836.1722 | 1266480.3413
32 | 2613836.7193 | 1266492.6812 | 2613836.1722 | 1266480.3413
33 | 2613837.8347 | 1266517.838 | 2613836.7193 | 1266492.6812
34 | 2613837.8347 | 1266517.838 | 2613816.0704 | 1266518.1673
35 | 2613804.0789 | 1266518.3487 | 2613816.0704 | 1266518.1673
36 | 2613640.5446 | 1266460.6787 | 2613640.2588 | 1266462.7758 | 2613637.5821 | 1266484.3069 | 2613639.4755 | 1266495.6858 | 2613643.0929 | 1266503.7442 | 2613650.338 | 1266512.1111 | 2613667.0234 | 1266530.0843 | 2613669.0249 | 1266532.5239
37 | 2613687.294 | 1266615.6796 | 2613693.6546 | 1266599.4719 | 2613693.8771 | 1266587.8976 | 2613692.1886 | 1266575.8186 | 2613684.3478 | 1266554.9193 | 2613676.5194 | 1266541.6587 | 2613669.0249 | 1266532.5239
38 | 2613640.7409 | 1266431.2481 | 2613641.2391 | 1266432.5792 | 2613642.6172 | 1266445.4691 | 2613640.5446 | 1266460.6787
39 | 2613586.585 | 1266439.8256 | 2613602.8225 | 1266453.0275 | 2613608.4509 | 1266460.6457 | 2613611.9706 | 1266471.9728 | 2613615.0829 | 1266486.9126 | 2613618.9738 | 1266500.4643 | 2613625.505 | 1266511.6093 | 2613634.7385 | 1266526.0628 | 2613662.2309 | 1266564.8753 | 2613669.1754 | 1266576.2659 | 2613671.7776 | 1266583.8216 | 2613670.7485 | 1266592.681 | 2613666.6852 | 1266601.7335 | 2613678.0115 | 1266609.5206 | 2613687.294 | 1266615.6796
40 | 2613615.5211 | 1266371.4219 | 2613624.5393 | 1266391.2453 | 2613635.6201 | 1266417.5669 | 2613640.7409 | 1266431.2481
41 | 2613586.585 | 1266439.8256 | 2613591.7744 | 1266428.7964 | 2613593.406 | 1266423.0628 | 2613591.8904 | 1266406.4845
42 | 2613585.0543 | 1266391.5995 | 2613591.8271 | 1266405.7916 | 2613591.8904 | 1266406.4845
43 | 2613585.0543 | 1266391.5995 | 2613587.5364 | 1266385.9568 | 2613592.4882 | 1266383.3552 | 2613594.5184 | 1266377.8227
44 | 2613745.4887 | 1266518.9354 | 2613749.486 | 1266518.9002
45 | 2613749.486 | 1266518.9002 | 2613762.8535 | 1266518.7652
46 | 2613790.8487 | 1266518.4824 | 2613762.8535 | 1266518.7652
47 | 2613790.8487 | 1266518.4824 | 2613791.3911 | 1266518.4769
48 | 2613804.0789 | 1266518.3487 | 2613791.3911 | 1266518.4769

## bus_geodata
| x | y | coords
0 | 2613757.9556 | 1266434.9998
1 | 2613759.6487 | 1266434.9179
2 | 2613741.6163 | 1266435.7906
3 | 2613788.0946 | 1266433.5412
4 | 2613740.6697 | 1266412.172
5 | 2613742.7166 | 1266460.4941
6 | 2613788.2231 | 1266433.535
7 | 2613739.2944 | 1266375.432
8 | 2613736.8387 | 1266431.3876
9 | 2613743.2618 | 1266472.7334
10 | 2613804.7523 | 1266432.735
11 | 2613781.1801 | 1266409.7292
12 | 2613803.7024 | 1266408.3711
13 | 2613734.8984 | 1266375.2884
14 | 2613739.0068 | 1266486.4375
15 | 2613721.3002 | 1266431.9821
16 | 2613701.7829 | 1266374.2153
17 | 2613689.4972 | 1266407.8952
18 | 2613670.8782 | 1266408.9308
19 | 2613692.0747 | 1266452.2988
20 | 2613743.7451 | 1266483.5843
21 | 2613801.7047 | 1266377.2225
22 | 2613780.5032 | 1266378.374
23 | 2613739.5399 | 1266499.73
24 | 2613701.0455 | 1266445.4132
25 | 2613653.5867 | 1266372.6535
26 | 2613744.2907 | 1266495.8348
27 | 2613740.0229 | 1266511.2381
28 | 2613740.479 | 1266522.1065
29 | 2613835.1419 | 1266457.1023
30 | 2613835.6914 | 1266469.4972
31 | 2613836.1722 | 1266480.3413
32 | 2613836.7193 | 1266492.6812
33 | 2613837.8347 | 1266517.838
34 | 2613816.0704 | 1266518.1673
35 | 2613669.0249 | 1266532.5239
36 | 2613640.5446 | 1266460.6787
37 | 2613687.294 | 1266615.6796
38 | 2613640.7409 | 1266431.2481
39 | 2613586.585 | 1266439.8256
40 | 2613615.5211 | 1266371.4219
41 | 2613591.8904 | 1266406.4845
42 | 2613585.0543 | 1266391.5995
43 | 2613594.5184 | 1266377.8227
44 | 2613745.4887 | 1266518.9354
45 | 2613749.486 | 1266518.9002
46 | 2613762.8535 | 1266518.7652
47 | 2613791.3911 | 1266518.4769
48 | 2613790.8487 | 1266518.4824
49 | 2613804.0789 | 1266518.3487
50 | 2613736.8387 | 1266431.3876

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98984 | -0.19421 | 0.006141 | 0.0015391
1 | 0.98978 | -0.19527 | 0.0054133 | 0.0013567
2 | 0.99045 | -0.18225 | 0 | 0
3 | 0.98901 | -0.21027 | 0.0025782 | 0.00064615
4 | 0.99272 | -0.13863 | 0 | 0
5 | 0.98902 | -0.20994 | 0.0054131 | 0.0013566
6 | 0.989 | -0.21034 | 0.0025873 | 0.00064844
7 | 0.99126 | -0.1664 | 0 | 0
8 | 0.99605 | -0.074982 | 0 | 0
9 | 0.98837 | -0.2225 | 0.0043876 | 0.0010996
10 | 0.98863 | -0.21754 | 0.0076563 | 0.0019188
11 | 0.98807 | -0.22858 | 0.0092925 | 0.0023289
12 | 0.98826 | -0.22484 | 0 | 0
13 | 0.99109 | -0.16972 | 0 | 0
14 | 0.99516 | -0.092112 | 0.0060827 | 0.0015245
15 | 0.99753 | -0.04674 | 0.0051802 | 0.0012983
16 | 0.98978 | -0.19483 | 0.016331 | 0.0040929
17 | 0.99897 | -0.019868 | 0 | 0
18 | 0.99877 | -0.023671 | 0.011708 | 0.0029344
19 | 0.99944 | -0.01077 | 0.042625 | 0.010683
20 | 0.98784 | -0.23281 | 0.0043732 | 0.001096
21 | 0.98804 | -0.229 | 0 | 0
22 | 0.9879 | -0.23184 | 0.0074755 | 0.0018735
23 | 0.99502 | -0.094828 | 0.0038652 | 0.00096872
24 | 1 | 0 | -0.2713 | -0.068774
25 | 0.98823 | -0.22445 | 0.0048451 | 0.0012143
26 | 0.98729 | -0.24349 | 0.0054266 | 0.00136
27 | 0.99494 | -0.096396 | 0.0038705 | 0.00097004
28 | 0.9949 | -0.097136 | 0.0038626 | 0.00096806
29 | 0.98226 | -0.34152 | 0.007643 | 0.0019155
30 | 0.98234 | -0.3398 | 0.0063098 | 0.0015814
31 | 0.98248 | -0.33707 | 0.0063256 | 0.0015853
32 | 0.98271 | -0.33255 | 0.007556 | 0.0018937
33 | 0.98336 | -0.3199 | 0 | 0
34 | 0.98392 | -0.30899 | 0.0050623 | 0.0012687
35 | 0.97666 | -0.44917 | 0.030019 | 0.0075234
36 | 0.98051 | -0.37379 | 0.0071172 | 0.0017837
37 | 0.97497 | -0.48224 | 0 | 0
38 | 0.98209 | -0.34308 | 0.0070526 | 0.0017676
39 | 0.97098 | -0.56081 | 0 | 0
40 | 0.98596 | -0.26813 | 0 | 0
41 | 0.97034 | -0.57363 | 0.0171 | 0.0042856
42 | 0.97029 | -0.57448 | 0 | 0
43 | 0.97025 | -0.5754 | 0.0028078 | 0.00070369
44 | 0.98636 | -0.26143 | 0 | 0
45 | 0.9862 | -0.26453 | 0 | 0
46 | 0.98567 | -0.27492 | 0.0053018 | 0.0013288
47 | 0.98467 | -0.29438 | 0.0025473 | 0.00063843
48 | 0.98469 | -0.29404 | 0.0025845 | 0.00064773
49 | 0.98428 | -0.30189 | 0 | 0
50 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.035044 | 0.0087972 | -0.035043 | -0.0087961 | 1.7645e-06 | 1.1075e-06 | 0.052687 | 0.052687 | 0.052687 | 0.98984 | -0.19421 | 0.98978 | -0.19527 | 14.4745
1 | -0.041185 | -0.010336 | 0.041209 | 0.010351 | 2.3519e-05 | 1.4842e-05 | 0.061919 | 0.061919 | 0.061919 | 0.98984 | -0.19421 | 0.99045 | -0.18225 | 17.0107
2 | 0.029629 | 0.0074394 | -0.029608 | -0.0074262 | 2.1195e-05 | 1.3199e-05 | 0.044549 | 0.044549 | 0.044549 | 0.98978 | -0.19527 | 0.98901 | -0.21027 | 12.2388
3 | -0.10447 | -0.026332 | 0.10469 | 0.026472 | 0.00021852 | 0.00013955 | 0.15701 | 0.15701 | 0.15701 | 0.99045 | -0.18225 | 0.99272 | -0.13863 | 43.1336
4 | 0.063262 | 0.015981 | -0.063178 | -0.015928 | 8.3843e-05 | 5.3342e-05 | 0.095088 | 0.095088 | 0.095088 | 0.99045 | -0.18225 | 0.98902 | -0.20994 | 26.123
5 | 0.02703 | 0.00678 | -0.02703 | -0.00678 | 7.9779e-08 | 4.9407e-08 | 0.04067 | 0.04067 | 0.04067 | 0.98901 | -0.21027 | 0.989 | -0.21034 | 11.1731
6 | 0.086359 | 0.022057 | -0.086244 | -0.021983 | 0.00011578 | 7.3147e-05 | 0.12959 | 0.12959 | 0.12959 | 0.99272 | -0.13863 | 0.99126 | -0.1664 | 17.8015
7 | -0.19105 | -0.048528 | 0.19164 | 0.048903 | 0.00058726 | 0.00037486 | 0.2866 | 0.2866 | 0.2866 | 0.99272 | -0.13863 | 0.99605 | -0.074982 | 39.3682
8 | 0.057765 | 0.014571 | -0.057731 | -0.014549 | 3.4729e-05 | 2.207e-05 | 0.086944 | 0.086944 | 0.086944 | 0.98902 | -0.20994 | 0.98837 | -0.2225 | 23.8856
9 | 0.024443 | 0.0061316 | -0.024434 | -0.0061264 | 8.3937e-06 | 5.1597e-06 | 0.036777 | 0.036777 | 0.036777 | 0.989 | -0.21034 | 0.98863 | -0.21754 | 10.1037
10 | 0.086244 | 0.021983 | -0.08623 | -0.021975 | 1.3808e-05 | 8.7244e-06 | 0.12959 | 0.12959 | 0.12959 | 0.99126 | -0.1664 | 0.99109 | -0.16972 | 17.8015
11 | 0.017698 | 0.0044408 | -0.017683 | -0.0044322 | 1.4444e-05 | 8.5275e-06 | 0.026441 | 0.026441 | 0.026441 | 0.99605 | -0.074982 | 0.99516 | -0.092112 | 7.264
12 | -0.20933 | -0.053344 | 0.20962 | 0.053526 | 0.00028571 | 0.00018245 | 0.31304 | 0.31304 | 0.31304 | 0.99605 | -0.074982 | 0.99753 | -0.04674 | 43.0001
13 | 0.053343 | 0.013449 | -0.053317 | -0.013433 | 2.6289e-05 | 1.6686e-05 | 0.080338 | 0.080338 | 0.080338 | 0.98837 | -0.2225 | 0.98784 | -0.23281 | 22.0709
14 | 0.016778 | 0.0042076 | -0.016772 | -0.0042041 | 5.8322e-06 | 3.4201e-06 | 0.025254 | 0.025254 | 0.025254 | 0.98863 | -0.21754 | 0.98826 | -0.22484 | 6.9379
15 | -0.0092925 | -0.0023289 | 0.0092941 | 0.0023297 | 1.6571e-06 | 7.7147e-07 | 0.013994 | 0.013994 | 0.013994 | 0.98807 | -0.22858 | 0.98826 | -0.22484 | 3.8446
16 | 0.0074779 | 0.0018744 | -0.0074765 | -0.0018739 | 1.484e-06 | 5.499e-07 | 0.01126 | 0.01126 | 0.01126 | 0.98826 | -0.22484 | 0.98804 | -0.229 | 3.0933
17 | 0.08623 | 0.021975 | -0.086125 | -0.021909 | 0.00010434 | 6.5922e-05 | 0.12959 | 0.12959 | 0.12959 | 0.99109 | -0.16972 | 0.98978 | -0.19483 | 17.8015
18 | 0.011601 | 0.0029078 | -0.011599 | -0.002907 | 1.501e-06 | 7.8782e-07 | 0.017346 | 0.017346 | 0.017346 | 0.99516 | -0.092112 | 0.99502 | -0.094828 | 4.7654
19 | -0.2148 | -0.054825 | 0.21529 | 0.055135 | 0.00048627 | 0.00031056 | 0.32077 | 0.32077 | 0.32077 | 0.99753 | -0.04674 | 1 | 0 | 44.0615
20 | 0.069794 | 0.017816 | -0.069695 | -0.017753 | 9.9766e-05 | 6.2613e-05 | 0.10504 | 0.10504 | 0.10504 | 0.98978 | -0.19483 | 0.98823 | -0.22445 | 14.4291
21 | 0.011711 | 0.0029355 | -0.011708 | -0.0029344 | 2.1215e-06 | 1.1144e-06 | 0.017444 | 0.017444 | 0.017444 | 0.99897 | -0.019868 | 0.99877 | -0.023671 | 4.7923
22 | -0.011711 | -0.0029355 | 0.011716 | 0.0029382 | 5.0781e-06 | 2.6671e-06 | 0.017444 | 0.017444 | 0.017444 | 0.99897 | -0.019868 | 0.99944 | -0.01077 | 4.7922
23 | -0.05434 | -0.013621 | 0.054368 | 0.013639 | 2.79e-05 | 1.7707e-05 | 0.080905 | 0.080905 | 0.080905 | 0.99944 | -0.01077 | 1 | 0 | 22.2267
24 | 0.048944 | 0.012337 | -0.048919 | -0.012321 | 2.5012e-05 | 1.5851e-05 | 0.073751 | 0.073751 | 0.073751 | 0.98784 | -0.23281 | 0.98729 | -0.24349 | 20.2611
25 | 0.0074765 | 0.0018739 | -0.0074755 | -0.0018735 | 1.0095e-06 | 3.7417e-07 | 0.01126 | 0.01126 | 0.01126 | 0.98804 | -0.229 | 0.9879 | -0.23184 | 3.0934
26 | 0.0077338 | 0.0019383 | -0.0077332 | -0.001938 | 5.7777e-07 | 2.2018e-07 | 0.011566 | 0.011566 | 0.011566 | 0.99502 | -0.094828 | 0.99494 | -0.096396 | 3.1774
27 | 0.06485 | 0.016539 | -0.064713 | -0.016452 | 0.00013646 | 8.6849e-05 | 0.097749 | 0.097749 | 0.097749 | 0.98823 | -0.22445 | 0.98596 | -0.26813 | 26.8541
28 | 0.043492 | 0.010961 | -0.043455 | -0.010937 | 3.7298e-05 | 2.3575e-05 | 0.065572 | 0.065572 | 0.065572 | 0.98729 | -0.24349 | 0.98636 | -0.26143 | 18.0142
29 | 0.0038627 | 0.00096801 | -0.0038626 | -0.00096806 | 1.3614e-07 | -5.4134e-08 | 0.005777 | 0.0057771 | 0.0057771 | 0.99494 | -0.096396 | 0.9949 | -0.097136 | 1.5871
30 | -0.007643 | -0.0019155 | 0.0076436 | 0.0019158 | 6.2372e-07 | 2.4212e-07 | 0.011578 | 0.011578 | 0.011578 | 0.98226 | -0.34152 | 0.98234 | -0.3398 | 3.1809
31 | -0.013953 | -0.0034971 | 0.013955 | 0.0034982 | 1.8184e-06 | 1.0264e-06 | 0.021136 | 0.021136 | 0.021136 | 0.98234 | -0.3398 | 0.98248 | -0.33707 | 5.8066
32 | -0.020281 | -0.0050835 | 0.020285 | 0.0050861 | 4.3703e-06 | 2.6405e-06 | 0.030716 | 0.030716 | 0.030716 | 0.98248 | -0.33707 | 0.98271 | -0.33255 | 8.4386
33 | -0.027841 | -0.0069799 | 0.027858 | 0.0069903 | 1.6783e-05 | 1.0422e-05 | 0.042158 | 0.042157 | 0.042158 | 0.98271 | -0.33255 | 0.98336 | -0.3199 | 11.5818
34 | -0.027858 | -0.0069903 | 0.027872 | 0.0069993 | 1.4507e-05 | 9.0081e-06 | 0.042157 | 0.042157 | 0.042157 | 0.98336 | -0.3199 | 0.98392 | -0.30899 | 11.5817
35 | -0.032935 | -0.008268 | 0.032946 | 0.008275 | 1.1159e-05 | 6.9897e-06 | 0.049813 | 0.049813 | 0.049813 | 0.98392 | -0.30899 | 0.98428 | -0.30189 | 13.6849
36 | -0.050045 | -0.012584 | 0.050226 | 0.012699 | 0.00018087 | 0.00011471 | 0.076263 | 0.076262 | 0.076263 | 0.97666 | -0.44917 | 0.98051 | -0.37379 | 20.9513
37 | 0.020027 | 0.0050609 | -0.019995 | -0.0050417 | 3.1704e-05 | 1.9157e-05 | 0.030527 | 0.030528 | 0.030528 | 0.97666 | -0.44917 | 0.97497 | -0.48224 | 8.3867
38 | -0.057343 | -0.014483 | 0.057428 | 0.014536 | 8.4522e-05 | 5.3718e-05 | 0.087063 | 0.087063 | 0.087063 | 0.98051 | -0.37379 | 0.98209 | -0.34308 | 23.9185
39 | 0.019995 | 0.0050417 | -0.01992 | -0.0049964 | 7.4899e-05 | 4.5274e-05 | 0.030528 | 0.030529 | 0.030529 | 0.97497 | -0.48224 | 0.97098 | -0.56081 | 8.387
40 | -0.06448 | -0.016304 | 0.064713 | 0.016452 | 0.0002327 | 0.00014811 | 0.097749 | 0.097749 | 0.097749 | 0.98209 | -0.34308 | 0.98596 | -0.26813 | 26.8541
41 | 0.01992 | 0.0049964 | -0.019908 | -0.0049891 | 1.2162e-05 | 7.3535e-06 | 0.030529 | 0.030529 | 0.030529 | 0.97098 | -0.56081 | 0.97034 | -0.57363 | 8.387
42 | 0.002808 | 0.00070342 | -0.0028079 | -0.00070355 | 1.1418e-07 | -1.2976e-07 | 0.004306 | 0.004306 | 0.004306 | 0.97034 | -0.57363 | 0.97029 | -0.57448 | 1.183
43 | 0.0028079 | 0.00070355 | -0.0028078 | -0.00070369 | 1.2274e-07 | -1.3946e-07 | 0.004306 | 0.0043061 | 0.0043061 | 0.97029 | -0.57448 | 0.97025 | -0.5754 | 1.183
44 | 0.043455 | 0.010937 | -0.043448 | -0.010933 | 6.4253e-06 | 4.0613e-06 | 0.065572 | 0.065572 | 0.065572 | 0.98636 | -0.26143 | 0.9862 | -0.26453 | 18.0142
45 | 0.043448 | 0.010933 | -0.043427 | -0.01092 | 2.1554e-05 | 1.3624e-05 | 0.065572 | 0.065572 | 0.065572 | 0.9862 | -0.26453 | 0.98567 | -0.27492 | 18.0142
46 | 0.038125 | 0.0095908 | -0.03809 | -0.0095689 | 3.4794e-05 | 2.1912e-05 | 0.057568 | 0.057568 | 0.057568 | 0.98567 | -0.27492 | 0.98469 | -0.29404 | 15.8154
47 | -0.035505 | -0.0089208 | 0.035506 | 0.0089212 | 5.8574e-07 | 3.6797e-07 | 0.053663 | 0.053663 | 0.053663 | 0.98467 | -0.29438 | 0.98469 | -0.29404 | 14.7425
48 | 0.032958 | 0.0082824 | -0.032946 | -0.008275 | 1.1807e-05 | 7.3949e-06 | 0.049813 | 0.049813 | 0.049813 | 0.98467 | -0.29438 | 0.98428 | -0.30189 | 13.6849

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28137 | 0.071297

## res_load
| p_mw | q_mvar
0 | 0.006141 | 0.0015391
1 | 0.0054133 | 0.0013567
2 | 0.0025782 | 0.00064615
3 | 0.0054131 | 0.0013566
4 | 0.0025873 | 0.00064844
5 | 0.0043876 | 0.0010996
6 | 0.0076563 | 0.0019188
7 | 0.0092925 | 0.0023289
8 | 0.0060827 | 0.0015245
9 | 0.0051802 | 0.0012983
10 | 0.016331 | 0.0040929
11 | 0.011708 | 0.0029344
12 | 0.042625 | 0.010683
13 | 0.0043732 | 0.001096
14 | 0.0074755 | 0.0018735
15 | 0.0038652 | 0.00096872
16 | 0.010067 | 0.002523
17 | 0.0048451 | 0.0012143
18 | 0.0054266 | 0.00136
19 | 0.0038705 | 0.00097004
20 | 0.0038626 | 0.00096806
21 | 0.007643 | 0.0019155
22 | 0.0063098 | 0.0015814
23 | 0.0063256 | 0.0015853
24 | 0.007556 | 0.0018937
25 | 0.0050623 | 0.0012687
26 | 0.030019 | 0.0075234
27 | 0.0071172 | 0.0017837
28 | 0.0070526 | 0.0017676
29 | 0.0171 | 0.0042856
30 | 0.0028078 | 0.00070369
31 | 0.0053018 | 0.0013288
32 | 0.0025473 | 0.00063843
33 | 0.0025845 | 0.00064773

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1