## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-106_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-106_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-106_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-106_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-106_0_4_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_2701-106_0_4_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_2701-106_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2701-106_0_4_node_51 | 0.4 | n |  | TRUE
8 | bus_LV_2701-106_0_4_node_50 | 0.4 | n |  | TRUE
9 | bus_LV_2701-106_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2701-106_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2701-106_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_2701-106_0_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_2701-106_0_4_node_49 | 0.4 | n |  | TRUE
14 | bus_LV_2701-106_0_4_node_52 | 0.4 | n |  | TRUE
15 | bus_LV_2701-106_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_2701-106_0_4_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_2701-106_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2701-106_0_4_node_45 | 0.4 | n |  | TRUE
19 | bus_LV_2701-106_0_4_node_48 | 0.4 | n |  | TRUE
20 | bus_LV_2701-106_0_4_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_2701-106_0_4_node_55 | 0.4 | n |  | TRUE
22 | bus_LV_2701-106_0_4_node_53 | 0.4 | n |  | TRUE
23 | bus_LV_2701-106_0_4_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_2701-106_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2701-106_0_4_node_56 | 0.4 | n |  | TRUE
26 | bus_LV_2701-106_0_4_node_47 | 0.4 | n |  | TRUE
27 | bus_LV_2701-106_0_4_node_63 | 0.4 | n |  | TRUE
28 | bus_LV_2701-106_0_4_node_60 | 0.4 | n |  | TRUE
29 | bus_LV_2701-106_0_4_node_44 | 0.4 | n |  | TRUE
30 | bus_LV_2701-106_0_4_node_42 | 0.4 | n |  | TRUE
31 | bus_LV_2701-106_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_2701-106_0_4_node_59 | 0.4 | n |  | TRUE
33 | bus_LV_2701-106_0_4_node_54 | 0.4 | n |  | TRUE
34 | bus_LV_2701-106_0_4_node_43 | 0.4 | n |  | TRUE
35 | bus_LV_2701-106_0_4_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_2701-106_0_4_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_2701-106_0_4_node_16 | 0.4 | n |  | TRUE
38 | bus_LV_2701-106_0_4_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_2701-106_0_4_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_2701-106_0_4_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_2701-106_0_4_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_2701-106_0_4_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_2701-106_0_4_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_2701-106_0_4_node_24 | 0.4 | n |  | TRUE
45 | bus_LV_2701-106_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_2701-106_0_4_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_2701-106_0_4_node_31 | 0.4 | n |  | TRUE
48 | bus_LV_2701-106_0_4_node_26 | 0.4 | n |  | TRUE
49 | bus_LV_2701-106_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_2701-106_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_2701-106_0_4_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_2701-106_0_4_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_2701-106_0_4_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_2701-106_0_4_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_2701-106_0_4_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_2701-106_0_4_node_46 | 0.4 | n |  | TRUE
57 | bus_LV_2701-106_0_4_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_2701-106_0_4_node_58 | 0.4 | n |  | TRUE
59 | bus_LV_2701-106_0_4_node_61 | 0.4 | n |  | TRUE
60 | bus_LV_2701-106_0_4_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_2701-106_0_4_node_64 | 0.4 | n |  | TRUE
62 | bus_MV_556_0_node_115 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-106_0_4_load_0 | 0 | 0.033022 | 0.0082762 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-106_0_4_load_14 | 5 | 0.0040203 | 0.0010076 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-106_0_4_load_50 | 8 | 0.0040359 | 0.0010115 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-106_0_4_load_49 | 13 | 0.04225 | 0.010589 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-106_0_4_load_52 | 14 | 0.013926 | 0.0034901 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-106_0_4_load_28 | 16 | 0.0045437 | 0.0011388 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-106_0_4_load_45 | 18 | 0.0072687 | 0.0018217 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-106_0_4_load_48 | 19 | 0.020953 | 0.0052514 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-106_0_4_load_21 | 20 | 0.0078033 | 0.0019557 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-106_0_4_load_55 | 21 | 0.035133 | 0.008805 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-106_0_4_load_53 | 22 | 0.017419 | 0.0043655 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-106_0_4_load_29 | 23 | 0.0052301 | 0.0013108 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-106_0_4_load_15 | 24 | 0.022811 | 0.0057169 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-106_0_4_load_56 | 25 | 0.002614 | 0.00065514 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-106_0_4_load_47 | 26 | 0.016191 | 0.004058 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-106_0_4_load_63 | 27 | 0.03899 | 0.0097719 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-106_0_4_load_60 | 28 | 0.026771 | 0.0067096 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-106_0_4_load_44 | 29 | 0.0072427 | 0.0018152 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-106_0_4_load_42 | 30 | 0.0095757 | 0.0023999 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-106_0_4_load_59 | 32 | 0.0048218 | 0.0012085 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-106_0_4_load_54 | 33 | 0.017612 | 0.004414 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-106_0_4_load_43 | 34 | 0.04408 | 0.011047 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-106_0_4_load_41 | 35 | 0.0055638 | 0.0013944 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-106_0_4_load_32 | 36 | 0.0062923 | 0.001577 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-106_0_4_load_16 | 37 | 0.0053041 | 0.0013293 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-106_0_4_load_17 | 38 | 0.0044965 | 0.0011269 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-106_0_4_load_18 | 39 | 0.0057276 | 0.0014355 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-106_0_4_load_19 | 40 | 0.0087527 | 0.0021936 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-106_0_4_load_20 | 41 | 0.0126 | 0.0031578 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-106_0_4_load_27 | 42 | 0.0034003 | 0.0008522 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-106_0_4_load_30 | 43 | 0.0090981 | 0.0022802 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-106_0_4_load_35 | 45 | 0.0044028 | 0.0011034 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-106_0_4_load_23 | 46 | 0.0036309 | 0.00090998 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-106_0_4_load_31 | 47 | 0.0033858 | 0.00084856 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-106_0_4_load_39 | 49 | 0.0077954 | 0.0019537 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-106_0_4_load_36 | 50 | 0.0052566 | 0.0013174 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-106_0_4_load_40 | 51 | 0.012432 | 0.0031159 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-106_0_4_load_33 | 52 | 0.0055167 | 0.0013826 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-106_0_4_load_34 | 53 | 0.0060629 | 0.0015195 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-106_0_4_load_37 | 54 | 0.015496 | 0.0038838 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-106_0_4_load_38 | 55 | 0.020574 | 0.0051564 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2701-106_0_4_load_46 | 56 | 0.006274 | 0.0015724 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2701-106_0_4_load_57 | 57 | 0.0012572 | 0.00031509 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2701-106_0_4_load_58 | 58 | 0.0024908 | 0.00062426 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2701-106_0_4_load_61 | 59 | 0.0030724 | 0.00077002 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2701-106_0_4_load_62 | 60 | 0.012142 | 0.0030431 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2701-106_0_4_load_64 | 61 | 0.012676 | 0.0031768 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-106_0_4_line_0 |  | 0 | 1 | 0.013527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-106_0_4_line_1 |  | 0 | 2 | 0.02235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-106_0_4_line_2 |  | 1 | 3 | 0.017588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-106_0_4_line_3 |  | 2 | 4 | 0.013034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-106_0_4_line_4 |  | 3 | 5 | 0.029682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-106_0_4_line_5 |  | 4 | 23 | 0.0010859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-106_0_4_line_6 |  | 4 | 16 | 0.0081889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-106_0_4_line_7 |  | 6 | 7 | 0.023408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-106_0_4_line_8 |  | 6 | 8 | 0.0092273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-106_0_4_line_9 |  | 7 | 25 | 0.0045601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-106_0_4_line_10 |  | 7 | 24 | 0.040884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-106_0_4_line_11 |  | 8 | 10 | 0.0042752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-106_0_4_line_12 |  | 9 | 10 | 0.024936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2701-106_0_4_line_13 |  | 9 | 11 | 0.016958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2701-106_0_4_line_14 |  | 9 | 12 | 0.079382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2701-106_0_4_line_15 |  | 9 | 13 | 0.011522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_2701-106_0_4_line_16 |  | 10 | 14 | 0.011671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2701-106_0_4_line_17 |  | 11 | 20 | 0.0073451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-106_0_4_line_18 |  | 11 | 15 | 0.013289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-106_0_4_line_19 |  | 12 | 21 | 0.031968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-106_0_4_line_20 |  | 12 | 22 | 0.013206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-106_0_4_line_21 |  | 13 | 26 | 0.01744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-106_0_4_line_22 |  | 15 | 16 | 0.070893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-106_0_4_line_23 |  | 17 | 18 | 0.018135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-106_0_4_line_24 |  | 17 | 19 | 0.0071889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-106_0_4_line_25 |  | 18 | 29 | 0.0057796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-106_0_4_line_26 |  | 19 | 30 | 0.0043437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-106_0_4_line_27 |  | 20 | 31 | 0.032678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-106_0_4_line_28 |  | 21 | 32 | 0.0037706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-106_0_4_line_29 |  | 22 | 33 | 0.0086674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-106_0_4_line_30 |  | 23 | 36 | 0.0048986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-106_0_4_line_31 |  | 25 | 57 | 0.010412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-106_0_4_line_32 |  | 26 | 56 | 0.0068852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-106_0_4_line_33 |  | 27 | 28 | 0.0063027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-106_0_4_line_34 |  | 28 | 32 | 0.0068789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-106_0_4_line_35 |  | 29 | 56 | 0.0049024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-106_0_4_line_36 |  | 30 | 48 | 0.020485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-106_0_4_line_37 |  | 31 | 46 | 0.0088946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-106_0_4_line_38 |  | 34 | 35 | 0.010241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2701-106_0_4_line_39 |  | 35 | 51 | 0.0083636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2701-106_0_4_line_40 |  | 36 | 52 | 0.0051883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2701-106_0_4_line_41 |  | 37 | 38 | 0.0048341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-106_0_4_line_42 |  | 37 | 39 | 0.0052902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-106_0_4_line_43 |  | 38 | 40 | 0.0064723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-106_0_4_line_44 |  | 39 | 41 | 0.0088901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2701-106_0_4_line_45 |  | 40 | 42 | 0.006407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2701-106_0_4_line_46 |  | 41 | 43 | 0.010585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2701-106_0_4_line_47 |  | 42 | 44 | 0.0028754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2701-106_0_4_line_48 |  | 43 | 45 | 0.006376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2701-106_0_4_line_49 |  | 44 | 47 | 0.0024816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2701-106_0_4_line_50 |  | 45 | 50 | 0.0089361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2701-106_0_4_line_51 |  | 46 | 47 | 0.004536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2701-106_0_4_line_52 |  | 48 | 49 | 0.030444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2701-106_0_4_line_53 |  | 49 | 51 | 0.010332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2701-106_0_4_line_54 |  | 52 | 53 | 0.0054209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2701-106_0_4_line_55 |  | 53 | 54 | 0.0094562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2701-106_0_4_line_56 |  | 54 | 55 | 0.0044064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2701-106_0_4_line_57 |  | 57 | 58 | 0.00033089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2701-106_0_4_line_58 |  | 58 | 59 | 0.0090492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2701-106_0_4_line_59 |  | 59 | 60 | 0.012461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2701-106_0_4_line_60 |  | 60 | 61 | 0.013708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-106_0_4_trafo_52 | 0.63 MVA 20/0.4 kV | 62 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2611022.4113 | 1267921.6623 | 2611031.4387 | 1267931.7362
1 | 2611046.3544 | 1267948.381 | 2611031.4387 | 1267931.7362
2 | 2611008.0054 | 1267918.2332 | 2611017.9517 | 1267915.8166 | 2611022.4113 | 1267921.6623
3 | 2611046.3544 | 1267948.381 | 2611050.2298 | 1267952.7024 | 2611051.499 | 1267954.1168 | 2611052.1897 | 1267955.0632 | 2611054.0751 | 1267956.9903 | 2611055.059 | 1267958.0707
4 | 2611008.0054 | 1267918.2332 | 2611000.4747 | 1267920.7321 | 2610994.5086 | 1267923.712 | 2610982.5135 | 1267932.849
5 | 2611055.059 | 1267958.0707 | 2611054.5408 | 1267959.025
6 | 2611055.059 | 1267958.0707 | 2611058.9349 | 1267950.8572
7 | 2611085.0964 | 1267860.536 | 2611074.7899 | 1267850.2206 | 2611068.6907 | 1267843.7937
8 | 2611085.0964 | 1267860.536 | 2611091.6863 | 1267854.0771
9 | 2611068.6907 | 1267843.7937 | 2611066.2295 | 1267839.9548
10 | 2611068.6907 | 1267843.7937 | 2611054.5019 | 1267853.0071 | 2611034.6081 | 1267866.3711
11 | 2611095.854 | 1267855.03 | 2611091.6863 | 1267854.0771
12 | 2611095.854 | 1267855.03 | 2611105.3178 | 1267865.2103 | 2611108.1444 | 1267866.9057 | 2611109.3472 | 1267867.6307 | 2611110.7004 | 1267868.4449 | 2611114.7749 | 1267870.8987
13 | 2611106.3257 | 1267885.6154 | 2611114.7749 | 1267870.8987
14 | 2611114.7749 | 1267870.8987 | 2611110.7004 | 1267868.4449 | 2611109.3472 | 1267867.6307 | 2611110.9702 | 1267865.0097 | 2611113.3022 | 1267861.5672 | 2611120.9145 | 1267851.6745 | 2611133.3418 | 1267838.6997 | 2611151.414 | 1267821.5883 | 2611150.6705 | 1267820.7752 | 2611144.5274 | 1267813.7032
15 | 2611114.7749 | 1267870.8987 | 2611123.0176 | 1267862.8487
16 | 2611105.7495 | 1267851.6572 | 2611101.6024 | 1267855.8413 | 2611095.854 | 1267855.03
17 | 2611106.3257 | 1267885.6154 | 2611108.4831 | 1267887.0316 | 2611111.1003 | 1267888.0149 | 2611113.0338 | 1267888.3855
18 | 2611096.1865 | 1267890.5555 | 2611097.6528 | 1267891.2254 | 2611099.7809 | 1267892.1856 | 2611102.6972 | 1267890.1563 | 2611106.3257 | 1267885.6154
19 | 2611144.5274 | 1267813.7032 | 2611130.9044 | 1267798.0222 | 2611124.4589 | 1267788.8677
20 | 2611144.5274 | 1267813.7032 | 2611140.6172 | 1267819.9224 | 2611136.2507 | 1267823.8294
21 | 2611135.3797 | 1267850.552 | 2611133.1948 | 1267852.9094 | 2611123.0176 | 1267862.8487
22 | 2611096.1865 | 1267890.5555 | 2611061.9465 | 1267945.2523 | 2611058.9349 | 1267950.8572
23 | 2611161.1212 | 1267826.3876 | 2611155.2306 | 1267829.1341 | 2611147.3213 | 1267837.6677
24 | 2611161.1212 | 1267826.3876 | 2611165.1048 | 1267829.1749 | 2611165.6335 | 1267831.4411
25 | 2611143.3925 | 1267841.9067 | 2611147.3213 | 1267837.6677
26 | 2611166.6204 | 1267835.6711 | 2611165.6335 | 1267831.4411
27 | 2611125.1552 | 1267906.065 | 2611128.9969 | 1267900.2014 | 2611129.8889 | 1267898.1238 | 2611130.2619 | 1267895.8896 | 2611129.9339 | 1267894.2101 | 2611129.2752 | 1267892.2853 | 2611127.7658 | 1267890.47 | 2611125.119 | 1267889.2531 | 2611122.8768 | 1267888.9376 | 2611113.0338 | 1267888.3855
28 | 2611124.4589 | 1267788.8677 | 2611122.2882 | 1267785.7846
29 | 2611129.7915 | 1267829.6089 | 2611136.2507 | 1267823.8294
30 | 2611054.5408 | 1267959.025 | 2611052.2033 | 1267963.3299
31 | 2611066.2295 | 1267839.9548 | 2611060.6097 | 1267831.1892
32 | 2611135.3797 | 1267850.552 | 2611140.06 | 1267845.5022
33 | 2611117.2677 | 1267773.8261 | 2611117.3926 | 1267775.1253 | 2611118.6807 | 1267779.954
34 | 2611122.2882 | 1267785.7846 | 2611122.0621 | 1267785.4635 | 2611118.8052 | 1267780.4205 | 2611118.6807 | 1267779.954
35 | 2611143.3925 | 1267841.9067 | 2611140.06 | 1267845.5022
36 | 2611173.2914 | 1267850.1383 | 2611169.4216 | 1267846.8843 | 2611173.277 | 1267841.7991 | 2611166.6204 | 1267835.6711
37 | 2611125.1552 | 1267906.065 | 2611120.9463 | 1267913.9007
38 | 2611209.0497 | 1267802.9142 | 2611206.6987 | 1267806.7819 | 2611203.558 | 1267811.5562
39 | 2611198.9616 | 1267818.5435 | 2611203.558 | 1267811.5562
40 | 2611049.7277 | 1267967.8894 | 2611052.2033 | 1267963.3299
41 | 2611106.9158 | 1267937.667 | 2611109.4303 | 1267933.5384
42 | 2611106.9158 | 1267937.667 | 2611104.164 | 1267942.1851
43 | 2611109.4303 | 1267933.5384 | 2611112.7971 | 1267928.0107
44 | 2611099.5395 | 1267949.7778 | 2611104.164 | 1267942.1851
45 | 2611116.1298 | 1267922.5387 | 2611112.7971 | 1267928.0107
46 | 2611099.5395 | 1267949.7778 | 2611094.0335 | 1267958.8181
47 | 2611117.6255 | 1267920.083 | 2611116.1298 | 1267922.5387
48 | 2611090.7169 | 1267964.2635 | 2611094.0335 | 1267958.8181
49 | 2611117.6255 | 1267920.083 | 2611118.7998 | 1267917.8967
50 | 2611090.7169 | 1267964.2635 | 2611086.0685 | 1267971.8955
51 | 2611118.7998 | 1267917.8967 | 2611120.9463 | 1267913.9007
52 | 2611173.2914 | 1267850.1383 | 2611175.0872 | 1267847.7289 | 2611193.1487 | 1267827.0724
53 | 2611193.1487 | 1267827.0724 | 2611193.9657 | 1267826.1381 | 2611198.9616 | 1267818.5435
54 | 2611049.7277 | 1267967.8894 | 2611047.1409 | 1267972.6534
55 | 2611042.6287 | 1267980.9636 | 2611042.6287 | 1267980.9636 | 2611047.1409 | 1267972.6534
56 | 2611042.6287 | 1267980.9636 | 2611040.2612 | 1267984.68
57 | 2611060.6097 | 1267831.1892 | 2611060.4311 | 1267830.9106
58 | 2611060.4311 | 1267830.9106 | 2611055.5471 | 1267823.2926
59 | 2611055.5471 | 1267823.2926 | 2611048.8216 | 1267812.8025
60 | 2611041.8497 | 1267801.015 | 2611044.4818 | 1267806.0333 | 2611048.8216 | 1267812.8025

## bus_geodata
| x | y | coords
0 | 2611031.4387 | 1267931.7362
1 | 2611022.4113 | 1267921.6623
2 | 2611046.3544 | 1267948.381
3 | 2611008.0054 | 1267918.2332
4 | 2611055.059 | 1267958.0707
5 | 2610982.5135 | 1267932.849
6 | 2611085.0964 | 1267860.536
7 | 2611068.6907 | 1267843.7937
8 | 2611091.6863 | 1267854.0771
9 | 2611114.7749 | 1267870.8987
10 | 2611095.854 | 1267855.03
11 | 2611106.3257 | 1267885.6154
12 | 2611144.5274 | 1267813.7032
13 | 2611123.0176 | 1267862.8487
14 | 2611105.7495 | 1267851.6572
15 | 2611096.1865 | 1267890.5555
16 | 2611058.9349 | 1267950.8572
17 | 2611161.1212 | 1267826.3876
18 | 2611147.3213 | 1267837.6677
19 | 2611165.6335 | 1267831.4411
20 | 2611113.0338 | 1267888.3855
21 | 2611124.4589 | 1267788.8677
22 | 2611136.2507 | 1267823.8294
23 | 2611054.5408 | 1267959.025
24 | 2611034.6081 | 1267866.3711
25 | 2611066.2295 | 1267839.9548
26 | 2611135.3797 | 1267850.552
27 | 2611117.2677 | 1267773.8261
28 | 2611118.6807 | 1267779.954
29 | 2611143.3925 | 1267841.9067
30 | 2611166.6204 | 1267835.6711
31 | 2611125.1552 | 1267906.065
32 | 2611122.2882 | 1267785.7846
33 | 2611129.7915 | 1267829.6089
34 | 2611209.0497 | 1267802.9142
35 | 2611203.558 | 1267811.5562
36 | 2611052.2033 | 1267963.3299
37 | 2611106.9158 | 1267937.667
38 | 2611109.4303 | 1267933.5384
39 | 2611104.164 | 1267942.1851
40 | 2611112.7971 | 1267928.0107
41 | 2611099.5395 | 1267949.7778
42 | 2611116.1298 | 1267922.5387
43 | 2611094.0335 | 1267958.8181
44 | 2611117.6255 | 1267920.083
45 | 2611090.7169 | 1267964.2635
46 | 2611120.9463 | 1267913.9007
47 | 2611118.7998 | 1267917.8967
48 | 2611173.2914 | 1267850.1383
49 | 2611193.1487 | 1267827.0724
50 | 2611086.0685 | 1267971.8955
51 | 2611198.9616 | 1267818.5435
52 | 2611049.7277 | 1267967.8894
53 | 2611047.1409 | 1267972.6534
54 | 2611042.6287 | 1267980.9636
55 | 2611040.2612 | 1267984.68
56 | 2611140.06 | 1267845.5022
57 | 2611060.6097 | 1267831.1892
58 | 2611060.4311 | 1267830.9106
59 | 2611055.5471 | 1267823.2926
60 | 2611048.8216 | 1267812.8025
61 | 2611041.8497 | 1267801.015
62 | 2611095.854 | 1267855.03

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98457 | -0.29688 | 0.033022 | 0.0082762
1 | 0.98452 | -0.29786 | 0 | 0
2 | 0.98533 | -0.282 | 0 | 0
3 | 0.98446 | -0.29913 | 0 | 0
4 | 0.98578 | -0.27334 | 0 | 0
5 | 0.98435 | -0.30128 | 0.0040203 | 0.0010076
6 | 0.99779 | -0.042105 | 0 | 0
7 | 0.99658 | -0.065519 | 0 | 0
8 | 0.99827 | -0.032891 | 0.0040359 | 0.0010115
9 | 0.99568 | -0.082424 | 0 | 0
10 | 0.99851 | -0.028324 | 0 | 0
11 | 0.99432 | -0.10849 | 0 | 0
12 | 0.99055 | -0.18115 | 0 | 0
13 | 0.99473 | -0.10063 | 0.04225 | 0.010589
14 | 1 | 0 | -0.56353 | -0.14306
15 | 0.99308 | -0.13213 | 0 | 0
16 | 0.9865 | -0.25922 | 0.0045437 | 0.0011388
17 | 0.98899 | -0.21113 | 0 | 0
18 | 0.99067 | -0.17874 | 0.0072687 | 0.0018217
19 | 0.98832 | -0.224 | 0.020953 | 0.0052514
20 | 0.99382 | -0.11806 | 0.0078033 | 0.0019557
21 | 0.98744 | -0.24137 | 0.035133 | 0.008805
22 | 0.99012 | -0.18937 | 0.017419 | 0.0043655
23 | 0.98572 | -0.27449 | 0.0052301 | 0.0013108
24 | 0.99573 | -0.0819 | 0.022811 | 0.0057169
25 | 0.99643 | -0.068261 | 0.002614 | 0.00065514
26 | 0.99252 | -0.14293 | 0.016191 | 0.004058
27 | 0.98655 | -0.25863 | 0.03899 | 0.0097719
28 | 0.98678 | -0.25423 | 0.026771 | 0.0067096
29 | 0.99124 | -0.16769 | 0.0072427 | 0.0018152
30 | 0.98801 | -0.23016 | 0.0095757 | 0.0023999
31 | 0.99184 | -0.15623 | 0 | 0
32 | 0.9872 | -0.24613 | 0.0048218 | 0.0012085
33 | 0.98998 | -0.19209 | 0.017612 | 0.004414
34 | 0.98334 | -0.32105 | 0.04408 | 0.011047
35 | 0.98375 | -0.31292 | 0.0055638 | 0.0013944
36 | 0.98547 | -0.27923 | 0.0062923 | 0.001577
37 | 0.98996 | -0.19265 | 0.0053041 | 0.0013293
38 | 0.99015 | -0.18901 | 0.0044965 | 0.0011269
39 | 0.98978 | -0.19614 | 0.0057276 | 0.0014355
40 | 0.99043 | -0.18362 | 0.0087527 | 0.0021936
41 | 0.98953 | -0.2011 | 0.0126 | 0.0031578
42 | 0.99075 | -0.17728 | 0.0034003 | 0.0008522
43 | 0.98934 | -0.20464 | 0.0090981 | 0.0022802
44 | 0.99091 | -0.17427 | 0 | 0
45 | 0.98929 | -0.20574 | 0.0044028 | 0.0011034
46 | 0.9913 | -0.16665 | 0.0036309 | 0.00090998
47 | 0.99104 | -0.17167 | 0.0033858 | 0.00084856
48 | 0.98669 | -0.25575 | 0 | 0
49 | 0.98473 | -0.29391 | 0.0077954 | 0.0019537
50 | 0.98924 | -0.20657 | 0.0052566 | 0.0013174
51 | 0.98413 | -0.30545 | 0.012432 | 0.0031159
52 | 0.98525 | -0.28367 | 0.0055167 | 0.0013826
53 | 0.98504 | -0.28777 | 0.0060629 | 0.0015195
54 | 0.98472 | -0.2939 | 0.015496 | 0.0038838
55 | 0.98464 | -0.29553 | 0.020574 | 0.0051564
56 | 0.99176 | -0.15771 | 0.006274 | 0.0015724
57 | 0.99613 | -0.074046 | 0.0012572 | 0.00031509
58 | 0.99613 | -0.074222 | 0.0024908 | 0.00062426
59 | 0.9959 | -0.078657 | 0.0030724 | 0.00077002
60 | 0.99561 | -0.084093 | 0.012142 | 0.0030431
61 | 0.99546 | -0.087149 | 0.012676 | 0.0031768
62 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0040211 | 0.0010073 | -0.0040209 | -0.0010074 | 1.8734e-07 | -5.2125e-08 | 0.0060771 | 0.0060771 | 0.0060771 | 0.98457 | -0.29688 | 0.98452 | -0.29786 | 1.6695
1 | -0.037044 | -0.0092835 | 0.03707 | 0.0093001 | 2.627e-05 | 1.6528e-05 | 0.055985 | 0.055985 | 0.055985 | 0.98457 | -0.29688 | 0.98533 | -0.282 | 15.3805
2 | 0.0040209 | 0.0010074 | -0.0040207 | -0.0010075 | 2.4359e-07 | -6.7745e-08 | 0.0060771 | 0.0060772 | 0.0060772 | 0.98452 | -0.29786 | 0.98446 | -0.29913 | 1.6696
3 | -0.03707 | -0.0093001 | 0.037085 | 0.0093097 | 1.5319e-05 | 9.6384e-06 | 0.055985 | 0.055985 | 0.055985 | 0.98533 | -0.282 | 0.98578 | -0.27334 | 15.3805
4 | 0.0040207 | 0.0010075 | -0.0040203 | -0.0010076 | 4.111e-07 | -1.1425e-07 | 0.0060772 | 0.0060774 | 0.0060774 | 0.98446 | -0.29913 | 0.98435 | -0.30128 | 1.6696
5 | 0.059219 | 0.014859 | -0.059216 | -0.014857 | 3.2544e-06 | 2.069e-06 | 0.089396 | 0.089396 | 0.089396 | 0.98578 | -0.27334 | 0.98572 | -0.27449 | 24.5594
6 | -0.096304 | -0.024169 | 0.096369 | 0.02421 | 6.4904e-05 | 4.1434e-05 | 0.14538 | 0.14538 | 0.14538 | 0.98578 | -0.27334 | 0.9865 | -0.25922 | 39.9398
7 | 0.057172 | 0.01437 | -0.057108 | -0.014329 | 6.3833e-05 | 4.0548e-05 | 0.085275 | 0.085276 | 0.085276 | 0.99779 | -0.042105 | 0.99658 | -0.065519 | 23.4274
8 | -0.057172 | -0.01437 | 0.057197 | 0.014386 | 2.5163e-05 | 1.5983e-05 | 0.085275 | 0.085275 | 0.085275 | 0.99779 | -0.042105 | 0.99827 | -0.032891 | 23.4273
9 | 0.03428 | 0.0086014 | -0.034275 | -0.0085986 | 4.4806e-06 | 2.8081e-06 | 0.051187 | 0.051187 | 0.051187 | 0.99658 | -0.065519 | 0.99643 | -0.068261 | 14.0625
10 | 0.022829 | 0.0057278 | -0.022811 | -0.0057169 | 1.7815e-05 | 1.0869e-05 | 0.034088 | 0.034088 | 0.034088 | 0.99658 | -0.065519 | 0.99573 | -0.0819 | 9.3649
11 | -0.061233 | -0.015397 | 0.061246 | 0.015406 | 1.3361e-05 | 8.4953e-06 | 0.091291 | 0.091291 | 0.091291 | 0.99827 | -0.032891 | 0.99851 | -0.028324 | 25.08
12 | -0.49857 | -0.12634 | 0.49987 | 0.12717 | 0.0012996 | 0.00083042 | 0.74559 | 0.74559 | 0.74559 | 0.99568 | -0.082424 | 0.99851 | -0.028324 | 51.2083
13 | 0.176 | 0.04464 | -0.17577 | -0.0445 | 0.00022028 | 0.00014054 | 0.26321 | 0.26321 | 0.26321 | 0.99568 | -0.082424 | 0.99432 | -0.10849 | 36.1551
14 | 0.14179 | 0.035937 | -0.14112 | -0.03551 | 0.0006692 | 0.00042623 | 0.21204 | 0.21204 | 0.21204 | 0.99568 | -0.082424 | 0.99055 | -0.18115 | 29.1263
15 | 0.18079 | 0.04576 | -0.18063 | -0.045659 | 0.00015789 | 0.00010075 | 0.27034 | 0.27034 | 0.27034 | 0.99568 | -0.082424 | 0.99473 | -0.10063 | 37.1352
16 | -0.56112 | -0.14257 | 0.56188 | 0.14306 | 0.00076632 | 0.00048983 | 0.83688 | 0.83688 | 0.83688 | 0.99851 | -0.028324 | 1 | 0 | 57.4782
17 | 0.074131 | 0.018683 | -0.074097 | -0.018662 | 3.3922e-05 | 2.1615e-05 | 0.11098 | 0.11098 | 0.11098 | 0.99432 | -0.10849 | 0.99382 | -0.11806 | 30.4877
18 | 0.10164 | 0.025816 | -0.10153 | -0.025742 | 0.00011549 | 7.3742e-05 | 0.15223 | 0.15223 | 0.15223 | 0.99432 | -0.10849 | 0.99308 | -0.13213 | 41.8226
19 | 0.10607 | 0.026721 | -0.10577 | -0.026526 | 0.00030456 | 0.00019451 | 0.15939 | 0.15939 | 0.15939 | 0.99055 | -0.18115 | 0.98744 | -0.24137 | 43.7884
20 | 0.035047 | 0.0087895 | -0.035033 | -0.0087809 | 1.3727e-05 | 8.6156e-06 | 0.05265 | 0.05265 | 0.05265 | 0.99055 | -0.18115 | 0.99012 | -0.18937 | 14.4643
21 | 0.13838 | 0.035071 | -0.1381 | -0.034891 | 0.00028061 | 0.00017937 | 0.20714 | 0.20714 | 0.20714 | 0.99473 | -0.10063 | 0.99252 | -0.14293 | 56.9073
22 | 0.10153 | 0.025742 | -0.10091 | -0.025349 | 0.00061611 | 0.0003934 | 0.15223 | 0.15223 | 0.15223 | 0.99308 | -0.13213 | 0.9865 | -0.25922 | 41.8227
23 | -0.10077 | -0.025397 | 0.10092 | 0.025497 | 0.00015643 | 9.9879e-05 | 0.15166 | 0.15166 | 0.15166 | 0.98899 | -0.21113 | 0.99067 | -0.17874 | 41.6661
24 | 0.10077 | 0.025397 | -0.10071 | -0.025357 | 6.201e-05 | 3.9594e-05 | 0.15166 | 0.15166 | 0.15166 | 0.98899 | -0.21113 | 0.98832 | -0.224 | 41.6661
25 | -0.10819 | -0.027319 | 0.10825 | 0.027355 | 5.729e-05 | 3.6591e-05 | 0.16258 | 0.16258 | 0.16258 | 0.99067 | -0.17874 | 0.99124 | -0.16769 | 44.6655
26 | 0.079753 | 0.020106 | -0.079729 | -0.020091 | 2.3502e-05 | 1.4986e-05 | 0.12012 | 0.12012 | 0.12012 | 0.98832 | -0.224 | 0.98801 | -0.23016 | 32.9993
27 | 0.066294 | 0.016706 | -0.066173 | -0.016629 | 0.00012081 | 7.6899e-05 | 0.099292 | 0.099292 | 0.099292 | 0.99382 | -0.11806 | 0.99184 | -0.15623 | 27.278
28 | 0.070633 | 0.017721 | -0.070617 | -0.017711 | 1.6021e-05 | 1.0206e-05 | 0.10645 | 0.10645 | 0.10645 | 0.98744 | -0.24137 | 0.9872 | -0.24613 | 29.2437
29 | 0.017614 | 0.0044153 | -0.017612 | -0.004414 | 2.2777e-06 | 1.3463e-06 | 0.026472 | 0.026472 | 0.026472 | 0.99012 | -0.18937 | 0.98998 | -0.19209 | 7.2726
30 | 0.053985 | 0.013546 | -0.053973 | -0.013539 | 1.2202e-05 | 7.7468e-06 | 0.081501 | 0.081501 | 0.081501 | 0.98572 | -0.27449 | 0.98547 | -0.27923 | 22.3904
31 | 0.031661 | 0.0079434 | -0.031652 | -0.007938 | 8.7298e-06 | 5.4515e-06 | 0.047284 | 0.047284 | 0.047284 | 0.99643 | -0.068261 | 0.99613 | -0.074046 | 12.9901
32 | 0.12191 | 0.030833 | -0.12182 | -0.030778 | 8.6343e-05 | 5.517e-05 | 0.18287 | 0.18287 | 0.18287 | 0.99252 | -0.14293 | 0.99176 | -0.15771 | 50.2385
33 | -0.03899 | -0.0097719 | 0.038998 | 0.009777 | 8.1742e-06 | 5.151e-06 | 0.058809 | 0.058809 | 0.058809 | 0.98655 | -0.25863 | 0.98678 | -0.25423 | 16.1563
34 | -0.06577 | -0.016487 | 0.065795 | 0.016503 | 2.5374e-05 | 1.6151e-05 | 0.099179 | 0.099179 | 0.099179 | 0.98678 | -0.25423 | 0.9872 | -0.24613 | 27.247
35 | -0.11549 | -0.02917 | 0.11555 | 0.029206 | 5.5311e-05 | 3.5336e-05 | 0.17345 | 0.17345 | 0.17345 | 0.99124 | -0.16769 | 0.99176 | -0.15771 | 47.6524
36 | 0.070154 | 0.017691 | -0.070068 | -0.017636 | 8.582e-05 | 5.4663e-05 | 0.1057 | 0.1057 | 0.1057 | 0.98801 | -0.23016 | 0.98669 | -0.25575 | 29.0373
37 | 0.066173 | 0.016629 | -0.06614 | -0.016608 | 3.2884e-05 | 2.0931e-05 | 0.099292 | 0.099292 | 0.099292 | 0.99184 | -0.15623 | 0.9913 | -0.16665 | 27.278
38 | -0.04408 | -0.011047 | 0.044097 | 0.011058 | 1.7087e-05 | 1.0805e-05 | 0.066703 | 0.066703 | 0.066703 | 0.98334 | -0.32105 | 0.98375 | -0.31292 | 18.325
39 | -0.049661 | -0.012453 | 0.049678 | 0.012464 | 1.7698e-05 | 1.122e-05 | 0.075119 | 0.075119 | 0.075119 | 0.98375 | -0.31292 | 0.98413 | -0.30545 | 20.637
40 | 0.047681 | 0.011962 | -0.047671 | -0.011955 | 1.0086e-05 | 6.3889e-06 | 0.072 | 0.072 | 0.072 | 0.98547 | -0.27923 | 0.98525 | -0.28367 | 19.7802
41 | -0.042407 | -0.010634 | 0.042414 | 0.010639 | 7.3658e-06 | 4.6519e-06 | 0.063744 | 0.063744 | 0.063744 | 0.98996 | -0.19265 | 0.99015 | -0.18901 | 17.512
42 | 0.037102 | 0.009305 | -0.037096 | -0.0093011 | 6.1705e-06 | 3.8811e-06 | 0.055771 | 0.055771 | 0.055771 | 0.98996 | -0.19265 | 0.98978 | -0.19614 | 15.3217
43 | -0.04691 | -0.011766 | 0.046922 | 0.011774 | 1.2064e-05 | 7.6376e-06 | 0.070501 | 0.070501 | 0.070501 | 0.99015 | -0.18901 | 0.99043 | -0.18362 | 19.3685
44 | 0.031369 | 0.0078657 | -0.031361 | -0.0078611 | 7.4147e-06 | 4.6312e-06 | 0.04716 | 0.04716 | 0.04716 | 0.98978 | -0.19614 | 0.98953 | -0.2011 | 12.9562
45 | -0.055675 | -0.013967 | 0.055692 | 0.013978 | 1.6812e-05 | 1.0677e-05 | 0.083651 | 0.083651 | 0.083651 | 0.99043 | -0.18362 | 0.99075 | -0.17728 | 22.9811
46 | 0.018761 | 0.0047032 | -0.018758 | -0.0047013 | 3.1596e-06 | 1.8862e-06 | 0.028213 | 0.028213 | 0.028213 | 0.98953 | -0.2011 | 0.98934 | -0.20464 | 7.7509
47 | -0.059092 | -0.01483 | 0.059101 | 0.014836 | 8.4946e-06 | 5.3995e-06 | 0.088758 | 0.088758 | 0.088758 | 0.99075 | -0.17728 | 0.99091 | -0.17427 | 24.3841
48 | 0.0096601 | 0.0024211 | -0.0096596 | -0.0024209 | 5.0474e-07 | 2.4116e-07 | 0.014529 | 0.014529 | 0.014529 | 0.98934 | -0.20464 | 0.98929 | -0.20574 | 3.9916
49 | -0.059101 | -0.014836 | 0.059108 | 0.01484 | 7.3314e-06 | 4.6601e-06 | 0.088758 | 0.088758 | 0.088758 | 0.99091 | -0.17427 | 0.99104 | -0.17167 | 24.3841
50 | 0.0052568 | 0.0013175 | -0.0052566 | -0.0013174 | 2.0951e-07 | 1.9353e-08 | 0.0079069 | 0.007907 | 0.007907 | 0.98929 | -0.20574 | 0.98924 | -0.20657 | 2.1722
51 | 0.062509 | 0.015698 | -0.062494 | -0.015689 | 1.4979e-05 | 9.5284e-06 | 0.093842 | 0.093842 | 0.093842 | 0.9913 | -0.16665 | 0.99104 | -0.17167 | 25.7807
52 | 0.070068 | 0.017636 | -0.06994 | -0.017555 | 0.00012754 | 8.1239e-05 | 0.1057 | 0.1057 | 0.1057 | 0.98669 | -0.25575 | 0.98473 | -0.29391 | 29.0374
53 | 0.062145 | 0.015601 | -0.062111 | -0.01558 | 3.4173e-05 | 2.1739e-05 | 0.093916 | 0.093916 | 0.093916 | 0.98473 | -0.29391 | 0.98413 | -0.30545 | 25.8012
54 | 0.042154 | 0.010573 | -0.042146 | -0.010567 | 8.2404e-06 | 5.2048e-06 | 0.063668 | 0.063668 | 0.063668 | 0.98525 | -0.28367 | 0.98504 | -0.28777 | 17.4912
55 | 0.036083 | 0.0090478 | -0.036072 | -0.0090412 | 1.0536e-05 | 6.6229e-06 | 0.054509 | 0.054509 | 0.054509 | 0.98504 | -0.28777 | 0.98472 | -0.2939 | 14.9751
56 | 0.020576 | 0.0051574 | -0.020574 | -0.0051564 | 1.5975e-06 | 9.6633e-07 | 0.031093 | 0.031093 | 0.031093 | 0.98472 | -0.2939 | 0.98464 | -0.29553 | 8.542
57 | 0.030395 | 0.0076229 | -0.030395 | -0.0076227 | 2.5582e-07 | 1.5942e-07 | 0.045406 | 0.045406 | 0.045406 | 0.99613 | -0.074046 | 0.99613 | -0.074222 | 12.4741
58 | 0.027904 | 0.0069985 | -0.027898 | -0.0069948 | 5.8966e-06 | 3.6561e-06 | 0.041685 | 0.041685 | 0.041685 | 0.99613 | -0.074222 | 0.9959 | -0.078657 | 11.4519
59 | 0.024826 | 0.0062248 | -0.024819 | -0.0062209 | 6.4298e-06 | 3.953e-06 | 0.037094 | 0.037094 | 0.037094 | 0.9959 | -0.078657 | 0.99561 | -0.084093 | 10.1908
60 | 0.012677 | 0.0031778 | -0.012676 | -0.0031768 | 1.8454e-06 | 1.0028e-06 | 0.018947 | 0.018948 | 0.018948 | 0.99561 | -0.084093 | 0.99546 | -0.087149 | 5.2054

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57746 | 0.14655

## res_load
| p_mw | q_mvar
0 | 0.033022 | 0.0082762
1 | 0.0040203 | 0.0010076
2 | 0.0040359 | 0.0010115
3 | 0.04225 | 0.010589
4 | 0.013926 | 0.0034901
5 | 0.0045437 | 0.0011388
6 | 0.0072687 | 0.0018217
7 | 0.020953 | 0.0052514
8 | 0.0078033 | 0.0019557
9 | 0.035133 | 0.008805
10 | 0.017419 | 0.0043655
11 | 0.0052301 | 0.0013108
12 | 0.022811 | 0.0057169
13 | 0.002614 | 0.00065514
14 | 0.016191 | 0.004058
15 | 0.03899 | 0.0097719
16 | 0.026771 | 0.0067096
17 | 0.0072427 | 0.0018152
18 | 0.0095757 | 0.0023999
19 | 0.0048218 | 0.0012085
20 | 0.017612 | 0.004414
21 | 0.04408 | 0.011047
22 | 0.0055638 | 0.0013944
23 | 0.0062923 | 0.001577
24 | 0.0053041 | 0.0013293
25 | 0.0044965 | 0.0011269
26 | 0.0057276 | 0.0014355
27 | 0.0087527 | 0.0021936
28 | 0.0126 | 0.0031578
29 | 0.0034003 | 0.0008522
30 | 0.0090981 | 0.0022802
31 | 0.0044028 | 0.0011034
32 | 0.0036309 | 0.00090998
33 | 0.0033858 | 0.00084856
34 | 0.0077954 | 0.0019537
35 | 0.0052566 | 0.0013174
36 | 0.012432 | 0.0031159
37 | 0.0055167 | 0.0013826
38 | 0.0060629 | 0.0015195
39 | 0.015496 | 0.0038838
40 | 0.020574 | 0.0051564
41 | 0.006274 | 0.0015724
42 | 0.0012572 | 0.00031509
43 | 0.0024908 | 0.00062426
44 | 0.0030724 | 0.00077002
45 | 0.012142 | 0.0030431
46 | 0.012676 | 0.0031768

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1