## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-114_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-114_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-114_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-114_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-114_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-114_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2701-114_0_5_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_2701-114_0_5_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2701-114_0_5_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_2701-114_0_5_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_2701-114_0_5_node_33 | 0.4 | n |  | TRUE
11 | bus_LV_2701-114_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2701-114_0_5_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_2701-114_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2701-114_0_5_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2701-114_0_5_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_2701-114_0_5_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_2701-114_0_5_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_2701-114_0_5_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_2701-114_0_5_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_2701-114_0_5_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_2701-114_0_5_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_2701-114_0_5_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2701-114_0_5_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_2701-114_0_5_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_2701-114_0_5_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_2701-114_0_5_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_2701-114_0_5_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_2701-114_0_5_node_39 | 0.4 | n |  | TRUE
29 | bus_LV_2701-114_0_5_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_2701-114_0_5_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_2701-114_0_5_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_2701-114_0_5_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_2701-114_0_5_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_2701-114_0_5_node_40 | 0.4 | n |  | TRUE
35 | bus_LV_2701-114_0_5_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_2701-114_0_5_node_36 | 0.4 | n |  | TRUE
37 | bus_MV_558_0_node_125 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-114_0_5_load_0 | 0 | 0.037746 | 0.00946 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-114_0_5_load_1 | 1 | 0.033598 | 0.0084204 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-114_0_5_load_4 | 4 | 0.01682 | 0.0042155 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-114_0_5_load_5 | 5 | 0.00838 | 0.0021002 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-114_0_5_load_8 | 7 | 0.071875 | 0.018014 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-114_0_5_load_25 | 8 | 0.0018572 | 0.00046547 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-114_0_5_load_34 | 9 | 0.03252 | 0.0081503 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-114_0_5_load_33 | 10 | 0.0079374 | 0.0019893 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-114_0_5_load_7 | 11 | 0.0060897 | 0.0015262 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-114_0_5_load_13 | 12 | 0.0025451 | 0.00063787 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-114_0_5_load_9 | 13 | 0.012345 | 0.0030939 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-114_0_5_load_10 | 14 | 0.052579 | 0.013177 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-114_0_5_load_14 | 15 | 0.013719 | 0.0034382 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-114_0_5_load_15 | 16 | 0.0069351 | 0.0017381 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-114_0_5_load_20 | 17 | 0.086755 | 0.021743 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-114_0_5_load_16 | 18 | 0.0088594 | 0.0022204 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-114_0_5_load_26 | 19 | 0.0044237 | 0.0011087 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-114_0_5_load_27 | 20 | 0.022195 | 0.0055626 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-114_0_5_load_17 | 21 | 0.012417 | 0.0031119 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-114_0_5_load_19 | 23 | 0.010854 | 0.0027203 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-114_0_5_load_21 | 24 | 0.020874 | 0.0052315 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-114_0_5_load_22 | 27 | 0.0090139 | 0.0022591 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-114_0_5_load_39 | 28 | 0.0039196 | 0.00098235 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-114_0_5_load_37 | 29 | 0.011541 | 0.0028924 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-114_0_5_load_28 | 30 | 0.0091432 | 0.0022915 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-114_0_5_load_29 | 31 | 0.0040753 | 0.0010214 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-114_0_5_load_30 | 32 | 0.0041889 | 0.0010498 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-114_0_5_load_31 | 33 | 0.0037739 | 0.00094584 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-114_0_5_load_40 | 34 | 0.015087 | 0.0037811 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-114_0_5_load_36 | 36 | 0.0059321 | 0.0014867 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-114_0_5_line_0 |  | 0 | 1 | 0.040164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-114_0_5_line_1 |  | 0 | 2 | 0.013839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-114_0_5_line_2 |  | 1 | 3 | 0.041759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-114_0_5_line_3 |  | 1 | 4 | 0.017438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-114_0_5_line_4 |  | 2 | 5 | 0.017685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-114_0_5_line_5 |  | 3 | 6 | 0.041275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2701-114_0_5_line_6 |  | 3 | 7 | 0.03228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2701-114_0_5_line_7 |  | 5 | 8 | 0.024333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-114_0_5_line_8 |  | 6 | 9 | 0.052462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-114_0_5_line_9 |  | 6 | 10 | 0.023902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_2701-114_0_5_line_10 |  | 7 | 11 | 0.017731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2701-114_0_5_line_11 |  | 8 | 12 | 0.015367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-114_0_5_line_12 |  | 10 | 17 | 0.00091527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2701-114_0_5_line_13 |  | 11 | 13 | 0.0084559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2701-114_0_5_line_14 |  | 13 | 14 | 0.011772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-114_0_5_line_15 |  | 14 | 15 | 0.00050625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-114_0_5_line_16 |  | 15 | 16 | 0.013758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-114_0_5_line_17 |  | 16 | 18 | 0.0097186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-114_0_5_line_18 |  | 17 | 22 | 0.033885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-114_0_5_line_19 |  | 18 | 19 | 0.0096879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-114_0_5_line_20 |  | 19 | 20 | 0.0016273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-114_0_5_line_21 |  | 20 | 30 | 0.0088858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-114_0_5_line_22 |  | 21 | 22 | 0.020811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-114_0_5_line_23 |  | 21 | 23 | 0.025159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-114_0_5_line_24 |  | 22 | 24 | 0.021276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-114_0_5_line_25 |  | 24 | 25 | 0.0048443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-114_0_5_line_26 |  | 25 | 26 | 0.015131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-114_0_5_line_27 |  | 25 | 27 | 0.034121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-114_0_5_line_28 |  | 26 | 28 | 0.025167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-114_0_5_line_29 |  | 28 | 29 | 0.0089621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-114_0_5_line_30 |  | 29 | 36 | 0.0082707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-114_0_5_line_31 |  | 30 | 31 | 0.0045776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-114_0_5_line_32 |  | 31 | 32 | 0.0050278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-114_0_5_line_33 |  | 32 | 33 | 0.0040995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-114_0_5_line_34 |  | 34 | 35 | 0.0049174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-114_0_5_line_35 |  | 35 | 36 | 0.0035745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-114_0_5_trafo_3 | 0.63 MVA 20/0.4 kV | 37 | 3 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2611519.3919 | 1267311.5995 | 2611552.5493 | 1267334.2647
1 | 2611563.9739 | 1267342.0741 | 2611552.5493 | 1267334.2647
2 | 2611542.5367 | 1267276.7978 | 2611519.3919 | 1267311.5995
3 | 2611519.3919 | 1267311.5995 | 2611510.3263 | 1267326.4957
4 | 2611563.9739 | 1267342.0741 | 2611551.3178 | 1267354.4269
5 | 2611582.2457 | 1267266.4901 | 2611579.3889 | 1267268.5749 | 2611575.6676 | 1267270.1465 | 2611571.5406 | 1267271.3171 | 2611550.0431 | 1267275.6338 | 2611549.1772 | 1267275.8101 | 2611542.5367 | 1267276.7978
6 | 2611542.5367 | 1267276.7978 | 2611523.2298 | 1267261.5608 | 2611517.7014 | 1267256.223
7 | 2611551.3178 | 1267354.4269 | 2611533.9043 | 1267371.4234
8 | 2611582.2457 | 1267266.4901 | 2611615.7285 | 1267291.6064 | 2611610.2844 | 1267300.7088
9 | 2611582.2457 | 1267266.4901 | 2611584.8023 | 1267263.9044 | 2611590.6344 | 1267256.8108 | 2611597.5451 | 1267248.1472
10 | 2611506.0074 | 1267243.0574 | 2611508.7828 | 1267247.612 | 2611517.7014 | 1267256.223
11 | 2611522.907 | 1267382.1572 | 2611533.9043 | 1267371.4234
12 | 2611597.5451 | 1267248.1472 | 2611598.1159 | 1267247.4317
13 | 2611506.0074 | 1267243.0574 | 2611501.6072 | 1267235.8365
14 | 2611501.6072 | 1267235.8365 | 2611499.5165 | 1267232.4056 | 2611493.1324 | 1267228.005
15 | 2611493.1324 | 1267228.005 | 2611492.7156 | 1267227.7177
16 | 2611482.4979 | 1267218.7705 | 2611482.9819 | 1267219.7537 | 2611485.7833 | 1267222.9391 | 2611492.7156 | 1267227.7177
17 | 2611480.5218 | 1267209.3591 | 2611481.4149 | 1267216.5706 | 2611482.4979 | 1267218.7705
18 | 2611619.2463 | 1267220.9416 | 2611598.1159 | 1267247.4317
19 | 2611479.3311 | 1267199.7446 | 2611480.5218 | 1267209.3591
20 | 2611479.3311 | 1267199.7446 | 2611479.131 | 1267198.1296
21 | 2611479.131 | 1267198.1296 | 2611478.0389 | 1267189.3112
22 | 2611619.2463 | 1267220.9416 | 2611635.4744 | 1267233.9701
23 | 2611655.0931 | 1267249.7208 | 2611635.4744 | 1267233.9701
24 | 2611619.2463 | 1267220.9416 | 2611632.4605 | 1267204.2668
25 | 2611635.4693 | 1267200.4701 | 2611632.4605 | 1267204.2668
26 | 2611645.4347 | 1267189.0594 | 2611640.0634 | 1267195.2199 | 2611635.4693 | 1267200.4701
27 | 2611635.4693 | 1267200.4701 | 2611654.1248 | 1267213.8605 | 2611664.1394 | 1267218.779
28 | 2611645.4347 | 1267189.0594 | 2611626.7189 | 1267175.6245 | 2611624.9141 | 1267174.4963
29 | 2611617.3147 | 1267169.7457 | 2611624.9141 | 1267174.4963
30 | 2611610.3015 | 1267165.3616 | 2611617.3147 | 1267169.7457
31 | 2611477.4763 | 1267184.7683 | 2611478.0389 | 1267189.3112
32 | 2611477.4763 | 1267184.7683 | 2611477.3461 | 1267183.7176 | 2611476.1189 | 1267179.943
33 | 2611476.1189 | 1267179.943 | 2611474.8513 | 1267176.0445
34 | 2611607.2705 | 1267163.4669 | 2611602.7214 | 1267161.5997
35 | 2611607.2705 | 1267163.4669 | 2611610.3015 | 1267165.3616

## bus_geodata
| x | y | coords
0 | 2611552.5493 | 1267334.2647
1 | 2611519.3919 | 1267311.5995
2 | 2611563.9739 | 1267342.0741
3 | 2611542.5367 | 1267276.7978
4 | 2611510.3263 | 1267326.4957
5 | 2611551.3178 | 1267354.4269
6 | 2611582.2457 | 1267266.4901
7 | 2611517.7014 | 1267256.223
8 | 2611533.9043 | 1267371.4233
9 | 2611610.2844 | 1267300.7088
10 | 2611597.5451 | 1267248.1472
11 | 2611506.0074 | 1267243.0574
12 | 2611522.907 | 1267382.1572
13 | 2611501.6072 | 1267235.8365
14 | 2611493.1324 | 1267228.005
15 | 2611492.7156 | 1267227.7177
16 | 2611482.4979 | 1267218.7705
17 | 2611598.1159 | 1267247.4317
18 | 2611480.5218 | 1267209.3591
19 | 2611479.3311 | 1267199.7446
20 | 2611479.131 | 1267198.1296
21 | 2611635.4744 | 1267233.9701
22 | 2611619.2463 | 1267220.9416
23 | 2611655.0931 | 1267249.7208
24 | 2611632.4605 | 1267204.2668
25 | 2611635.4693 | 1267200.4701
26 | 2611645.4347 | 1267189.0594
27 | 2611664.1394 | 1267218.779
28 | 2611624.9141 | 1267174.4963
29 | 2611617.3147 | 1267169.7457
30 | 2611478.0389 | 1267189.3112
31 | 2611477.4763 | 1267184.7683
32 | 2611476.1189 | 1267179.943
33 | 2611474.8513 | 1267176.0445
34 | 2611602.7214 | 1267161.5997
35 | 2611607.2705 | 1267163.4669
36 | 2611610.3015 | 1267165.3616
37 | 2611582.2457 | 1267266.4901

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99431 | -0.10947 | 0.037746 | 0.00946
1 | 0.99616 | -0.073759 | 0.033598 | 0.0084204
2 | 0.99415 | -0.11259 | 0 | 0
3 | 1 | 0 | -0.54287 | -0.13689
4 | 0.99589 | -0.078912 | 0.01682 | 0.0042155
5 | 0.99394 | -0.11658 | 0.00838 | 0.0021002
6 | 0.99591 | -0.078325 | 0 | 0
7 | 0.99676 | -0.062148 | 0.071875 | 0.018014
8 | 0.99384 | -0.11847 | 0.0018572 | 0.00046547
9 | 0.99435 | -0.10835 | 0.03252 | 0.0081503
10 | 0.99389 | -0.11712 | 0.0079374 | 0.0019893
11 | 0.99556 | -0.085245 | 0.0060897 | 0.0015262
12 | 0.99381 | -0.11916 | 0.0025451 | 0.00063787
13 | 0.99501 | -0.095826 | 0.012345 | 0.0030939
14 | 0.99361 | -0.12278 | 0.052579 | 0.013177
15 | 0.99358 | -0.12347 | 0.013719 | 0.0034382
16 | 0.99278 | -0.13893 | 0.0069351 | 0.0017381
17 | 0.99382 | -0.11854 | 0.086755 | 0.021743
18 | 0.99227 | -0.14868 | 0.0088594 | 0.0022204
19 | 0.99185 | -0.15688 | 0.0044237 | 0.0011087
20 | 0.99178 | -0.15813 | 0.022195 | 0.0055626
21 | 0.99059 | -0.1809 | 0.012417 | 0.0031119
22 | 0.99103 | -0.1723 | 0 | 0
23 | 0.99034 | -0.18575 | 0.010854 | 0.0027203
24 | 0.98974 | -0.19739 | 0.020874 | 0.0052315
25 | 0.98954 | -0.20131 | 0 | 0
26 | 0.98903 | -0.21114 | 0 | 0
27 | 0.98925 | -0.20679 | 0.0090139 | 0.0022591
28 | 0.98819 | -0.22751 | 0.0039196 | 0.00098235
29 | 0.98792 | -0.23272 | 0.011541 | 0.0028924
30 | 0.99161 | -0.16146 | 0.0091432 | 0.0022915
31 | 0.99156 | -0.16244 | 0.0040753 | 0.0010214
32 | 0.99153 | -0.16315 | 0.0041889 | 0.0010498
33 | 0.99151 | -0.16342 | 0.0037739 | 0.00094584
34 | 0.98764 | -0.23812 | 0.015087 | 0.0037811
35 | 0.98771 | -0.23679 | 0 | 0
36 | 0.98776 | -0.23583 | 0.0059321 | 0.0014867
37 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.050533 | -0.012666 | 0.050619 | 0.01272 | 8.6138e-05 | 5.4606e-05 | 0.075625 | 0.075625 | 0.075625 | 0.99431 | -0.10947 | 0.99616 | -0.073759 | 20.7761
1 | 0.012787 | 0.0032057 | -0.012785 | -0.0032047 | 1.9005e-06 | 1.0368e-06 | 0.019137 | 0.019137 | 0.019137 | 0.99431 | -0.10947 | 0.99415 | -0.11259 | 5.2574
2 | -0.10104 | -0.025359 | 0.1014 | 0.025586 | 0.00035679 | 0.0002278 | 0.15094 | 0.15094 | 0.15094 | 0.99616 | -0.073759 | 1 | 0 | 41.4679
3 | 0.016824 | 0.0042179 | -0.01682 | -0.0042155 | 4.1301e-06 | 2.4163e-06 | 0.025131 | 0.025132 | 0.025132 | 0.99616 | -0.073759 | 0.99589 | -0.078912 | 6.9043
4 | 0.012785 | 0.0032047 | -0.012783 | -0.0032034 | 2.4288e-06 | 1.3251e-06 | 0.019137 | 0.019137 | 0.019137 | 0.99415 | -0.11259 | 0.99394 | -0.11658 | 5.2574
5 | 0.21846 | 0.055375 | -0.21764 | -0.054852 | 0.00081893 | 0.00052303 | 0.3253 | 0.3253 | 0.3253 | 1 | 0 | 0.99591 | -0.078325 | 44.6835
6 | 0.22136 | 0.055929 | -0.22071 | -0.055509 | 0.00065732 | 0.00041984 | 0.32955 | 0.32955 | 0.32955 | 1 | 0 | 0.99676 | -0.062148 | 45.2681
7 | 0.0044028 | 0.0011031 | -0.0044024 | -0.0011032 | 3.9645e-07 | -6.1622e-08 | 0.0065913 | 0.0065914 | 0.0065914 | 0.99394 | -0.11658 | 0.99384 | -0.11847 | 1.8108
8 | 0.032567 | 0.0081795 | -0.03252 | -0.0081503 | 4.6593e-05 | 2.9138e-05 | 0.048665 | 0.048666 | 0.048666 | 0.99591 | -0.078325 | 0.99435 | -0.10835 | 13.3696
9 | 0.18508 | 0.046672 | -0.18473 | -0.046453 | 0.00034295 | 0.00021887 | 0.27663 | 0.27663 | 0.27663 | 0.99591 | -0.078325 | 0.99389 | -0.11712 | 37.9987
10 | 0.14883 | 0.037496 | -0.14867 | -0.037391 | 0.00016422 | 0.00010464 | 0.22225 | 0.22225 | 0.22225 | 0.99676 | -0.062148 | 0.99556 | -0.085245 | 30.5292
11 | 0.0025452 | 0.00063772 | -0.0025451 | -0.00063787 | 8.3686e-08 | -1.4557e-07 | 0.0038107 | 0.0038108 | 0.0038108 | 0.99384 | -0.11847 | 0.99381 | -0.11916 | 1.0469
12 | 0.1768 | 0.044464 | -0.17678 | -0.044456 | 1.2029e-05 | 7.6746e-06 | 0.26475 | 0.26475 | 0.26475 | 0.99389 | -0.11712 | 0.99382 | -0.11854 | 36.3664
13 | 0.14258 | 0.035865 | -0.14251 | -0.035819 | 7.2034e-05 | 4.5882e-05 | 0.21315 | 0.21315 | 0.21315 | 0.99556 | -0.085245 | 0.99501 | -0.095826 | 29.279
14 | 0.13016 | 0.032725 | -0.12999 | -0.032618 | 0.00016732 | 0.00010693 | 0.19469 | 0.19469 | 0.19469 | 0.99501 | -0.095826 | 0.99361 | -0.12278 | 53.4862
15 | 0.077415 | 0.019441 | -0.077412 | -0.019439 | 2.5523e-06 | 1.6269e-06 | 0.11595 | 0.11595 | 0.11595 | 0.99361 | -0.12278 | 0.99358 | -0.12347 | 31.8541
16 | 0.063694 | 0.016001 | -0.063647 | -0.015971 | 4.6957e-05 | 2.9875e-05 | 0.095403 | 0.095403 | 0.095403 | 0.99358 | -0.12347 | 0.99278 | -0.13893 | 26.2097
17 | 0.056711 | 0.014233 | -0.056685 | -0.014216 | 2.6337e-05 | 1.673e-05 | 0.085009 | 0.085009 | 0.085009 | 0.99278 | -0.13893 | 0.99227 | -0.14868 | 23.354
18 | 0.09003 | 0.022714 | -0.089799 | -0.022566 | 0.00023108 | 0.00014745 | 0.13485 | 0.13485 | 0.13485 | 0.99382 | -0.11854 | 0.99103 | -0.1723 | 37.0473
19 | 0.047826 | 0.011996 | -0.047807 | -0.011984 | 1.8689e-05 | 1.1836e-05 | 0.071723 | 0.071723 | 0.071723 | 0.99227 | -0.14868 | 0.99185 | -0.15688 | 19.7041
20 | 0.043383 | 0.010875 | -0.043381 | -0.010874 | 2.5851e-06 | 1.6335e-06 | 0.065086 | 0.065086 | 0.065086 | 0.99185 | -0.15688 | 0.99178 | -0.15813 | 17.8809
21 | 0.021186 | 0.005311 | -0.021182 | -0.0053089 | 3.3667e-06 | 2.04e-06 | 0.031786 | 0.031786 | 0.031786 | 0.99178 | -0.15813 | 0.99161 | -0.16146 | 8.7325
22 | -0.023273 | -0.0058335 | 0.023283 | 0.0058394 | 9.5383e-06 | 5.8365e-06 | 0.03496 | 0.03496 | 0.03496 | 0.99059 | -0.1809 | 0.99103 | -0.1723 | 9.6045
23 | 0.010857 | 0.0027216 | -0.010854 | -0.0027203 | 2.5094e-06 | 1.2822e-06 | 0.016309 | 0.016309 | 0.016309 | 0.99059 | -0.1809 | 0.99034 | -0.18575 | 4.4805
24 | 0.066516 | 0.016727 | -0.066436 | -0.016676 | 7.9612e-05 | 5.0678e-05 | 0.099892 | 0.099892 | 0.099892 | 0.99103 | -0.1723 | 0.98974 | -0.19739 | 27.4429
25 | 0.045562 | 0.011445 | -0.045554 | -0.011439 | 8.5265e-06 | 5.3947e-06 | 0.06851 | 0.06851 | 0.06851 | 0.98974 | -0.19739 | 0.98954 | -0.20131 | 18.8213
26 | 0.036538 | 0.0091791 | -0.03652 | -0.0091683 | 1.7134e-05 | 1.0771e-05 | 0.054951 | 0.054951 | 0.054951 | 0.98954 | -0.20131 | 0.98903 | -0.21114 | 15.0965
27 | 0.0090163 | 0.0022602 | -0.0090139 | -0.0022591 | 2.3522e-06 | 1.0672e-06 | 0.013558 | 0.013559 | 0.013559 | 0.98954 | -0.20131 | 0.98925 | -0.20679 | 3.7249
28 | 0.03652 | 0.0091683 | -0.036492 | -0.0091504 | 2.8498e-05 | 1.7916e-05 | 0.054951 | 0.054951 | 0.054951 | 0.98903 | -0.21114 | 0.98819 | -0.22751 | 15.0965
29 | 0.032572 | 0.0081681 | -0.032564 | -0.008163 | 8.0855e-06 | 5.0599e-06 | 0.049049 | 0.049049 | 0.049049 | 0.98819 | -0.22751 | 0.98792 | -0.23272 | 13.4751
30 | 0.021023 | 0.0052706 | -0.02102 | -0.0052687 | 3.1101e-06 | 1.8846e-06 | 0.031666 | 0.031666 | 0.031666 | 0.98792 | -0.23272 | 0.98776 | -0.23583 | 8.6996
31 | 0.012039 | 0.0030174 | -0.012038 | -0.0030171 | 5.6025e-07 | 2.9951e-07 | 0.018066 | 0.018066 | 0.018066 | 0.99161 | -0.16146 | 0.99156 | -0.16244 | 4.9631
32 | 0.0079632 | 0.0019958 | -0.0079629 | -0.0019957 | 2.6925e-07 | 1.0747e-07 | 0.01195 | 0.01195 | 0.01195 | 0.99156 | -0.16244 | 0.99153 | -0.16315 | 3.283
33 | 0.003774 | 0.00094582 | -0.0037739 | -0.00094584 | 4.9314e-08 | -2.1313e-08 | 0.0056637 | 0.0056638 | 0.0056638 | 0.99153 | -0.16315 | 0.99151 | -0.16342 | 1.556
34 | -0.015087 | -0.0037811 | 0.015088 | 0.0037816 | 9.5271e-07 | 5.468e-07 | 0.02273 | 0.02273 | 0.02273 | 0.98764 | -0.23812 | 0.98771 | -0.23679 | 6.2445
35 | -0.015088 | -0.0037816 | 0.015088 | 0.003782 | 6.9254e-07 | 3.9748e-07 | 0.02273 | 0.02273 | 0.02273 | 0.98771 | -0.23679 | 0.98776 | -0.23583 | 6.2445

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.54287 | 0.13689

## res_load
| p_mw | q_mvar
0 | 0.037746 | 0.00946
1 | 0.033598 | 0.0084204
2 | 0.01682 | 0.0042155
3 | 0.00838 | 0.0021002
4 | 0.071875 | 0.018014
5 | 0.0018572 | 0.00046547
6 | 0.03252 | 0.0081503
7 | 0.0079374 | 0.0019893
8 | 0.0060897 | 0.0015262
9 | 0.0025451 | 0.00063787
10 | 0.012345 | 0.0030939
11 | 0.052579 | 0.013177
12 | 0.013719 | 0.0034382
13 | 0.0069351 | 0.0017381
14 | 0.086755 | 0.021743
15 | 0.0088594 | 0.0022204
16 | 0.0044237 | 0.0011087
17 | 0.022195 | 0.0055626
18 | 0.012417 | 0.0031119
19 | 0.010854 | 0.0027203
20 | 0.020874 | 0.0052315
21 | 0.0090139 | 0.0022591
22 | 0.0039196 | 0.00098235
23 | 0.011541 | 0.0028924
24 | 0.0091432 | 0.0022915
25 | 0.0040753 | 0.0010214
26 | 0.0041889 | 0.0010498
27 | 0.0037739 | 0.00094584
28 | 0.015087 | 0.0037811
29 | 0.0059321 | 0.0014867

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1