## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-120_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-120_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-120_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-120_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-120_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-120_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2701-120_0_4_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_2701-120_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2701-120_0_4_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_2701-120_0_4_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_2701-120_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2701-120_0_4_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_2701-120_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2701-120_0_4_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_2701-120_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2701-120_0_4_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_2701-120_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2701-120_0_4_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_2701-120_0_4_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_2701-120_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_2701-120_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_2701-120_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_2701-120_0_4_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_2701-120_0_4_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_2701-120_0_4_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_2701-120_0_4_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_2701-120_0_4_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_2701-120_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_2701-120_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_2701-120_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_2701-120_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_2701-120_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2701-120_0_4_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_2701-120_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_2701-120_0_4_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_2701-120_0_4_node_31 | 0.4 | n |  | TRUE
36 | bus_MV_558_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-120_0_4_load_0 | 0 | 0.021007 | 0.005265 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-120_0_4_load_1 | 1 | 0.022656 | 0.0056781 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-120_0_4_load_3 | 3 | 0.022713 | 0.0056924 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-120_0_4_load_4 | 4 | 0.0042629 | 0.0010684 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-120_0_4_load_27 | 6 | 0.011153 | 0.0027951 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-120_0_4_load_6 | 7 | 0.020756 | 0.0052019 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-120_0_4_load_22 | 8 | 0.0088997 | 0.0022305 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-120_0_4_load_26 | 9 | 0.02187 | 0.0054812 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-120_0_4_load_20 | 11 | 0.0017905 | 0.00044873 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-120_0_4_load_8 | 12 | 0.010505 | 0.0026328 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-120_0_4_load_32 | 13 | 0.0085125 | 0.0021334 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-120_0_4_load_36 | 17 | 0.0030978 | 0.00077639 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-120_0_4_load_16 | 18 | 0.015917 | 0.0039891 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-120_0_4_load_15 | 19 | 0.03685 | 0.0092355 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-120_0_4_load_17 | 21 | 0.014344 | 0.0035949 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-120_0_4_load_38 | 22 | 0.058979 | 0.014782 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-120_0_4_load_30 | 23 | 0.009286 | 0.0023273 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-120_0_4_load_34 | 24 | 0.020237 | 0.0050718 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-120_0_4_load_35 | 25 | 0.041014 | 0.010279 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-120_0_4_load_28 | 26 | 0.042169 | 0.010569 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-120_0_4_load_24 | 27 | 0.010678 | 0.002676 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-120_0_4_load_18 | 29 | 0.0039426 | 0.0009881 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-120_0_4_load_19 | 30 | 0.0032511 | 0.0008148 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-120_0_4_load_21 | 31 | 0.0089851 | 0.0022519 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-120_0_4_load_37 | 32 | 0.022917 | 0.0057435 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-120_0_4_load_23 | 33 | 0.0061525 | 0.001542 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-120_0_4_load_29 | 34 | 0.014903 | 0.0037351 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-120_0_4_load_31 | 35 | 0.060542 | 0.015173 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-120_0_4_line_0 |  | 0 | 1 | 0.0017627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_2701-120_0_4_line_1 |  | 0 | 2 | 0.013099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2701-120_0_4_line_2 |  | 1 | 3 | 0.023765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_2701-120_0_4_line_3 |  | 2 | 4 | 0.024969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-120_0_4_line_4 |  | 2 | 5 | 0.015131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-120_0_4_line_5 |  | 3 | 6 | 0.018155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2701-120_0_4_line_6 |  | 4 | 7 | 0.0061824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-120_0_4_line_7 |  | 5 | 8 | 0.019674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-120_0_4_line_8 |  | 6 | 9 | 0.013718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2701-120_0_4_line_9 |  | 7 | 10 | 0.014823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-120_0_4_line_10 |  | 8 | 11 | 0.026509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-120_0_4_line_11 |  | 9 | 26 | 0.011161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_2701-120_0_4_line_12 |  | 10 | 12 | 0.018311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-120_0_4_line_13 |  | 11 | 29 | 0.0012534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-120_0_4_line_14 |  | 12 | 13 | 0.00077002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-120_0_4_line_15 |  | 13 | 23 | 0.0092635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-120_0_4_line_16 |  | 14 | 15 | 0.087631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-120_0_4_line_17 |  | 14 | 16 | 0.013483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-120_0_4_line_18 |  | 14 | 17 | 0.035176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-120_0_4_line_19 |  | 15 | 22 | 0.007162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-120_0_4_line_20 |  | 16 | 18 | 0.021335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_2701-120_0_4_line_21 |  | 16 | 19 | 0.015011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-120_0_4_line_22 |  | 17 | 25 | 0.0079829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-120_0_4_line_23 |  | 18 | 26 | 0.0010603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2701-120_0_4_line_24 |  | 19 | 20 | 0.0078318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-120_0_4_line_25 |  | 20 | 21 | 0.030815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-120_0_4_line_26 |  | 21 | 27 | 0.00066985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-120_0_4_line_27 |  | 23 | 34 | 0.014092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-120_0_4_line_28 |  | 24 | 25 | 0.03056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-120_0_4_line_29 |  | 27 | 28 | 0.019086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-120_0_4_line_30 |  | 28 | 33 | 0.065338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-120_0_4_line_31 |  | 29 | 30 | 0.0068333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-120_0_4_line_32 |  | 30 | 31 | 0.0069834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-120_0_4_line_33 |  | 31 | 32 | 0.0027865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-120_0_4_line_34 |  | 34 | 35 | 0.031326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-120_0_4_trafo_27 | 0.63 MVA 20/0.4 kV | 36 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2611654.4526 | 1267179.5589 | 2611655.6668 | 1267178.281
1 | 2611645.4347 | 1267189.0594 | 2611649.9074 | 1267184.3427 | 2611654.4526 | 1267179.5589
2 | 2611655.6668 | 1267178.281 | 2611663.8686 | 1267169.6487 | 2611672.7875 | 1267161.835
3 | 2611645.4347 | 1267189.0594 | 2611626.7189 | 1267175.6245 | 2611625.082 | 1267174.6012
4 | 2611645.4347 | 1267189.0594 | 2611640.0634 | 1267195.2199 | 2611635.4693 | 1267200.4701
5 | 2611687.3869 | 1267151.1146 | 2611678.0513 | 1267157.2234 | 2611672.7875 | 1267161.835
6 | 2611619.8396 | 1267171.3241 | 2611625.082 | 1267174.6012
7 | 2611635.4693 | 1267200.4701 | 2611651.452 | 1267211.9421
8 | 2611687.3869 | 1267151.1146 | 2611693.705 | 1267146.9804 | 2611699.1059 | 1267144.0027
9 | 2611607.2705 | 1267163.4669 | 2611619.8396 | 1267171.3241
10 | 2611674.9657 | 1267224.0961 | 2611654.1248 | 1267213.8605 | 2611651.452 | 1267211.9421
11 | 2611708.8799 | 1267138.614 | 2611699.1059 | 1267144.0027
12 | 2611607.2705 | 1267163.4669 | 2611604.6604 | 1267145.3425
13 | 2611674.9657 | 1267224.0961 | 2611676.0907 | 1267224.6486
14 | 2611604.5507 | 1267144.5803 | 2611604.6604 | 1267145.3425
15 | 2611603.2303 | 1267135.4114 | 2611604.5507 | 1267144.5803
16 | 2611663.991 | 1267072.8368 | 2611707.6295 | 1267089.9123 | 2611728.8196 | 1267100.6283 | 2611727.9499 | 1267102.6947 | 2611727.2616 | 1267104.35 | 2611726.823 | 1267105.4054 | 2611725.7113 | 1267108.0607 | 2611725.1894 | 1267109.3049 | 2611724.8718 | 1267110.0604 | 2611724.5091 | 1267110.7713 | 2611723.3831 | 1267113.0262 | 2611721.8189 | 1267116.1364
17 | 2611728.3974 | 1267127.6352 | 2611724.4693 | 1267123.3244 | 2611721.8189 | 1267116.1364
18 | 2611721.8189 | 1267116.1364 | 2611689.9764 | 1267101.1893
19 | 2611667.1049 | 1267066.3828 | 2611663.991 | 1267072.8368
20 | 2611728.3974 | 1267127.6352 | 2611725.0741 | 1267129.5967 | 2611719.6486 | 1267132.677 | 2611709.8084 | 1267138.1021
21 | 2611728.3974 | 1267127.6352 | 2611731.9199 | 1267131.5004 | 2611740.7905 | 1267135.6214
22 | 2611689.9764 | 1267101.1893 | 2611682.75 | 1267097.7972
23 | 2611708.8799 | 1267138.614 | 2611709.8084 | 1267138.1021
24 | 2611747.9859 | 1267137.4029 | 2611746.005 | 1267138.0439 | 2611740.7905 | 1267135.6214
25 | 2611747.9859 | 1267137.4029 | 2611763.0772 | 1267164.2692
26 | 2611763.4053 | 1267164.8533 | 2611763.0772 | 1267164.2692
27 | 2611601.2216 | 1267121.4629 | 2611603.2303 | 1267135.4114
28 | 2611655.0865 | 1267084.8118 | 2611682.75 | 1267097.7972
29 | 2611772.7526 | 1267181.4939 | 2611763.4053 | 1267164.8533
30 | 2611772.7526 | 1267181.4939 | 2611755.6926 | 1267244.5658
31 | 2611682.2242 | 1267227.6609 | 2611676.0907 | 1267224.6486
32 | 2611682.2242 | 1267227.6609 | 2611688.4924 | 1267230.7394
33 | 2611690.9935 | 1267231.9678 | 2611688.4924 | 1267230.7394
34 | 2611601.2216 | 1267121.4629 | 2611598.1362 | 1267100.038 | 2611602.2985 | 1267091.2986

## bus_geodata
| x | y | coords
0 | 2611654.4526 | 1267179.5589
1 | 2611655.6668 | 1267178.281
2 | 2611645.4347 | 1267189.0594
3 | 2611672.7875 | 1267161.835
4 | 2611625.082 | 1267174.6012
5 | 2611635.4693 | 1267200.4701
6 | 2611687.3869 | 1267151.1146
7 | 2611619.8396 | 1267171.3241
8 | 2611651.452 | 1267211.9421
9 | 2611699.1059 | 1267144.0027
10 | 2611607.2705 | 1267163.4669
11 | 2611674.9657 | 1267224.0961
12 | 2611604.6604 | 1267145.3425
13 | 2611604.5507 | 1267144.5803
14 | 2611721.8189 | 1267116.1364
15 | 2611663.991 | 1267072.8368
16 | 2611728.3974 | 1267127.6352
17 | 2611689.9764 | 1267101.1893
18 | 2611709.8084 | 1267138.1021
19 | 2611740.7905 | 1267135.6214
20 | 2611747.9859 | 1267137.4029
21 | 2611763.0772 | 1267164.2692
22 | 2611667.1049 | 1267066.3828
23 | 2611603.2303 | 1267135.4114
24 | 2611655.0865 | 1267084.8118
25 | 2611682.75 | 1267097.7972
26 | 2611708.8799 | 1267138.614
27 | 2611763.4053 | 1267164.8533
28 | 2611772.7526 | 1267181.4939
29 | 2611676.0907 | 1267224.6486
30 | 2611682.2242 | 1267227.6609
31 | 2611688.4924 | 1267230.7394
32 | 2611690.9935 | 1267231.9678
33 | 2611755.6926 | 1267244.5658
34 | 2611601.2216 | 1267121.4629
35 | 2611602.2985 | 1267091.2986
36 | 2611728.3974 | 1267127.6352

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99538 | -0.08825 | 0.021007 | 0.005265
1 | 0.99554 | -0.085156 | 0.022656 | 0.0056781
2 | 0.9943 | -0.10885 | 0 | 0
3 | 0.99796 | -0.038832 | 0.022713 | 0.0056924
4 | 0.99135 | -0.1657 | 0.0042629 | 0.0010684
5 | 0.99362 | -0.12214 | 0 | 0
6 | 1 | 0 | -0.52192 | -0.13196
7 | 0.99064 | -0.17936 | 0.020756 | 0.0052019
8 | 0.99272 | -0.13944 | 0.0088997 | 0.0022305
9 | 0.9983 | -0.032491 | 0.02187 | 0.0054812
10 | 0.98922 | -0.20671 | 0 | 0
11 | 0.99173 | -0.15863 | 0.0017905 | 0.00044873
12 | 0.98747 | -0.24061 | 0.010505 | 0.0026328
13 | 0.98741 | -0.2419 | 0.0085125 | 0.0021334
14 | 0.99353 | -0.12398 | 0 | 0
15 | 0.98879 | -0.21567 | 0 | 0
16 | 0.99506 | -0.09466 | 0 | 0
17 | 0.99146 | -0.16403 | 0.0030978 | 0.00077639
18 | 0.99693 | -0.058794 | 0.015917 | 0.0039891
19 | 0.99413 | -0.11265 | 0.03685 | 0.0092355
20 | 0.9939 | -0.11696 | 0 | 0
21 | 0.99303 | -0.13392 | 0.014344 | 0.0035949
22 | 0.98841 | -0.22321 | 0.058979 | 0.014782
23 | 0.98668 | -0.25594 | 0.009286 | 0.0023273
24 | 0.99045 | -0.18368 | 0.020237 | 0.0050718
25 | 0.99102 | -0.1727 | 0.041014 | 0.010279
26 | 0.99703 | -0.056867 | 0.042169 | 0.010569
27 | 0.99302 | -0.13412 | 0.010678 | 0.002676
28 | 0.99291 | -0.1362 | 0 | 0
29 | 0.99168 | -0.1595 | 0.0039426 | 0.0009881
30 | 0.99146 | -0.16376 | 0.0032511 | 0.0008148
31 | 0.99126 | -0.16771 | 0.0089851 | 0.0022519
32 | 0.9912 | -0.16884 | 0.022917 | 0.0057435
33 | 0.99254 | -0.14331 | 0.0061525 | 0.001542
34 | 0.9857 | -0.27499 | 0.014903 | 0.0037351
35 | 0.98396 | -0.30907 | 0.060542 | 0.015173
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.20084 | -0.050827 | 0.20087 | 0.050846 | 2.9827e-05 | 1.9044e-05 | 0.30041 | 0.30041 | 0.30041 | 0.99538 | -0.08825 | 0.99554 | -0.085156 | 41.2649
1 | 0.17983 | 0.045562 | -0.17965 | -0.045449 | 0.00017773 | 0.00011341 | 0.269 | 0.269 | 0.269 | 0.99538 | -0.08825 | 0.9943 | -0.10885 | 36.9511
2 | -0.22352 | -0.056525 | 0.22402 | 0.056843 | 0.00049789 | 0.00031803 | 0.33427 | 0.33427 | 0.33427 | 0.99554 | -0.085156 | 0.99796 | -0.038832 | 45.9165
3 | 0.12974 | 0.032892 | -0.12938 | -0.032666 | 0.00035346 | 0.00022589 | 0.19429 | 0.19429 | 0.19429 | 0.9943 | -0.10885 | 0.99135 | -0.1657 | 53.3769
4 | 0.049912 | 0.012557 | -0.04988 | -0.012537 | 3.1672e-05 | 2.0074e-05 | 0.074712 | 0.074712 | 0.074712 | 0.9943 | -0.10885 | 0.99362 | -0.12214 | 20.5253
5 | -0.24673 | -0.062535 | 0.24719 | 0.06283 | 0.00046133 | 0.00029478 | 0.36814 | 0.36814 | 0.36814 | 0.99796 | -0.038832 | 1 | 0 | 50.5684
6 | 0.12512 | 0.031598 | -0.12504 | -0.031545 | 8.1848e-05 | 5.2303e-05 | 0.18789 | 0.18789 | 0.18789 | 0.99135 | -0.1657 | 0.99064 | -0.17936 | 51.6191
7 | 0.04988 | 0.012537 | -0.049839 | -0.012511 | 4.1181e-05 | 2.6102e-05 | 0.074712 | 0.074712 | 0.074712 | 0.99362 | -0.12214 | 0.99272 | -0.13944 | 20.5254
8 | 0.27308 | 0.069126 | -0.27266 | -0.068854 | 0.00042521 | 0.00027177 | 0.40659 | 0.40659 | 0.40659 | 1 | 0 | 0.9983 | -0.032491 | 55.8503
9 | 0.10428 | 0.026343 | -0.10415 | -0.026256 | 0.00013652 | 8.7182e-05 | 0.15672 | 0.15672 | 0.15672 | 0.99064 | -0.17936 | 0.98922 | -0.20671 | 43.054
10 | 0.040939 | 0.010281 | -0.040902 | -0.010257 | 3.7443e-05 | 2.3621e-05 | 0.061372 | 0.061372 | 0.061372 | 0.99272 | -0.13944 | 0.99173 | -0.15863 | 16.8606
11 | 0.25078 | 0.063373 | -0.25049 | -0.063186 | 0.00029271 | 0.00018704 | 0.37399 | 0.37399 | 0.37399 | 0.9983 | -0.032491 | 0.99703 | -0.056867 | 51.3724
12 | 0.10415 | 0.026256 | -0.10398 | -0.026148 | 0.00016865 | 0.0001077 | 0.15672 | 0.15672 | 0.15672 | 0.98922 | -0.20671 | 0.98747 | -0.24061 | 43.0541
13 | 0.039111 | 0.0098083 | -0.03911 | -0.0098072 | 1.6188e-06 | 1.0199e-06 | 0.058686 | 0.058686 | 0.058686 | 0.99173 | -0.15863 | 0.99168 | -0.1595 | 16.1225
14 | 0.093474 | 0.023516 | -0.093468 | -0.023512 | 5.7316e-06 | 3.6584e-06 | 0.14089 | 0.14089 | 0.14089 | 0.98747 | -0.24061 | 0.98741 | -0.2419 | 38.7053
15 | 0.084956 | 0.021379 | -0.084899 | -0.021342 | 5.6967e-05 | 3.6341e-05 | 0.12806 | 0.12806 | 0.12806 | 0.98741 | -0.2419 | 0.98668 | -0.25594 | 35.181
16 | 0.059259 | 0.01496 | -0.059 | -0.014795 | 0.00025908 | 0.00016468 | 0.088791 | 0.088791 | 0.088791 | 0.99353 | -0.12398 | 0.98879 | -0.21567 | 24.3932
17 | -0.12377 | -0.031188 | 0.12394 | 0.031299 | 0.00017384 | 0.00011108 | 0.18542 | 0.18542 | 0.18542 | 0.99353 | -0.12398 | 0.99506 | -0.09466 | 50.9408
18 | 0.064507 | 0.016228 | -0.064384 | -0.01615 | 0.00012318 | 7.838e-05 | 0.096634 | 0.096634 | 0.096634 | 0.99353 | -0.12398 | 0.99146 | -0.16403 | 26.5478
19 | 0.059 | 0.014795 | -0.058979 | -0.014782 | 2.1174e-05 | 1.346e-05 | 0.088791 | 0.088791 | 0.088791 | 0.98879 | -0.21567 | 0.98841 | -0.22321 | 24.3932
20 | -0.19206 | -0.048405 | 0.19239 | 0.048616 | 0.00033018 | 0.00021076 | 0.2873 | 0.2873 | 0.2873 | 0.99506 | -0.09466 | 0.99693 | -0.058794 | 39.4641
21 | 0.068117 | 0.017106 | -0.068058 | -0.017069 | 5.842e-05 | 3.7194e-05 | 0.10187 | 0.10187 | 0.10187 | 0.99506 | -0.09466 | 0.99413 | -0.11265 | 27.9875
22 | 0.061286 | 0.015373 | -0.061261 | -0.015357 | 2.5329e-05 | 1.6108e-05 | 0.091985 | 0.091985 | 0.091985 | 0.99146 | -0.16403 | 0.99102 | -0.1727 | 25.2705
23 | -0.2083 | -0.052605 | 0.20832 | 0.052617 | 1.9235e-05 | 1.2283e-05 | 0.31106 | 0.31106 | 0.31106 | 0.99693 | -0.058794 | 0.99703 | -0.056867 | 42.7275
24 | 0.031208 | 0.0078334 | -0.031202 | -0.0078294 | 6.4098e-06 | 4.0008e-06 | 0.046717 | 0.046717 | 0.046717 | 0.99413 | -0.11265 | 0.9939 | -0.11696 | 12.8343
25 | 0.031202 | 0.0078294 | -0.031177 | -0.0078136 | 2.522e-05 | 1.5742e-05 | 0.046717 | 0.046717 | 0.046717 | 0.9939 | -0.11696 | 0.99303 | -0.13392 | 12.8344
26 | 0.016833 | 0.0042187 | -0.016833 | -0.0042187 | 1.5982e-07 | 9.3618e-08 | 0.025224 | 0.025224 | 0.025224 | 0.99303 | -0.13392 | 0.99302 | -0.13412 | 6.9296
27 | 0.075613 | 0.019015 | -0.075544 | -0.018971 | 6.8745e-05 | 4.3817e-05 | 0.11405 | 0.11405 | 0.11405 | 0.98668 | -0.25594 | 0.9857 | -0.27499 | 31.3337
28 | -0.020237 | -0.0050718 | 0.020247 | 0.0050781 | 1.0593e-05 | 6.3857e-06 | 0.030403 | 0.030403 | 0.030403 | 0.99045 | -0.18368 | 0.99102 | -0.1727 | 8.3524
29 | 0.0061552 | 0.0015426 | -0.0061546 | -0.0015425 | 6.089e-07 | 1.4281e-07 | 0.0092235 | 0.0092236 | 0.0092236 | 0.99302 | -0.13412 | 0.99291 | -0.1362 | 2.5339
30 | 0.0061546 | 0.0015425 | -0.0061525 | -0.001542 | 2.0845e-06 | 4.8934e-07 | 0.0092236 | 0.0092239 | 0.0092239 | 0.99291 | -0.1362 | 0.99254 | -0.14331 | 2.534
31 | 0.035167 | 0.0088191 | -0.03516 | -0.0088147 | 7.1357e-06 | 4.4787e-06 | 0.05277 | 0.05277 | 0.05277 | 0.99168 | -0.1595 | 0.99146 | -0.16376 | 14.4973
32 | 0.031909 | 0.0079999 | -0.031903 | -0.0079961 | 6.0062e-06 | 3.7539e-06 | 0.047891 | 0.047891 | 0.047891 | 0.99146 | -0.16376 | 0.99126 | -0.16771 | 13.1569
33 | 0.022918 | 0.0057442 | -0.022917 | -0.0057435 | 1.2367e-06 | 7.556e-07 | 0.034403 | 0.034403 | 0.034403 | 0.99126 | -0.16771 | 0.9912 | -0.16884 | 9.4514
34 | 0.060641 | 0.015236 | -0.060542 | -0.015173 | 9.8473e-05 | 6.2624e-05 | 0.091557 | 0.091557 | 0.091557 | 0.9857 | -0.27499 | 0.98396 | -0.30907 | 25.153

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53308 | 0.13475

## res_load
| p_mw | q_mvar
0 | 0.021007 | 0.005265
1 | 0.022656 | 0.0056781
2 | 0.022713 | 0.0056924
3 | 0.0042629 | 0.0010684
4 | 0.011153 | 0.0027951
5 | 0.020756 | 0.0052019
6 | 0.0088997 | 0.0022305
7 | 0.02187 | 0.0054812
8 | 0.0017905 | 0.00044873
9 | 0.010505 | 0.0026328
10 | 0.0085125 | 0.0021334
11 | 0.0030978 | 0.00077639
12 | 0.015917 | 0.0039891
13 | 0.03685 | 0.0092355
14 | 0.014344 | 0.0035949
15 | 0.058979 | 0.014782
16 | 0.009286 | 0.0023273
17 | 0.020237 | 0.0050718
18 | 0.041014 | 0.010279
19 | 0.042169 | 0.010569
20 | 0.010678 | 0.002676
21 | 0.0039426 | 0.0009881
22 | 0.0032511 | 0.0008148
23 | 0.0089851 | 0.0022519
24 | 0.022917 | 0.0057435
25 | 0.0061525 | 0.001542
26 | 0.014903 | 0.0037351
27 | 0.060542 | 0.015173

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1