## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-125_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-125_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-125_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-125_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-125_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2701-125_0_6_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_2701-125_0_6_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_2701-125_0_6_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2701-125_0_6_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_2701-125_0_6_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_2701-125_0_6_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_2701-125_0_6_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_2701-125_0_6_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_2701-125_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2701-125_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2701-125_0_6_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2701-125_0_6_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2701-125_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_2701-125_0_6_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_2701-125_0_6_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_2701-125_0_6_node_26 | 0.4 | n |  | TRUE
21 | bus_LV_2701-125_0_6_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2701-125_0_6_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_2701-125_0_6_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_2701-125_0_6_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2701-125_0_6_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_2701-125_0_6_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_2701-125_0_6_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_2701-125_0_6_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_2701-125_0_6_node_24 | 0.4 | n |  | TRUE
30 | bus_MV_562_0_node_83 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-125_0_6_load_0 | 0 | 0.011471 | 0.002875 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-125_0_6_load_1 | 1 | 0.023777 | 0.0059592 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-125_0_6_load_3 | 3 | 0.029573 | 0.0074118 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-125_0_6_load_5 | 4 | 0.025019 | 0.0062704 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-125_0_6_load_31 | 5 | 0.01216 | 0.0030475 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-125_0_6_load_20 | 6 | 0.017854 | 0.0044747 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-125_0_6_load_22 | 9 | 0.03924 | 0.0098344 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-125_0_6_load_25 | 10 | 0.036201 | 0.0090727 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-125_0_6_load_30 | 12 | 0.019045 | 0.0047731 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-125_0_6_load_9 | 13 | 0.011646 | 0.0029187 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-125_0_6_load_8 | 14 | 0.033351 | 0.0083586 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-125_0_6_load_12 | 16 | 0.046167 | 0.011571 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-125_0_6_load_10 | 17 | 0.010341 | 0.0025918 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-125_0_6_load_23 | 19 | 0.013912 | 0.0034866 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-125_0_6_load_26 | 20 | 0.024054 | 0.0060285 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-125_0_6_load_13 | 21 | 0.03262 | 0.0081754 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-125_0_6_load_14 | 22 | 0.024173 | 0.0060583 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-125_0_6_load_17 | 23 | 0.017361 | 0.0043511 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-125_0_6_load_18 | 24 | 0.025772 | 0.006459 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-125_0_6_load_27 | 25 | 0.062278 | 0.015608 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-125_0_6_load_28 | 26 | 0.018186 | 0.0045578 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-125_0_6_load_29 | 27 | 0.026202 | 0.0065668 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-125_0_6_load_21 | 28 | 0.030892 | 0.0077423 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-125_0_6_load_24 | 29 | 0.015794 | 0.0039584 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-125_0_6_line_0 |  | 0 | 1 | 0.0061336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2701-125_0_6_line_1 |  | 0 | 2 | 0.013536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2701-125_0_6_line_2 |  | 1 | 3 | 0.00054137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_2701-125_0_6_line_3 |  | 2 | 4 | 0.013524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2701-125_0_6_line_4 |  | 3 | 5 | 0.0054771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-125_0_6_line_5 |  | 4 | 6 | 0.0027347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2701-125_0_6_line_6 |  | 5 | 11 | 0.011954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-125_0_6_line_7 |  | 6 | 18 | 0.0075566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2701-125_0_6_line_8 |  | 7 | 8 | 0.035293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-125_0_6_line_9 |  | 7 | 9 | 0.017526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-125_0_6_line_10 |  | 8 | 10 | 0.019529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-125_0_6_line_11 |  | 9 | 19 | 0.011071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-125_0_6_line_12 |  | 10 | 20 | 0.006493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-125_0_6_line_13 |  | 11 | 12 | 0.020954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-125_0_6_line_14 |  | 12 | 27 | 0.0071781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-125_0_6_line_15 |  | 13 | 14 | 0.0062546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-125_0_6_line_16 |  | 14 | 17 | 0.0096598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-125_0_6_line_17 |  | 15 | 16 | 0.021028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-125_0_6_line_18 |  | 15 | 17 | 0.019481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-125_0_6_line_19 |  | 16 | 21 | 0.025632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-125_0_6_line_20 |  | 18 | 28 | 0.020628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_2701-125_0_6_line_21 |  | 18 | 24 | 0.0090434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2701-125_0_6_line_22 |  | 19 | 29 | 0.0041918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-125_0_6_line_23 |  | 21 | 22 | 0.013182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-125_0_6_line_24 |  | 22 | 23 | 0.0021408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2701-125_0_6_line_25 |  | 23 | 24 | 0.0059981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2701-125_0_6_line_26 |  | 25 | 26 | 0.012713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-125_0_6_line_27 |  | 26 | 27 | 0.0075986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-125_0_6_line_28 |  | 28 | 29 | 0.010002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-125_0_6_trafo_2 | 0.63 MVA 20/0.4 kV | 30 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2611327.4173 | 1266982.6414 | 2611333.5107 | 1266981.941
1 | 2611313.9703 | 1266984.1871 | 2611327.4173 | 1266982.6414
2 | 2611334.0486 | 1266981.8792 | 2611333.5107 | 1266981.941
3 | 2611313.9703 | 1266984.1871 | 2611307.453 | 1266987.4547 | 2611301.4248 | 1266989.0413
4 | 2611334.0486 | 1266981.8792 | 2611339.4898 | 1266981.2538
5 | 2611301.4248 | 1266989.0413 | 2611298.7801 | 1266989.7373
6 | 2611351.366 | 1266979.8887 | 2611339.4898 | 1266981.2538
7 | 2611291.4723 | 1266991.6606 | 2611298.7801 | 1266989.7373
8 | 2611293.8894 | 1266915.979 | 2611296.5906 | 1266920.5318 | 2611269.4231 | 1266933.2557
9 | 2611269.4231 | 1266933.2557 | 2611276.2492 | 1266941.7746 | 2611279.0711 | 1266947.7514
10 | 2611293.8894 | 1266915.979 | 2611310.8597 | 1266906.3155
11 | 2611279.0711 | 1266947.7514 | 2611283.7979 | 1266957.7631
12 | 2611310.8597 | 1266906.3155 | 2611316.502 | 1266903.1025
13 | 2611351.366 | 1266979.8887 | 2611348.1125 | 1266959.1886
14 | 2611348.1125 | 1266959.1886 | 2611346.998 | 1266952.0976
15 | 2611298.4535 | 1267052.0957 | 2611302.4993 | 1267051.1676 | 2611304.5869 | 1267050.9075
16 | 2611298.4535 | 1267052.0957 | 2611289.0383 | 1267054.2555
17 | 2611270.0509 | 1267058.6112 | 2611267.1702 | 1267045.5855 | 2611264.8652 | 1267042.479 | 2611264.8274 | 1267038.6603
18 | 2611270.0509 | 1267058.6112 | 2611289.0383 | 1267054.2555
19 | 2611264.8274 | 1267038.6603 | 2611264.7768 | 1267033.5615 | 2611267.6063 | 1267025.9615 | 2611275.4226 | 1267016.3047
20 | 2611291.4723 | 1266991.6606 | 2611287.2701 | 1266971.4653
21 | 2611291.4723 | 1266991.6606 | 2611289.4458 | 1267000.474
22 | 2611283.7979 | 1266957.7631 | 2611284.9084 | 1266960.115 | 2611285.2324 | 1266961.6725
23 | 2611275.4226 | 1267016.3047 | 2611279.1801 | 1267011.6624 | 2611284.819 | 1267007.1699
24 | 2611286.036 | 1267005.4087 | 2611284.819 | 1267007.1699 | 2611284.819 | 1267007.1699
25 | 2611286.036 | 1267005.4087 | 2611289.4458 | 1267000.474 | 2611289.4458 | 1267000.474
26 | 2611343.2129 | 1266932.1427 | 2611344.1246 | 1266936.6891 | 2611345.6126 | 1266944.6265
27 | 2611345.6126 | 1266944.6265 | 2611346.9188 | 1266951.5938 | 2611346.998 | 1266952.0976
28 | 2611285.2324 | 1266961.6725 | 2611287.2701 | 1266971.4653

## bus_geodata
| x | y | coords
0 | 2611327.4173 | 1266982.6414
1 | 2611333.5107 | 1266981.941
2 | 2611313.9703 | 1266984.1871
3 | 2611334.0486 | 1266981.8792
4 | 2611301.4248 | 1266989.0413
5 | 2611339.4898 | 1266981.2538
6 | 2611298.7801 | 1266989.7373
7 | 2611269.4231 | 1266933.2557
8 | 2611293.8894 | 1266915.979
9 | 2611279.0711 | 1266947.7514
10 | 2611310.8597 | 1266906.3155
11 | 2611351.366 | 1266979.8887
12 | 2611348.1125 | 1266959.1886
13 | 2611304.5869 | 1267050.9075
14 | 2611298.4535 | 1267052.0957
15 | 2611270.0509 | 1267058.6112
16 | 2611264.8274 | 1267038.6603
17 | 2611289.0383 | 1267054.2555
18 | 2611291.4723 | 1266991.6606
19 | 2611283.7979 | 1266957.7631
20 | 2611316.502 | 1266903.1025
21 | 2611275.4226 | 1267016.3047
22 | 2611284.819 | 1267007.1699
23 | 2611286.036 | 1267005.4087
24 | 2611289.4458 | 1267000.474
25 | 2611343.2129 | 1266932.1427
26 | 2611345.6126 | 1266944.6265
27 | 2611346.998 | 1266952.0976
28 | 2611287.2701 | 1266971.4653
29 | 2611285.2324 | 1266961.6725
30 | 2611291.4723 | 1266991.6606

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99917 | -0.015953 | 0.011471 | 0.002875
1 | 0.99881 | -0.022781 | 0.023777 | 0.0059592
2 | 1 | 0 | -0.6121 | -0.1543
3 | 0.99877 | -0.023573 | 0.029573 | 0.0074118
4 | 0.99834 | -0.031828 | 0.025019 | 0.0062704
5 | 0.99808 | -0.036776 | 0.01216 | 0.0030475
6 | 0.99802 | -0.037878 | 0.017854 | 0.0044747
7 | 0.99208 | -0.15207 | 0 | 0
8 | 0.99013 | -0.18981 | 0 | 0
9 | 0.99305 | -0.13339 | 0.03924 | 0.0098344
10 | 0.98906 | -0.21075 | 0.036201 | 0.0090727
11 | 0.99671 | -0.063107 | 0 | 0
12 | 0.9943 | -0.10943 | 0.019045 | 0.0047731
13 | 0.98964 | -0.19948 | 0.011646 | 0.0029187
14 | 0.98971 | -0.19818 | 0.033351 | 0.0083586
15 | 0.99109 | -0.17131 | 0 | 0
16 | 0.99216 | -0.15068 | 0.046167 | 0.011571
17 | 0.99011 | -0.19045 | 0.010341 | 0.0025918
18 | 0.99719 | -0.053826 | 0 | 0
19 | 0.99406 | -0.11394 | 0.013912 | 0.0034866
20 | 0.98891 | -0.21353 | 0.024054 | 0.0060285
21 | 0.99454 | -0.10472 | 0.03262 | 0.0081754
22 | 0.99616 | -0.073616 | 0.024173 | 0.0060583
23 | 0.99631 | -0.070641 | 0.017361 | 0.0043511
24 | 0.99663 | -0.064476 | 0.025772 | 0.006459
25 | 0.99232 | -0.14775 | 0.062278 | 0.015608
26 | 0.99304 | -0.13374 | 0.018186 | 0.0045578
27 | 0.9936 | -0.12294 | 0.026202 | 0.0065668
28 | 0.99568 | -0.082813 | 0.030892 | 0.0077423
29 | 0.9945 | -0.10556 | 0.015794 | 0.0039584
30 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.19197 | 0.048401 | -0.19191 | -0.048361 | 6.2709e-05 | 3.9893e-05 | 0.28599 | 0.28599 | 0.28599 | 0.99917 | -0.015953 | 0.99881 | -0.022781 | 26.1897
1 | -0.20344 | -0.051276 | 0.20359 | 0.051375 | 0.00015541 | 9.8932e-05 | 0.30308 | 0.30308 | 0.30308 | 0.99917 | -0.015953 | 1 | 0 | 27.7542
2 | 0.16813 | 0.042402 | -0.16812 | -0.042398 | 6.3731e-06 | 4.0646e-06 | 0.25057 | 0.25057 | 0.25057 | 0.99881 | -0.022781 | 0.99877 | -0.023573 | 34.4187
3 | 0.40686 | 0.10292 | -0.40624 | -0.10252 | 0.00062029 | 0.00039646 | 0.60574 | 0.60574 | 0.60574 | 1 | 0 | 0.99834 | -0.031828 | 55.4711
4 | 0.13855 | 0.034986 | -0.13846 | -0.03493 | 8.7591e-05 | 5.5986e-05 | 0.20651 | 0.20651 | 0.20651 | 0.99877 | -0.023573 | 0.99808 | -0.036776 | 56.7331
5 | 0.38122 | 0.096254 | -0.38111 | -0.096183 | 0.00011046 | 7.0588e-05 | 0.56845 | 0.56845 | 0.56845 | 0.99834 | -0.031828 | 0.99802 | -0.037878 | 52.0562
6 | 0.1263 | 0.031883 | -0.12614 | -0.031781 | 0.00015908 | 0.00010166 | 0.18838 | 0.18838 | 0.18838 | 0.99808 | -0.036776 | 0.99671 | -0.063107 | 51.7527
7 | 0.36325 | 0.091709 | -0.36297 | -0.091532 | 0.00027731 | 0.00017718 | 0.54183 | 0.54183 | 0.54183 | 0.99802 | -0.037878 | 0.99719 | -0.053826 | 49.6185
8 | 0.060427 | 0.015211 | -0.060318 | -0.015141 | 0.00010877 | 6.916e-05 | 0.090657 | 0.090657 | 0.090657 | 0.99208 | -0.15207 | 0.99013 | -0.18981 | 24.9057
9 | -0.060427 | -0.015211 | 0.060481 | 0.015245 | 5.4014e-05 | 3.4343e-05 | 0.090657 | 0.090656 | 0.090657 | 0.99208 | -0.15207 | 0.99305 | -0.13339 | 24.9056
10 | 0.060318 | 0.015141 | -0.060258 | -0.015103 | 6.0188e-05 | 3.8269e-05 | 0.090657 | 0.090657 | 0.090657 | 0.99013 | -0.18981 | 0.98906 | -0.21075 | 24.9057
11 | -0.09972 | -0.025079 | 0.099813 | 0.025138 | 9.2737e-05 | 5.9208e-05 | 0.14945 | 0.14945 | 0.14945 | 0.99305 | -0.13339 | 0.99406 | -0.11394 | 41.0588
12 | 0.024057 | 0.0060304 | -0.024054 | -0.0060285 | 3.1896e-06 | 1.9581e-06 | 0.036194 | 0.036194 | 0.036194 | 0.98906 | -0.21075 | 0.98891 | -0.21353 | 9.9433
13 | 0.12614 | 0.031781 | -0.12586 | -0.031603 | 0.00027885 | 0.00017819 | 0.18838 | 0.18838 | 0.18838 | 0.99671 | -0.063107 | 0.9943 | -0.10943 | 51.7527
14 | 0.10682 | 0.02683 | -0.10675 | -0.026786 | 6.8804e-05 | 4.3942e-05 | 0.15988 | 0.15988 | 0.15988 | 0.9943 | -0.10943 | 0.9936 | -0.12294 | 43.9226
15 | -0.011646 | -0.0029187 | 0.011647 | 0.0029191 | 7.1917e-07 | 3.799e-07 | 0.017511 | 0.017511 | 0.017511 | 0.98964 | -0.19948 | 0.98971 | -0.19818 | 4.8106
16 | -0.044998 | -0.011278 | 0.045014 | 0.011288 | 1.658e-05 | 1.0487e-05 | 0.067654 | 0.067653 | 0.067654 | 0.98971 | -0.19818 | 0.99011 | -0.19045 | 18.5861
17 | -0.055406 | -0.013912 | 0.055461 | 0.013947 | 5.4578e-05 | 3.4658e-05 | 0.083195 | 0.083195 | 0.083195 | 0.99109 | -0.17131 | 0.99216 | -0.15068 | 22.8558
18 | 0.055406 | 0.013912 | -0.055355 | -0.01388 | 5.0563e-05 | 3.2109e-05 | 0.083195 | 0.083195 | 0.083195 | 0.99109 | -0.17131 | 0.99011 | -0.19045 | 22.8558
19 | -0.10163 | -0.025517 | 0.10185 | 0.02566 | 0.00022335 | 0.00014261 | 0.15243 | 0.15243 | 0.15243 | 0.99216 | -0.15068 | 0.99454 | -0.10472 | 41.8777
20 | 0.16082 | 0.040587 | -0.1606 | -0.040445 | 0.00022293 | 0.00014214 | 0.24008 | 0.24008 | 0.24008 | 0.99719 | -0.053826 | 0.99568 | -0.082813 | 32.9777
21 | 0.20215 | 0.050944 | -0.20205 | -0.050879 | 0.00010293 | 6.5523e-05 | 0.30176 | 0.30176 | 0.30176 | 0.99719 | -0.053826 | 0.99663 | -0.064476 | 27.6333
22 | -0.11372 | -0.028625 | 0.11377 | 0.028654 | 4.5577e-05 | 2.9115e-05 | 0.17028 | 0.17028 | 0.17028 | 0.99406 | -0.11394 | 0.9945 | -0.10556 | 46.7798
23 | -0.13447 | -0.033835 | 0.13467 | 0.033963 | 0.00020019 | 0.00012795 | 0.20124 | 0.20124 | 0.20124 | 0.99454 | -0.10472 | 0.99616 | -0.073616 | 55.2859
24 | -0.15884 | -0.040021 | 0.15887 | 0.040036 | 2.2613e-05 | 1.4417e-05 | 0.23735 | 0.23735 | 0.23735 | 0.99616 | -0.073616 | 0.99631 | -0.070641 | 32.6029
25 | -0.17623 | -0.044387 | 0.17628 | 0.04442 | 5.197e-05 | 3.3027e-05 | 0.26328 | 0.26328 | 0.26328 | 0.99631 | -0.070641 | 0.99663 | -0.064476 | 24.1097
26 | -0.062278 | -0.015608 | 0.06232 | 0.015635 | 4.1577e-05 | 2.6445e-05 | 0.093389 | 0.093389 | 0.093389 | 0.99232 | -0.14775 | 0.99304 | -0.13374 | 25.6562
27 | -0.080506 | -0.020193 | 0.080547 | 0.020219 | 4.1471e-05 | 2.6443e-05 | 0.12064 | 0.12064 | 0.12064 | 0.99304 | -0.13374 | 0.9936 | -0.12294 | 33.1425
28 | 0.12971 | 0.032703 | -0.12956 | -0.032613 | 0.00014104 | 9.0136e-05 | 0.19391 | 0.19391 | 0.19391 | 0.99568 | -0.082813 | 0.9945 | -0.10556 | 53.2721

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.6121 | 0.1543

## res_load
| p_mw | q_mvar
0 | 0.011471 | 0.002875
1 | 0.023777 | 0.0059592
2 | 0.029573 | 0.0074118
3 | 0.025019 | 0.0062704
4 | 0.01216 | 0.0030475
5 | 0.017854 | 0.0044747
6 | 0.03924 | 0.0098344
7 | 0.036201 | 0.0090727
8 | 0.019045 | 0.0047731
9 | 0.011646 | 0.0029187
10 | 0.033351 | 0.0083586
11 | 0.046167 | 0.011571
12 | 0.010341 | 0.0025918
13 | 0.013912 | 0.0034866
14 | 0.024054 | 0.0060285
15 | 0.03262 | 0.0081754
16 | 0.024173 | 0.0060583
17 | 0.017361 | 0.0043511
18 | 0.025772 | 0.006459
19 | 0.062278 | 0.015608
20 | 0.018186 | 0.0045578
21 | 0.026202 | 0.0065668
22 | 0.030892 | 0.0077423
23 | 0.015794 | 0.0039584

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1