## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-127_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-127_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-127_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2701-127_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2701-127_0_4_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_2701-127_0_4_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_2701-127_0_4_node_40 | 0.4 | n |  | TRUE
7 | bus_LV_2701-127_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2701-127_0_4_node_41 | 0.4 | n |  | TRUE
9 | bus_LV_2701-127_0_4_node_42 | 0.4 | n |  | TRUE
10 | bus_LV_2701-127_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_2701-127_0_4_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_2701-127_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_2701-127_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2701-127_0_4_node_38 | 0.4 | n |  | TRUE
15 | bus_LV_2701-127_0_4_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_2701-127_0_4_node_47 | 0.4 | n |  | TRUE
17 | bus_LV_2701-127_0_4_node_49 | 0.4 | n |  | TRUE
18 | bus_LV_2701-127_0_4_node_50 | 0.4 | n |  | TRUE
19 | bus_LV_2701-127_0_4_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_2701-127_0_4_node_26 | 0.4 | n |  | TRUE
21 | bus_LV_2701-127_0_4_node_43 | 0.4 | n |  | TRUE
22 | bus_LV_2701-127_0_4_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_2701-127_0_4_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_2701-127_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2701-127_0_4_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_2701-127_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_2701-127_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_2701-127_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_2701-127_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2701-127_0_4_node_48 | 0.4 | n |  | TRUE
31 | bus_LV_2701-127_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_2701-127_0_4_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_2701-127_0_4_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_2701-127_0_4_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_2701-127_0_4_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_2701-127_0_4_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_2701-127_0_4_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_2701-127_0_4_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_2701-127_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_2701-127_0_4_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_2701-127_0_4_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_2701-127_0_4_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_2701-127_0_4_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_2701-127_0_4_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_2701-127_0_4_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_2701-127_0_4_node_45 | 0.4 | n |  | TRUE
47 | bus_MV_556_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-127_0_4_load_0 | 0 | 0.0027857 | 0.00069817 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-127_0_4_load_13 | 4 | 0.04966 | 0.012446 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-127_0_4_load_12 | 5 | 0.020345 | 0.005099 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-127_0_4_load_40 | 6 | 0.012998 | 0.0032577 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-127_0_4_load_41 | 8 | 0.011876 | 0.0029764 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-127_0_4_load_42 | 9 | 0.0041642 | 0.0010436 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-127_0_4_load_17 | 11 | 0.0057274 | 0.0014354 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-127_0_4_load_14 | 12 | 0.0071049 | 0.0017807 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-127_0_4_load_38 | 14 | 0.010697 | 0.002681 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-127_0_4_load_39 | 15 | 0.0034884 | 0.00087428 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-127_0_4_load_47 | 16 | 0.00593 | 0.0014862 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-127_0_4_load_49 | 17 | 0.013394 | 0.0033568 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-127_0_4_load_50 | 18 | 0.0045425 | 0.0011385 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-127_0_4_load_46 | 19 | 0.0052305 | 0.0013109 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-127_0_4_load_26 | 20 | 0.005149 | 0.0012905 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-127_0_4_load_43 | 21 | 0.004618 | 0.0011574 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-127_0_4_load_44 | 22 | 0.0046102 | 0.0011554 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-127_0_4_load_51 | 23 | 0.0044217 | 0.0011082 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-127_0_4_load_15 | 24 | 0.005102 | 0.0012787 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-127_0_4_load_37 | 25 | 0.0057256 | 0.001435 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-127_0_4_load_21 | 26 | 0.014666 | 0.0036757 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-127_0_4_load_16 | 27 | 0.02967 | 0.0074359 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-127_0_4_load_18 | 28 | 0.01789 | 0.0044837 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-127_0_4_load_19 | 29 | 0.0032618 | 0.00081747 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-127_0_4_load_48 | 30 | 0.0046123 | 0.001156 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-127_0_4_load_20 | 31 | 0.0040137 | 0.0010059 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-127_0_4_load_36 | 32 | 0.0063894 | 0.0016013 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-127_0_4_load_35 | 33 | 0.0052035 | 0.0013041 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-127_0_4_load_22 | 34 | 0.035396 | 0.0088711 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-127_0_4_load_23 | 35 | 0.0051443 | 0.0012893 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-127_0_4_load_24 | 36 | 0.0051607 | 0.0012934 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-127_0_4_load_25 | 37 | 0.0051492 | 0.0012905 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-127_0_4_load_27 | 38 | 0.0042748 | 0.0010714 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-127_0_4_load_28 | 39 | 0.0099554 | 0.002495 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-127_0_4_load_34 | 40 | 0.0042697 | 0.0010701 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-127_0_4_load_29 | 41 | 0.02199 | 0.0055112 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-127_0_4_load_30 | 42 | 0.0042145 | 0.0010563 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-127_0_4_load_31 | 43 | 0.010792 | 0.0027048 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-127_0_4_load_32 | 44 | 0.0042149 | 0.0010564 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-127_0_4_load_33 | 45 | 0.0051937 | 0.0013017 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-127_0_4_load_45 | 46 | 0.0046133 | 0.0011562 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-127_0_4_line_0 |  | 0 | 1 | 0.018919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-127_0_4_line_1 |  | 1 | 2 | 0.046118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-127_0_4_line_2 |  | 1 | 3 | 0.090577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-127_0_4_line_3 |  | 2 | 4 | 0.015825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-127_0_4_line_4 |  | 2 | 5 | 0.027572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-127_0_4_line_5 |  | 3 | 6 | 0.043317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2701-127_0_4_line_6 |  | 6 | 7 | 0.017673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2701-127_0_4_line_7 |  | 7 | 8 | 0.0052089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2701-127_0_4_line_8 |  | 7 | 9 | 0.00842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-127_0_4_line_9 |  | 8 | 16 | 0.013509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2701-127_0_4_line_10 |  | 9 | 17 | 0.013527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-127_0_4_line_11 |  | 10 | 11 | 0.015825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-127_0_4_line_12 |  | 10 | 12 | 0.015216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-127_0_4_line_13 |  | 11 | 23 | 0.012398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-127_0_4_line_14 |  | 12 | 24 | 0.0076898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-127_0_4_line_15 |  | 13 | 14 | 0.015269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2701-127_0_4_line_16 |  | 13 | 15 | 0.029789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2701-127_0_4_line_17 |  | 14 | 25 | 0.011554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2701-127_0_4_line_18 |  | 15 | 26 | 0.017524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2701-127_0_4_line_19 |  | 16 | 45 | 0.0086398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2701-127_0_4_line_20 |  | 17 | 18 | 4.7611e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-127_0_4_line_21 |  | 19 | 20 | 0.0026741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-127_0_4_line_22 |  | 20 | 36 | 0.0062411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-127_0_4_line_23 |  | 21 | 22 | 0.008288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-127_0_4_line_24 |  | 22 | 46 | 0.0087144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-127_0_4_line_25 |  | 23 | 30 | 0.0086099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-127_0_4_line_26 |  | 24 | 27 | 0.031358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-127_0_4_line_27 |  | 25 | 44 | 0.0087265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2701-127_0_4_line_28 |  | 26 | 27 | 0.017722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2701-127_0_4_line_29 |  | 27 | 28 | 0.019147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_2701-127_0_4_line_30 |  | 28 | 29 | 0.014992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2701-127_0_4_line_31 |  | 29 | 31 | 0.0045405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2701-127_0_4_line_32 |  | 30 | 46 | 0.0082871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-127_0_4_line_33 |  | 31 | 32 | 0.0063675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_2701-127_0_4_line_34 |  | 32 | 33 | 0.0041997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2701-127_0_4_line_35 |  | 33 | 40 | 0.0090013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_2701-127_0_4_line_36 |  | 34 | 35 | 0.016559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-127_0_4_line_37 |  | 34 | 36 | 0.0041133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-127_0_4_line_38 |  | 35 | 37 | 0.0080018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2701-127_0_4_line_39 |  | 37 | 38 | 0.0077244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2701-127_0_4_line_40 |  | 38 | 39 | 0.0042083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2701-127_0_4_line_41 |  | 39 | 40 | 0.0028543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2701-127_0_4_line_42 |  | 41 | 42 | 0.022191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2701-127_0_4_line_43 |  | 41 | 43 | 0.00067143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2701-127_0_4_line_44 |  | 42 | 44 | 0.0087056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2701-127_0_4_line_45 |  | 43 | 45 | 0.01304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-127_0_4_trafo_23 | 0.63 MVA 20/0.4 kV | 47 | 35 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2610749.283 | 1268476.2406 | 2610751.2608 | 1268476.9891 | 2610752.3811 | 1268477.4915 | 2610753.7046 | 1268478.0276 | 2610764.9845 | 1268482.4734 | 2610766.6989 | 1268483.5503
1 | 2610729.4842 | 1268517.7673 | 2610740.733 | 1268497.7291 | 2610745.5983 | 1268487.2194 | 2610749.283 | 1268476.2406
2 | 2610728.2808 | 1268409.0887 | 2610736.6251 | 1268413.9961 | 2610757.0572 | 1268426.0304 | 2610754.4149 | 1268430.6956 | 2610756.1861 | 1268433.3006 | 2610757.9042 | 1268436.1724 | 2610758.276 | 1268438.6748 | 2610760.3364 | 1268439.5236 | 2610762.5621 | 1268440.5284 | 2610755.6008 | 1268457.3165 | 2610749.283 | 1268476.2406
3 | 2610729.4842 | 1268517.7673 | 2610721.2805 | 1268531.2998
4 | 2610729.4842 | 1268517.7673 | 2610730.7094 | 1268518.5479 | 2610753.8574 | 1268530.6467
5 | 2610728.2808 | 1268409.0887 | 2610704.5703 | 1268445.3407
6 | 2610694.8967 | 1268460.1311 | 2610704.5703 | 1268445.3407
7 | 2610694.8967 | 1268460.1311 | 2610690.4287 | 1268457.4534
8 | 2610694.8967 | 1268460.1311 | 2610702.0852 | 1268464.5154
9 | 2610690.4287 | 1268457.4534 | 2610678.8417 | 1268450.509
10 | 2610702.0852 | 1268464.5154 | 2610713.6342 | 1268471.5591
11 | 2610534.4494 | 1268502.719 | 2610547.8518 | 1268511.1331
12 | 2610534.4494 | 1268502.719 | 2610543.2689 | 1268490.3192
13 | 2610558.3517 | 1268517.725 | 2610547.8518 | 1268511.1331
14 | 2610543.2689 | 1268490.3192 | 2610547.7258 | 1268484.0528
15 | 2610602.6749 | 1268404.8604 | 2610615.7722 | 1268412.71
16 | 2610602.6749 | 1268404.8604 | 2610585.8308 | 1268429.4294
17 | 2610625.6831 | 1268418.6497 | 2610615.7722 | 1268412.71
18 | 2610585.8308 | 1268429.4294 | 2610575.9216 | 1268443.8829
19 | 2610671.4309 | 1268446.0675 | 2610678.8417 | 1268450.509
20 | 2610713.6748 | 1268471.5839 | 2610713.6342 | 1268471.5591
21 | 2610643.7944 | 1268523.0837 | 2610645.2154 | 1268520.8184
22 | 2610645.2154 | 1268520.8184 | 2610648.5318 | 1268515.5313 | 2610648.5318 | 1268515.5313
23 | 2610587.0621 | 1268535.7496 | 2610580.0428 | 1268531.3428
24 | 2610580.0428 | 1268531.3428 | 2610572.6623 | 1268526.7092
25 | 2610565.6437 | 1268522.303 | 2610558.3517 | 1268517.725
26 | 2610565.9008 | 1268458.4993 | 2610547.7258 | 1268484.0528
27 | 2610633.1682 | 1268423.1358 | 2610625.6831 | 1268418.6497
28 | 2610565.9008 | 1268458.4993 | 2610575.9216 | 1268443.8829
29 | 2610565.9008 | 1268458.4993 | 2610581.9823 | 1268468.8919
30 | 2610594.5738 | 1268477.0291 | 2610589.7962 | 1268473.9416 | 2610581.9823 | 1268468.8919
31 | 2610598.3872 | 1268479.4936 | 2610594.5738 | 1268477.0291
32 | 2610572.6623 | 1268526.7092 | 2610565.6437 | 1268522.303
33 | 2610598.3872 | 1268479.4936 | 2610603.7352 | 1268482.9497
34 | 2610607.2624 | 1268485.2292 | 2610603.7352 | 1268482.9497
35 | 2610607.2624 | 1268485.2292 | 2610614.8224 | 1268490.1149
36 | 2610633.9622 | 1268502.4841 | 2610647.8693 | 1268511.4717
37 | 2610648.5318 | 1268515.5313 | 2610647.8693 | 1268511.4717 | 2610647.8693 | 1268511.4717
38 | 2610633.9622 | 1268502.4841 | 2610627.2417 | 1268498.1409
39 | 2610627.2417 | 1268498.1409 | 2610620.7541 | 1268493.9483
40 | 2610617.2197 | 1268491.6642 | 2610620.7541 | 1268493.9483
41 | 2610617.2197 | 1268491.6642 | 2610614.8224 | 1268490.1149
42 | 2610640.6355 | 1268427.6111 | 2610659.6696 | 1268439.0187
43 | 2610659.6696 | 1268439.0187 | 2610660.2455 | 1268439.3639
44 | 2610640.6355 | 1268427.6111 | 2610633.1682 | 1268423.1358
45 | 2610671.4309 | 1268446.0675 | 2610660.2455 | 1268439.3639

## bus_geodata
| x | y | coords
0 | 2610766.6989 | 1268483.5503
1 | 2610749.283 | 1268476.2406
2 | 2610729.4842 | 1268517.7673
3 | 2610728.2808 | 1268409.0887
4 | 2610721.2805 | 1268531.2998
5 | 2610753.8574 | 1268530.6467
6 | 2610704.5703 | 1268445.3407
7 | 2610694.8967 | 1268460.1311
8 | 2610690.4287 | 1268457.4534
9 | 2610702.0852 | 1268464.5154
10 | 2610534.4494 | 1268502.719
11 | 2610547.8518 | 1268511.1331
12 | 2610543.2689 | 1268490.3192
13 | 2610602.6749 | 1268404.8604
14 | 2610615.7722 | 1268412.71
15 | 2610585.8308 | 1268429.4294
16 | 2610678.8417 | 1268450.509
17 | 2610713.6342 | 1268471.5591
18 | 2610713.6748 | 1268471.5839
19 | 2610643.7944 | 1268523.0837
20 | 2610645.2154 | 1268520.8184
21 | 2610587.0621 | 1268535.7496
22 | 2610580.0428 | 1268531.3428
23 | 2610558.3517 | 1268517.725
24 | 2610547.7258 | 1268484.0528
25 | 2610625.6831 | 1268418.6497
26 | 2610575.9216 | 1268443.8829
27 | 2610565.9008 | 1268458.4993
28 | 2610581.9823 | 1268468.8919
29 | 2610594.5738 | 1268477.0291
30 | 2610565.6437 | 1268522.303
31 | 2610598.3872 | 1268479.4936
32 | 2610603.7352 | 1268482.9497
33 | 2610607.2624 | 1268485.2292
34 | 2610647.8693 | 1268511.4717
35 | 2610633.9622 | 1268502.4841
36 | 2610648.5318 | 1268515.5313
37 | 2610627.2417 | 1268498.1409
38 | 2610620.7541 | 1268493.9483
39 | 2610617.2197 | 1268491.6642
40 | 2610614.8224 | 1268490.1149
41 | 2610659.6696 | 1268439.0187
42 | 2610640.6355 | 1268427.6111
43 | 2610660.2455 | 1268439.3639
44 | 2610633.1682 | 1268423.1358
45 | 2610671.4309 | 1268446.0675
46 | 2610572.6623 | 1268526.7092
47 | 2610622.0654 | 1268557.7247

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97523 | -0.47728 | 0.0027857 | 0.00069817
1 | 0.97528 | -0.47631 | 0 | 0
2 | 0.97226 | -0.53566 | 0 | 0
3 | 0.98143 | -0.35625 | 0 | 0
4 | 0.97153 | -0.55016 | 0.04966 | 0.012446
5 | 0.97174 | -0.54601 | 0.020345 | 0.005099
6 | 0.9829 | -0.32776 | 0.012998 | 0.0032577
7 | 0.98338 | -0.31865 | 0 | 0
8 | 0.98355 | -0.31527 | 0.011876 | 0.0029764
9 | 0.9832 | -0.322 | 0.0041642 | 0.0010436
10 | 0.99059 | -0.17983 | 0 | 0
11 | 0.99017 | -0.18788 | 0.0057274 | 0.0014354
12 | 0.99099 | -0.1721 | 0.0071049 | 0.0017807
13 | 0.98851 | -0.21944 | 0 | 0
14 | 0.98762 | -0.23658 | 0.010697 | 0.002681
15 | 0.99024 | -0.18611 | 0.0034884 | 0.00087428
16 | 0.98405 | -0.30556 | 0.00593 | 0.0014862
17 | 0.98298 | -0.32638 | 0.013394 | 0.0033568
18 | 0.98298 | -0.32638 | 0.0045425 | 0.0011385
19 | 0.99911 | -0.017203 | 0.0052305 | 0.0013109
20 | 0.99912 | -0.016959 | 0.005149 | 0.0012905
21 | 0.98955 | -0.1999 | 0.004618 | 0.0011574
22 | 0.98959 | -0.19922 | 0.0046102 | 0.0011554
23 | 0.98991 | -0.19292 | 0.0044217 | 0.0011082
24 | 0.99124 | -0.16723 | 0.005102 | 0.0012787
25 | 0.98698 | -0.24882 | 0.0057256 | 0.001435
26 | 0.99128 | -0.16619 | 0.014666 | 0.0036757
27 | 0.99241 | -0.14456 | 0.02967 | 0.0074359
28 | 0.99404 | -0.1133 | 0.01789 | 0.0044837
29 | 0.9954 | -0.087324 | 0.0032618 | 0.00081747
30 | 0.98977 | -0.19575 | 0.0046123 | 0.001156
31 | 0.99582 | -0.079384 | 0.0040137 | 0.0010059
32 | 0.99641 | -0.068112 | 0.0063894 | 0.0016013
33 | 0.99681 | -0.060527 | 0.0052035 | 0.0013041
34 | 0.99923 | -0.014712 | 0.035396 | 0.0088711
35 | 1 | 0 | -0.39471 | -0.10027
36 | 0.99918 | -0.015828 | 0.0051607 | 0.0012934
37 | 0.99917 | -0.015708 | 0.0051492 | 0.0012905
38 | 0.99838 | -0.030664 | 0.0042748 | 0.0010714
39 | 0.99796 | -0.038717 | 0.0099554 | 0.002495
40 | 0.99768 | -0.044018 | 0.0042697 | 0.0010701
41 | 0.98494 | -0.28825 | 0.02199 | 0.0055112
42 | 0.98607 | -0.26652 | 0.0042145 | 0.0010563
43 | 0.98492 | -0.28882 | 0.010792 | 0.0027048
44 | 0.98652 | -0.25779 | 0.0042149 | 0.0010564
45 | 0.98439 | -0.29904 | 0.0051937 | 0.0013017
46 | 0.98966 | -0.19779 | 0.0046133 | 0.0011562
47 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0027857 | -0.00069817 | 0.0027859 | 0.00069802 | 1.2818e-07 | -1.5404e-07 | 0.0042505 | 0.0042504 | 0.0042505 | 0.97523 | -0.47728 | 0.97528 | -0.47631 | 1.1677
1 | 0.070248 | 0.017699 | -0.070049 | -0.017573 | 0.0001988 | 0.00012666 | 0.10721 | 0.10721 | 0.10721 | 0.97528 | -0.47631 | 0.97226 | -0.53566 | 29.4545
2 | -0.073034 | -0.018397 | 0.073456 | 0.018666 | 0.00042201 | 0.00026895 | 0.11146 | 0.11146 | 0.11146 | 0.97528 | -0.47631 | 0.98143 | -0.35625 | 30.6221
3 | 0.049694 | 0.012468 | -0.04966 | -0.012446 | 3.4331e-05 | 2.1776e-05 | 0.07606 | 0.07606 | 0.07606 | 0.97226 | -0.53566 | 0.97153 | -0.55016 | 20.8956
4 | 0.020355 | 0.0051051 | -0.020345 | -0.005099 | 1.0035e-05 | 6.081e-06 | 0.031154 | 0.031155 | 0.031155 | 0.97226 | -0.53566 | 0.97174 | -0.54601 | 8.5589
5 | -0.073456 | -0.018666 | 0.073557 | 0.01873 | 0.00010091 | 6.3486e-05 | 0.11146 | 0.11146 | 0.11146 | 0.98143 | -0.35625 | 0.9829 | -0.32776 | 15.311
6 | -0.086555 | -0.021988 | 0.086593 | 0.022011 | 3.7993e-05 | 2.3643e-05 | 0.13114 | 0.13114 | 0.13114 | 0.9829 | -0.32776 | 0.98338 | -0.31865 | 12.0093
7 | -0.1087 | -0.027554 | 0.10872 | 0.027566 | 1.7639e-05 | 1.1091e-05 | 0.16459 | 0.16459 | 0.16459 | 0.98338 | -0.31865 | 0.98355 | -0.31527 | 15.0728
8 | 0.022108 | 0.0055433 | -0.022104 | -0.0055411 | 3.5337e-06 | 2.1548e-06 | 0.033454 | 0.033454 | 0.033454 | 0.98338 | -0.31865 | 0.9832 | -0.322 | 9.1906
9 | -0.12059 | -0.030542 | 0.12065 | 0.030577 | 5.6278e-05 | 3.5504e-05 | 0.18256 | 0.18256 | 0.18256 | 0.98355 | -0.31527 | 0.98405 | -0.30556 | 16.7181
10 | 0.01794 | 0.0044975 | -0.017936 | -0.0044952 | 3.7397e-06 | 2.2219e-06 | 0.027151 | 0.027151 | 0.027151 | 0.9832 | -0.322 | 0.98298 | -0.32638 | 7.4592
11 | 0.028624 | 0.0071812 | -0.028613 | -0.0071744 | 1.0973e-05 | 6.8188e-06 | 0.043 | 0.043 | 0.043 | 0.99059 | -0.17983 | 0.99017 | -0.18788 | 11.8133
12 | -0.028624 | -0.0071812 | 0.028634 | 0.0071878 | 1.0551e-05 | 6.5565e-06 | 0.043 | 0.043 | 0.043 | 0.99059 | -0.17983 | 0.99099 | -0.1721 | 11.8132
13 | 0.022886 | 0.005739 | -0.02288 | -0.0057356 | 5.4994e-06 | 3.3602e-06 | 0.034393 | 0.034393 | 0.034393 | 0.99017 | -0.18788 | 0.98991 | -0.19292 | 9.4487
14 | -0.035739 | -0.0089685 | 0.035748 | 0.0089737 | 8.3058e-06 | 5.2166e-06 | 0.053668 | 0.053668 | 0.053668 | 0.99099 | -0.1721 | 0.99124 | -0.16723 | 14.7441
15 | 0.1901 | 0.048247 | -0.18994 | -0.048147 | 0.00015653 | 9.9591e-05 | 0.28637 | 0.28637 | 0.28637 | 0.98851 | -0.21944 | 0.98762 | -0.23658 | 26.2245
16 | -0.1901 | -0.048247 | 0.1904 | 0.048441 | 0.00030536 | 0.00019429 | 0.28637 | 0.28637 | 0.28637 | 0.98851 | -0.21944 | 0.99024 | -0.18611 | 26.2245
17 | 0.17924 | 0.045466 | -0.17914 | -0.045399 | 0.00010549 | 6.7069e-05 | 0.27025 | 0.27025 | 0.27025 | 0.98762 | -0.23658 | 0.98698 | -0.24882 | 24.7486
18 | -0.19389 | -0.049315 | 0.19408 | 0.049434 | 0.00018628 | 0.00011854 | 0.29161 | 0.29161 | 0.29161 | 0.99024 | -0.18611 | 0.99128 | -0.16619 | 26.7045
19 | -0.12658 | -0.032064 | 0.12662 | 0.032089 | 3.9617e-05 | 2.5025e-05 | 0.19153 | 0.19153 | 0.19153 | 0.98405 | -0.30556 | 0.98439 | -0.29904 | 17.5392
20 | 0.0045425 | 0.0011385 | -0.0045425 | -0.0011385 | 8.4435e-10 | -6.4065e-11 | 0.0068764 | 0.0068764 | 0.0068764 | 0.98298 | -0.32638 | 0.98298 | -0.32638 | 1.8891
21 | -0.0052305 | -0.0013109 | 0.0052305 | 0.0013109 | 6.0853e-08 | 3.9259e-09 | 0.00779 | 0.00779 | 0.00779 | 0.99911 | -0.017203 | 0.99912 | -0.016959 | 2.1401
22 | -0.01038 | -0.0026013 | 0.01038 | 0.0026016 | 5.5928e-07 | 2.762e-07 | 0.015459 | 0.015458 | 0.015459 | 0.99912 | -0.016959 | 0.99918 | -0.015828 | 4.2468
23 | -0.004618 | -0.0011574 | 0.0046181 | 0.0011574 | 1.4987e-07 | -1.0559e-08 | 0.0069442 | 0.0069441 | 0.0069442 | 0.98955 | -0.1999 | 0.98959 | -0.19922 | 1.9077
24 | -0.0092283 | -0.0023128 | 0.0092289 | 0.0023131 | 6.2924e-07 | 2.9075e-07 | 0.013876 | 0.013876 | 0.013876 | 0.98959 | -0.19922 | 0.98966 | -0.19779 | 3.8122
25 | 0.018458 | 0.0046275 | -0.018456 | -0.004626 | 2.4857e-06 | 1.4802e-06 | 0.027747 | 0.027747 | 0.027747 | 0.98991 | -0.19292 | 0.98977 | -0.19575 | 7.6227
26 | -0.04085 | -0.010252 | 0.040894 | 0.01028 | 4.4227e-05 | 2.79e-05 | 0.061327 | 0.061327 | 0.061327 | 0.99124 | -0.16723 | 0.99241 | -0.14456 | 16.8482
27 | 0.17341 | 0.043964 | -0.17334 | -0.043917 | 7.4663e-05 | 4.745e-05 | 0.26162 | 0.26162 | 0.26162 | 0.98698 | -0.24882 | 0.98652 | -0.25779 | 23.9581
28 | -0.20874 | -0.053109 | 0.20896 | 0.053248 | 0.00021789 | 0.00013877 | 0.31363 | 0.31363 | 0.31363 | 0.99128 | -0.16619 | 0.99241 | -0.14456 | 28.7205
29 | -0.27952 | -0.070964 | 0.27995 | 0.071233 | 0.00042108 | 0.00026874 | 0.41944 | 0.41944 | 0.41944 | 0.99241 | -0.14456 | 0.99404 | -0.1133 | 38.4103
30 | -0.29784 | -0.075717 | 0.29821 | 0.075955 | 0.00037314 | 0.00023822 | 0.44622 | 0.44622 | 0.44622 | 0.99404 | -0.1133 | 0.9954 | -0.087324 | 40.8627
31 | -0.30147 | -0.076772 | 0.30159 | 0.076846 | 0.00011549 | 7.3738e-05 | 0.4511 | 0.4511 | 0.4511 | 0.9954 | -0.087324 | 0.99582 | -0.079384 | 41.3092
32 | 0.013844 | 0.00347 | -0.013842 | -0.0034693 | 1.3461e-06 | 7.5502e-07 | 0.020813 | 0.020813 | 0.020813 | 0.98977 | -0.19575 | 0.98966 | -0.19779 | 5.7178
33 | -0.3056 | -0.077852 | 0.30577 | 0.077958 | 0.0001663 | 0.00010618 | 0.45709 | 0.45709 | 0.45709 | 0.99582 | -0.079384 | 0.99641 | -0.068112 | 41.8584
34 | -0.31216 | -0.07956 | 0.31227 | 0.079633 | 0.00011431 | 7.2994e-05 | 0.46664 | 0.46664 | 0.46664 | 0.99641 | -0.068112 | 0.99681 | -0.060527 | 42.7322
35 | -0.31747 | -0.080937 | 0.31773 | 0.081098 | 0.00025323 | 0.00016171 | 0.4744 | 0.4744 | 0.4744 | 0.99681 | -0.060527 | 0.99768 | -0.044018 | 43.4435
36 | -0.050938 | -0.012767 | 0.050973 | 0.012789 | 3.5728e-05 | 2.2649e-05 | 0.075854 | 0.075854 | 0.075854 | 0.99923 | -0.014712 | 1 | 0 | 20.8391
37 | 0.015542 | 0.0038955 | -0.015541 | -0.003895 | 8.2622e-07 | 4.749e-07 | 0.023144 | 0.023144 | 0.023144 | 0.99923 | -0.014712 | 0.99918 | -0.015828 | 6.3582
38 | 0.34209 | 0.087482 | -0.34183 | -0.087316 | 0.00025981 | 0.00016596 | 0.50965 | 0.50965 | 0.50965 | 1 | 0 | 0.99917 | -0.015708 | 46.6716
39 | 0.33668 | 0.086026 | -0.33644 | -0.08587 | 0.00024331 | 0.00015541 | 0.50199 | 0.50199 | 0.50199 | 0.99917 | -0.015708 | 0.99838 | -0.030664 | 45.9694
40 | 0.33216 | 0.084799 | -0.33203 | -0.084716 | 0.00012921 | 8.2531e-05 | 0.49561 | 0.49561 | 0.49561 | 0.99838 | -0.030664 | 0.99796 | -0.038717 | 45.386
41 | 0.32208 | 0.082221 | -0.322 | -0.082169 | 8.2468e-05 | 5.2668e-05 | 0.48077 | 0.48077 | 0.48077 | 0.99796 | -0.038717 | 0.99768 | -0.044018 | 44.0266
42 | -0.16466 | -0.04165 | 0.16484 | 0.041759 | 0.00017185 | 0.00010914 | 0.24891 | 0.24891 | 0.24891 | 0.98494 | -0.28825 | 0.98607 | -0.26652 | 22.7935
43 | 0.14267 | 0.036139 | -0.14267 | -0.036136 | 3.9043e-06 | 2.4731e-06 | 0.21568 | 0.21568 | 0.21568 | 0.98494 | -0.28825 | 0.98492 | -0.28882 | 19.7513
44 | -0.16905 | -0.042815 | 0.16912 | 0.04286 | 7.0907e-05 | 4.5047e-05 | 0.25527 | 0.25526 | 0.25527 | 0.98607 | -0.26652 | 0.98652 | -0.25779 | 23.3759
45 | 0.13188 | 0.033431 | -0.13181 | -0.03339 | 6.4798e-05 | 4.0973e-05 | 0.19938 | 0.19938 | 0.19938 | 0.98492 | -0.28882 | 0.98439 | -0.29904 | 18.2582

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39986 | 0.10156

## res_load
| p_mw | q_mvar
0 | 0.0027857 | 0.00069817
1 | 0.04966 | 0.012446
2 | 0.020345 | 0.005099
3 | 0.012998 | 0.0032577
4 | 0.011876 | 0.0029764
5 | 0.0041642 | 0.0010436
6 | 0.0057274 | 0.0014354
7 | 0.0071049 | 0.0017807
8 | 0.010697 | 0.002681
9 | 0.0034884 | 0.00087428
10 | 0.00593 | 0.0014862
11 | 0.013394 | 0.0033568
12 | 0.0045425 | 0.0011385
13 | 0.0052305 | 0.0013109
14 | 0.005149 | 0.0012905
15 | 0.004618 | 0.0011574
16 | 0.0046102 | 0.0011554
17 | 0.0044217 | 0.0011082
18 | 0.005102 | 0.0012787
19 | 0.0057256 | 0.001435
20 | 0.014666 | 0.0036757
21 | 0.02967 | 0.0074359
22 | 0.01789 | 0.0044837
23 | 0.0032618 | 0.00081747
24 | 0.0046123 | 0.001156
25 | 0.0040137 | 0.0010059
26 | 0.0063894 | 0.0016013
27 | 0.0052035 | 0.0013041
28 | 0.035396 | 0.0088711
29 | 0.0051443 | 0.0012893
30 | 0.0051607 | 0.0012934
31 | 0.0051492 | 0.0012905
32 | 0.0042748 | 0.0010714
33 | 0.0099554 | 0.002495
34 | 0.0042697 | 0.0010701
35 | 0.02199 | 0.0055112
36 | 0.0042145 | 0.0010563
37 | 0.010792 | 0.0027048
38 | 0.0042149 | 0.0010564
39 | 0.0051937 | 0.0013017
40 | 0.0046133 | 0.0011562

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1