## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-12_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-12_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-12_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-12_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-12_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-12_0_5_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_2701-12_0_5_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_2701-12_0_5_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_2701-12_0_5_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_2701-12_0_5_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_2701-12_0_5_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2701-12_0_5_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_2701-12_0_5_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_2701-12_0_5_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2701-12_0_5_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_2701-12_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2701-12_0_5_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_2701-12_0_5_node_27 | 0.4 | n |  | TRUE
18 | bus_LV_2701-12_0_5_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_2701-12_0_5_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_2701-12_0_5_node_19 | 0.4 | n |  | TRUE
21 | bus_MV_558_0_node_131 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-12_0_5_load_0 | 0 | 0.054499 | 0.013659 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-12_0_5_load_16 | 5 | 0.069337 | 0.017377 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-12_0_5_load_17 | 6 | 0.010832 | 0.0027147 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-12_0_5_load_25 | 7 | 0.038534 | 0.0096575 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-12_0_5_load_20 | 9 | 0.064601 | 0.01619 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-12_0_5_load_26 | 12 | 0.0093856 | 0.0023522 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-12_0_5_load_22 | 14 | 0.0077832 | 0.0019506 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-12_0_5_load_18 | 16 | 0.016405 | 0.0041115 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-12_0_5_load_27 | 17 | 0.090784 | 0.022753 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-12_0_5_load_24 | 18 | 0.0061343 | 0.0015374 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-12_0_5_load_21 | 19 | 0.047287 | 0.011851 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-12_0_5_load_19 | 20 | 0.067091 | 0.016815 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-12_0_5_line_0 |  | 0 | 1 | 0.012164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-12_0_5_line_1 |  | 0 | 2 | 0.014749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-12_0_5_line_2 |  | 1 | 3 | 0.012775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-12_0_5_line_3 |  | 1 | 4 | 0.015445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2701-12_0_5_line_4 |  | 2 | 5 | 0.010689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-12_0_5_line_5 |  | 2 | 6 | 0.040342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-12_0_5_line_6 |  | 3 | 7 | 0.010508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-12_0_5_line_7 |  | 4 | 8 | 0.026798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2701-12_0_5_line_8 |  | 4 | 9 | 0.027354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-12_0_5_line_9 |  | 8 | 18 | 0.0087019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-12_0_5_line_10 |  | 8 | 15 | 0.063812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2701-12_0_5_line_11 |  | 9 | 19 | 0.017491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-12_0_5_line_12 |  | 10 | 11 | 0.030032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-12_0_5_line_13 |  | 10 | 12 | 0.036038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-12_0_5_line_14 |  | 10 | 13 | 0.074379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-12_0_5_line_15 |  | 11 | 17 | 0.015934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-12_0_5_line_16 |  | 11 | 15 | 0.044071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-12_0_5_line_17 |  | 13 | 14 | 0.12418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-12_0_5_line_18 |  | 15 | 16 | 0.065113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-12_0_5_line_19 |  | 16 | 20 | 0.064582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-12_0_5_trafo_4 | 0.63 MVA 20/0.4 kV | 21 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2611703.4025 | 1266733.0547 | 2611693.8646 | 1266740.6044
1 | 2611682.3002 | 1266749.7582 | 2611693.8646 | 1266740.6044
2 | 2611703.4025 | 1266733.0547 | 2611706.6391 | 1266737.0305 | 2611709.6352 | 1266736.9363 | 2611712.9559 | 1266740.223
3 | 2611705.9338 | 1266720.5621 | 2611701.5829 | 1266724.3673 | 2611700.7369 | 1266729.6804 | 2611703.4025 | 1266733.0547
4 | 2611682.3002 | 1266749.7582 | 2611673.3222 | 1266755.5583
5 | 2611682.3002 | 1266749.7582 | 2611687.1447 | 1266755.2159 | 2611708.9236 | 1266780.0673
6 | 2611712.9559 | 1266740.223 | 2611720.2303 | 1266747.8064
7 | 2611705.9338 | 1266720.5621 | 2611715.305 | 1266713.2087 | 2611726.3961 | 1266723.1375
8 | 2611705.9338 | 1266720.5621 | 2611687.0384 | 1266700.7827
9 | 2611726.3961 | 1266723.1375 | 2611732.4976 | 1266729.3419
10 | 2611726.3961 | 1266723.1375 | 2611728.8946 | 1266719.64 | 2611738.8574 | 1266721.4832 | 2611739.7911 | 1266721.3183 | 2611740.9967 | 1266720.7202 | 2611743.5435 | 1266719.4577 | 2611745.1033 | 1266718.6714 | 2611754.3259 | 1266725.5833 | 2611758.3629 | 1266728.2376 | 2611762.2817 | 1266729.7909 | 2611765.7129 | 1266730.4648 | 2611769.3185 | 1266730.4831 | 2611772.0812 | 1266730.433 | 2611773.2048 | 1266725.6096 | 2611774.8144 | 1266718.6857
11 | 2611674.9562 | 1266688.1352 | 2611687.0384 | 1266700.7827
12 | 2611821.3805 | 1266665.3632 | 2611805.3413 | 1266690.7824
13 | 2611789.5274 | 1266648.3436 | 2611803.8982 | 1266655.6216 | 2611821.3805 | 1266665.3632
14 | 2611821.3805 | 1266665.3632 | 2611851.8973 | 1266616.3453 | 2611860.6877 | 1266602.2197
15 | 2611793.0163 | 1266680.6397 | 2611805.3413 | 1266690.7824
16 | 2611774.8144 | 1266718.6857 | 2611784.1806 | 1266717.6814 | 2611787.6043 | 1266714.5749 | 2611794.6021 | 1266708.4178 | 2611796.674 | 1266703.7298 | 2611803.816 | 1266693.1921 | 2611805.3413 | 1266690.7824
17 | 2611860.6877 | 1266602.2197 | 2611788.7829 | 1266534.1736 | 2611770.6154 | 1266516.729
18 | 2611774.8144 | 1266718.6857 | 2611763.5876 | 1266716.5175 | 2611754.5035 | 1266711.9186 | 2611746.3714 | 1266705.4647 | 2611722.9553 | 1266682.0486
19 | 2611722.9553 | 1266682.0486 | 2611716.6586 | 1266675.7519 | 2611693.2297 | 1266654.402 | 2611676.2678 | 1266637.451

## bus_geodata
| x | y | coords
0 | 2611693.8646 | 1266740.6044
1 | 2611703.4025 | 1266733.0547
2 | 2611682.3002 | 1266749.7582
3 | 2611712.9559 | 1266740.223
4 | 2611705.9338 | 1266720.5621
5 | 2611673.3222 | 1266755.5583
6 | 2611708.9236 | 1266780.0673
7 | 2611720.2303 | 1266747.8064
8 | 2611726.3961 | 1266723.1375
9 | 2611687.0384 | 1266700.7827
10 | 2611821.3805 | 1266665.3632
11 | 2611805.3413 | 1266690.7824
12 | 2611789.5274 | 1266648.3436
13 | 2611860.6877 | 1266602.2197
14 | 2611770.6154 | 1266516.729
15 | 2611774.8144 | 1266718.6857
16 | 2611722.9553 | 1266682.0486
17 | 2611793.0163 | 1266680.6397
18 | 2611732.4976 | 1266729.3419
19 | 2611674.9562 | 1266688.1352
20 | 2611676.2678 | 1266637.451
21 | 2611711.4777 | 1266726.3548

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99729 | -0.052006 | 0.054499 | 0.013659
1 | 0.99878 | -0.023342 | 0 | 0
2 | 0.99622 | -0.072749 | 0 | 0
3 | 0.99834 | -0.031946 | 0 | 0
4 | 1 | 0 | -0.48783 | -0.12321
5 | 0.99554 | -0.085774 | 0.069337 | 0.017377
6 | 0.99582 | -0.080427 | 0.010832 | 0.0027147
7 | 0.99797 | -0.03903 | 0.038534 | 0.0096575
8 | 0.99756 | -0.04626 | 0 | 0
9 | 0.99722 | -0.053494 | 0.064601 | 0.01619
10 | 0.98709 | -0.24774 | 0 | 0
11 | 0.98756 | -0.23852 | 0 | 0
12 | 0.98677 | -0.2538 | 0.0093856 | 0.0023522
13 | 0.98655 | -0.25811 | 0 | 0
14 | 0.98566 | -0.27544 | 0.0077832 | 0.0019506
15 | 0.99193 | -0.15386 | 0 | 0
16 | 0.98692 | -0.25066 | 0.016405 | 0.0041115
17 | 0.98623 | -0.26441 | 0.090784 | 0.022753
18 | 0.99751 | -0.047195 | 0.0061343 | 0.0015374
19 | 0.99646 | -0.068002 | 0.047287 | 0.011851
20 | 0.98292 | -0.32851 | 0.067091 | 0.016815
21 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13479 | -0.033831 | 0.13498 | 0.033949 | 0.00018454 | 0.00011795 | 0.20114 | 0.20114 | 0.20114 | 0.99729 | -0.052006 | 0.99878 | -0.023342 | 55.2573
1 | 0.080295 | 0.020172 | -0.080215 | -0.020121 | 7.9407e-05 | 5.0628e-05 | 0.11982 | 0.11982 | 0.11982 | 0.99729 | -0.052006 | 0.99622 | -0.072749 | 32.918
2 | 0.038563 | 0.0096757 | -0.038547 | -0.0096657 | 1.5815e-05 | 9.9543e-06 | 0.057456 | 0.057456 | 0.057456 | 0.99878 | -0.023342 | 0.99834 | -0.031946 | 15.7846
3 | -0.17354 | -0.043624 | 0.17373 | 0.043748 | 0.00019365 | 0.00012353 | 0.25859 | 0.25859 | 0.25859 | 0.99878 | -0.023342 | 1 | 0 | 35.5209
4 | 0.06938 | 0.017405 | -0.069337 | -0.017377 | 4.305e-05 | 2.7413e-05 | 0.10364 | 0.10364 | 0.10364 | 0.99622 | -0.072749 | 0.99554 | -0.085774 | 28.4715
5 | 0.010836 | 0.0027167 | -0.010832 | -0.0027147 | 3.963e-06 | 2.0113e-06 | 0.016185 | 0.016185 | 0.016185 | 0.99622 | -0.072749 | 0.99582 | -0.080427 | 4.4465
6 | 0.038547 | 0.0096657 | -0.038534 | -0.0096575 | 1.3009e-05 | 8.1883e-06 | 0.057456 | 0.057456 | 0.057456 | 0.99834 | -0.031946 | 0.99797 | -0.03903 | 15.7846
7 | 0.20024 | 0.051212 | -0.19979 | -0.050927 | 0.00044718 | 0.0002855 | 0.29833 | 0.29833 | 0.29833 | 1 | 0 | 0.99756 | -0.04626 | 40.979
8 | 0.11221 | 0.028245 | -0.11192 | -0.028062 | 0.00028611 | 0.00018275 | 0.16701 | 0.16701 | 0.16701 | 1 | 0 | 0.99722 | -0.053494 | 45.8815
9 | 0.0061346 | 0.0015375 | -0.0061343 | -0.0015374 | 2.7325e-07 | 6.1277e-08 | 0.0091507 | 0.0091507 | 0.0091507 | 0.99756 | -0.04626 | 0.99751 | -0.047195 | 2.5139
10 | 0.19366 | 0.049389 | -0.19266 | -0.048751 | 0.0010005 | 0.00063868 | 0.28918 | 0.28918 | 0.28918 | 0.99756 | -0.04626 | 0.99193 | -0.15386 | 39.7221
11 | 0.04732 | 0.011872 | -0.047287 | -0.011851 | 3.2706e-05 | 2.0704e-05 | 0.070613 | 0.070613 | 0.070613 | 0.99722 | -0.053494 | 0.99646 | -0.068002 | 19.3993
12 | -0.017182 | -0.0043082 | 0.017189 | 0.0043127 | 7.5558e-06 | 4.4516e-06 | 0.025902 | 0.025902 | 0.025902 | 0.98709 | -0.24774 | 0.98756 | -0.23852 | 7.1159
13 | 0.0093883 | 0.0023535 | -0.0093856 | -0.0023522 | 2.707e-06 | 1.272e-06 | 0.014153 | 0.014153 | 0.014153 | 0.98709 | -0.24774 | 0.98677 | -0.2538 | 3.8882
14 | 0.0077935 | 0.0019547 | -0.0077896 | -0.0019532 | 3.8503e-06 | 1.514e-06 | 0.011749 | 0.011749 | 0.011749 | 0.98709 | -0.24774 | 0.98655 | -0.25811 | 3.2279
15 | 0.090896 | 0.022824 | -0.090784 | -0.022753 | 0.00011211 | 7.1545e-05 | 0.13697 | 0.13697 | 0.13697 | 0.98756 | -0.23852 | 0.98623 | -0.26441 | 37.6303
16 | -0.10809 | -0.027137 | 0.10852 | 0.027417 | 0.00043843 | 0.00028003 | 0.16288 | 0.16288 | 0.16288 | 0.98756 | -0.23852 | 0.99193 | -0.15386 | 44.7461
17 | 0.0077896 | 0.0019532 | -0.0077832 | -0.0019506 | 6.4291e-06 | 2.5304e-06 | 0.011749 | 0.01175 | 0.01175 | 0.98655 | -0.25811 | 0.98566 | -0.27544 | 3.228
18 | 0.084136 | 0.021334 | -0.083746 | -0.021085 | 0.00038951 | 0.00024845 | 0.1263 | 0.1263 | 0.1263 | 0.99193 | -0.15386 | 0.98692 | -0.25066 | 34.6982
19 | 0.067341 | 0.016974 | -0.067091 | -0.016815 | 0.00024983 | 0.00015907 | 0.10157 | 0.10157 | 0.10157 | 0.98692 | -0.25066 | 0.98292 | -0.32851 | 27.903

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48783 | 0.12321

## res_load
| p_mw | q_mvar
0 | 0.054499 | 0.013659
1 | 0.069337 | 0.017377
2 | 0.010832 | 0.0027147
3 | 0.038534 | 0.0096575
4 | 0.064601 | 0.01619
5 | 0.0093856 | 0.0023522
6 | 0.0077832 | 0.0019506
7 | 0.016405 | 0.0041115
8 | 0.090784 | 0.022753
9 | 0.0061343 | 0.0015374
10 | 0.047287 | 0.011851
11 | 0.067091 | 0.016815

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1