## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-137_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-137_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-137_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-137_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-137_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-137_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2701-137_0_5_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_2701-137_0_5_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2701-137_0_5_node_34 | 0.4 | n |  | TRUE
9 | bus_LV_2701-137_0_5_node_39 | 0.4 | n |  | TRUE
10 | bus_LV_2701-137_0_5_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_2701-137_0_5_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_2701-137_0_5_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_2701-137_0_5_node_37 | 0.4 | n |  | TRUE
14 | bus_LV_2701-137_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2701-137_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2701-137_0_5_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2701-137_0_5_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_2701-137_0_5_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2701-137_0_5_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_2701-137_0_5_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_2701-137_0_5_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_2701-137_0_5_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2701-137_0_5_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_2701-137_0_5_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_2701-137_0_5_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_2701-137_0_5_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_2701-137_0_5_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2701-137_0_5_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_2701-137_0_5_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_2701-137_0_5_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_2701-137_0_5_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_2701-137_0_5_node_41 | 0.4 | n |  | TRUE
33 | bus_LV_2701-137_0_5_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_2701-137_0_5_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_2701-137_0_5_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_2701-137_0_5_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_2701-137_0_5_node_36 | 0.4 | n |  | TRUE
38 | bus_LV_2701-137_0_5_node_38 | 0.4 | n |  | TRUE
39 | bus_MV_560_0_node_157 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-137_0_5_load_0 | 0 | 0.033793 | 0.0084694 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-137_0_5_load_1 | 1 | 0.023987 | 0.0060117 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-137_0_5_load_4 | 4 | 0.015114 | 0.0037879 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-137_0_5_load_5 | 5 | 0.016567 | 0.004152 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-137_0_5_load_8 | 6 | 0.024975 | 0.0062593 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-137_0_5_load_6 | 7 | 0.0058583 | 0.0014682 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-137_0_5_load_34 | 8 | 0.0097558 | 0.002445 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-137_0_5_load_33 | 11 | 0.013627 | 0.0034153 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-137_0_5_load_10 | 16 | 0.010816 | 0.0027109 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-137_0_5_load_17 | 17 | 0.0093849 | 0.0023521 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-137_0_5_load_12 | 18 | 0.061603 | 0.015439 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-137_0_5_load_27 | 20 | 0.0062007 | 0.001554 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-137_0_5_load_24 | 21 | 0.0088396 | 0.0022154 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-137_0_5_load_18 | 22 | 0.071524 | 0.017926 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-137_0_5_load_32 | 23 | 0.0092108 | 0.0023084 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-137_0_5_load_30 | 24 | 0.014105 | 0.0035351 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-137_0_5_load_16 | 25 | 0.013717 | 0.0034377 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-137_0_5_load_35 | 26 | 0.01414 | 0.0035438 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-137_0_5_load_19 | 27 | 0.0079969 | 0.0020042 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-137_0_5_load_21 | 28 | 0.0098185 | 0.0024608 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-137_0_5_load_22 | 29 | 0.006719 | 0.0016839 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-137_0_5_load_40 | 30 | 0.0071208 | 0.0017846 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-137_0_5_load_25 | 31 | 0.017604 | 0.0044119 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-137_0_5_load_41 | 32 | 0.0093786 | 0.0023505 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-137_0_5_load_26 | 33 | 0.0052979 | 0.0013278 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-137_0_5_load_28 | 34 | 0.020645 | 0.0051741 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-137_0_5_load_29 | 35 | 0.0058947 | 0.0014774 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-137_0_5_load_31 | 36 | 0.01256 | 0.0031478 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-137_0_5_load_36 | 37 | 0.0064538 | 0.0016175 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-137_0_5_load_38 | 38 | 0.0049727 | 0.0012463 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-137_0_5_line_0 |  | 0 | 1 | 0.019481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-137_0_5_line_1 |  | 0 | 2 | 0.023056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2701-137_0_5_line_2 |  | 1 | 3 | 0.013986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-137_0_5_line_3 |  | 2 | 4 | 0.0055774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-137_0_5_line_4 |  | 2 | 5 | 0.0076084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2701-137_0_5_line_5 |  | 3 | 6 | 0.010174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-137_0_5_line_6 |  | 3 | 7 | 0.016976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-137_0_5_line_7 |  | 4 | 8 | 0.0037745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-137_0_5_line_8 |  | 5 | 9 | 0.014076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2701-137_0_5_line_9 |  | 6 | 10 | 0.028617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-137_0_5_line_10 |  | 8 | 11 | 0.0063546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-137_0_5_line_11 |  | 9 | 12 | 0.004018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_2701-137_0_5_line_12 |  | 9 | 13 | 0.008108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-137_0_5_line_13 |  | 10 | 18 | 0.023769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-137_0_5_line_14 |  | 11 | 26 | 0.00076649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-137_0_5_line_15 |  | 12 | 32 | 0.01069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-137_0_5_line_16 |  | 12 | 29 | 0.019427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-137_0_5_line_17 |  | 13 | 37 | 0.0074819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-137_0_5_line_18 |  | 13 | 36 | 0.0026351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-137_0_5_line_19 |  | 14 | 15 | 0.011134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-137_0_5_line_20 |  | 14 | 16 | 0.0133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-137_0_5_line_21 |  | 15 | 17 | 0.014112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-137_0_5_line_22 |  | 17 | 22 | 0.0068255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-137_0_5_line_23 |  | 19 | 20 | 0.0070959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-137_0_5_line_24 |  | 19 | 21 | 0.015586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-137_0_5_line_25 |  | 20 | 30 | 0.011086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-137_0_5_line_26 |  | 21 | 31 | 0.011031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-137_0_5_line_27 |  | 22 | 27 | 2.2042e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-137_0_5_line_28 |  | 23 | 24 | 0.0046867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-137_0_5_line_29 |  | 24 | 34 | 0.0026396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-137_0_5_line_30 |  | 25 | 26 | 0.0060445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-137_0_5_line_31 |  | 27 | 28 | 0.0052447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-137_0_5_line_32 |  | 28 | 29 | 0.005047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-137_0_5_line_33 |  | 31 | 33 | 0.005477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-137_0_5_line_34 |  | 32 | 33 | 0.00044124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-137_0_5_line_35 |  | 34 | 35 | 0.0051929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-137_0_5_line_36 |  | 35 | 36 | 0.012262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-137_0_5_line_37 |  | 37 | 38 | 0.0042012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-137_0_5_trafo_2 | 0.63 MVA 20/0.4 kV | 39 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2611181.5435 | 1267472.9552 | 2611188.3026 | 1267454.6843
1 | 2611170.9594 | 1267493.4283 | 2611181.1568 | 1267474.0006 | 2611181.5435 | 1267472.9552
2 | 2611193.1551 | 1267441.5671 | 2611188.3026 | 1267454.6843
3 | 2611170.9594 | 1267493.4283 | 2611175.7961 | 1267496.2058
4 | 2611170.9594 | 1267493.4283 | 2611163.3513 | 1267493.3633
5 | 2611193.1551 | 1267441.5671 | 2611202.834 | 1267444.7029
6 | 2611193.1551 | 1267441.5671 | 2611177.0679 | 1267436.1474
7 | 2611179.0693 | 1267498.0854 | 2611175.7961 | 1267496.2058
8 | 2611149.2758 | 1267493.243 | 2611163.3513 | 1267493.3633
9 | 2611230.058 | 1267453.5229 | 2611202.834 | 1267444.7029
10 | 2611184.5799 | 1267501.2498 | 2611179.0693 | 1267498.0854
11 | 2611149.2758 | 1267493.243 | 2611149.1178 | 1267489.2288
12 | 2611149.2758 | 1267493.243 | 2611149.4563 | 1267501.3491
13 | 2611230.058 | 1267453.5229 | 2611226.1117 | 1267466.7135 | 2611221.5918 | 1267475.6346
14 | 2611184.5799 | 1267501.2498 | 2611185.2445 | 1267501.6315
15 | 2611149.1178 | 1267489.2288 | 2611138.4278 | 1267489.1538
16 | 2611149.1178 | 1267489.2288 | 2611149.8301 | 1267469.8146
17 | 2611149.4563 | 1267501.3491 | 2611141.9754 | 1267501.4703
18 | 2611149.4563 | 1267501.3491 | 2611149.5744 | 1267503.9815
19 | 2611153.5601 | 1267428.2278 | 2611149.5439 | 1267438.6164
20 | 2611153.5601 | 1267428.2278 | 2611160.1467 | 1267416.6738
21 | 2611149.5439 | 1267438.6164 | 2611150.5297 | 1267450.749 | 2611150.4586 | 1267452.6868
22 | 2611150.2083 | 1267459.5078 | 2611150.4586 | 1267452.6868
23 | 2611105.8934 | 1267488.9255 | 2611106.1987 | 1267494.7079 | 2611106.267 | 1267496.0116
24 | 2611105.8934 | 1267488.9255 | 2611121.479 | 1267489.0349
25 | 2611110.7202 | 1267503.7893 | 2611106.65 | 1267502.9256 | 2611106.5766 | 1267501.9247 | 2611106.267 | 1267496.0116
26 | 2611132.5097 | 1267489.1123 | 2611121.479 | 1267489.0349
27 | 2611150.2083 | 1267459.5078 | 2611150.2075 | 1267459.5298
28 | 2611150.4756 | 1267524.0559 | 2611150.6858 | 1267528.7379
29 | 2611150.4756 | 1267524.0559 | 2611150.3572 | 1267521.4189
30 | 2611190.4863 | 1267504.6416 | 2611185.2445 | 1267501.6315
31 | 2611150.2075 | 1267459.5298 | 2611150.0152 | 1267464.771
32 | 2611149.8301 | 1267469.8146 | 2611150.0152 | 1267464.771
33 | 2611137.9866 | 1267489.1507 | 2611132.5097 | 1267489.1123
34 | 2611138.4278 | 1267489.1538 | 2611137.9866 | 1267489.1507
35 | 2611150.1243 | 1267516.2312 | 2611150.3572 | 1267521.4189
36 | 2611150.1243 | 1267516.2312 | 2611149.5744 | 1267503.9815
37 | 2611137.7748 | 1267501.5384 | 2611141.9754 | 1267501.4703

## bus_geodata
| x | y | coords
0 | 2611181.5435 | 1267472.9552
1 | 2611188.3026 | 1267454.6843
2 | 2611170.9594 | 1267493.4283
3 | 2611193.1551 | 1267441.5671
4 | 2611175.7961 | 1267496.2058
5 | 2611163.3513 | 1267493.3633
6 | 2611202.834 | 1267444.7029
7 | 2611177.0679 | 1267436.1474
8 | 2611179.0693 | 1267498.0854
9 | 2611149.2758 | 1267493.243
10 | 2611230.058 | 1267453.5229
11 | 2611184.5799 | 1267501.2498
12 | 2611149.1178 | 1267489.2288
13 | 2611149.4563 | 1267501.3491
14 | 2611153.5601 | 1267428.2278
15 | 2611149.5439 | 1267438.6164
16 | 2611160.1467 | 1267416.6738
17 | 2611150.4586 | 1267452.6868
18 | 2611221.5917 | 1267475.6346
19 | 2611105.8934 | 1267488.9255
20 | 2611106.267 | 1267496.0116
21 | 2611121.479 | 1267489.0349
22 | 2611150.2083 | 1267459.5078
23 | 2611150.6858 | 1267528.7379
24 | 2611150.4756 | 1267524.0559
25 | 2611190.4863 | 1267504.6416
26 | 2611185.2445 | 1267501.6315
27 | 2611150.2075 | 1267459.5298
28 | 2611150.0152 | 1267464.771
29 | 2611149.8301 | 1267469.8146
30 | 2611110.7202 | 1267503.7893
31 | 2611132.5097 | 1267489.1123
32 | 2611138.4278 | 1267489.1538
33 | 2611137.9866 | 1267489.1507
34 | 2611150.3572 | 1267521.4189
35 | 2611150.1243 | 1267516.2312
36 | 2611149.5744 | 1267503.9815
37 | 2611141.9754 | 1267501.4703
38 | 2611137.7748 | 1267501.5384
39 | 2611149.2758 | 1267493.243

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99842 | -0.030231 | 0.033793 | 0.0084694
1 | 0.99635 | -0.06997 | 0.023987 | 0.0060117
2 | 1 | 0 | -0.48121 | -0.12091
3 | 0.99517 | -0.092696 | 0 | 0
4 | 0.99966 | -0.0064525 | 0.015114 | 0.0037879
5 | 0.9991 | -0.017329 | 0.016567 | 0.004152
6 | 0.99436 | -0.10821 | 0.024975 | 0.0062593
7 | 0.99508 | -0.094447 | 0.0058583 | 0.0014682
8 | 0.99949 | -0.0098262 | 0.0097558 | 0.002445
9 | 0.99753 | -0.047429 | 0 | 0
10 | 0.99275 | -0.13934 | 0 | 0
11 | 0.99925 | -0.014427 | 0.013627 | 0.0034153
12 | 0.99721 | -0.053438 | 0 | 0
13 | 0.99698 | -0.057922 | 0 | 0
14 | 0.9938 | -0.11935 | 0 | 0
15 | 0.99391 | -0.11722 | 0 | 0
16 | 0.99367 | -0.12189 | 0.010816 | 0.0027109
17 | 0.99405 | -0.11453 | 0.0093849 | 0.0023521
18 | 0.99141 | -0.16527 | 0.061603 | 0.015439
19 | 0.99606 | -0.075755 | 0 | 0
20 | 0.99597 | -0.077416 | 0.0062007 | 0.001554
21 | 0.99625 | -0.072108 | 0.0088396 | 0.0022154
22 | 0.99417 | -0.1121 | 0.071524 | 0.017926
23 | 0.99597 | -0.077385 | 0.0092108 | 0.0023084
24 | 0.99601 | -0.076626 | 0.014105 | 0.0035351
25 | 0.99916 | -0.016247 | 0.013717 | 0.0034377
26 | 0.99923 | -0.014799 | 0.01414 | 0.0035438
27 | 0.99417 | -0.11206 | 0.0079969 | 0.0020042
28 | 0.99465 | -0.10284 | 0.0098185 | 0.0024608
29 | 0.99515 | -0.093107 | 0.006719 | 0.0016839
30 | 0.9959 | -0.078803 | 0.0071208 | 0.0017846
31 | 0.99647 | -0.067816 | 0.017604 | 0.0044119
32 | 0.99668 | -0.063644 | 0.0093786 | 0.0023505
33 | 0.99667 | -0.063993 | 0.0052979 | 0.0013278
34 | 0.99607 | -0.075545 | 0.020645 | 0.0051741
35 | 0.99628 | -0.071536 | 0.0058947 | 0.0014774
36 | 0.99683 | -0.060807 | 0.01256 | 0.0031478
37 | 0.9969 | -0.059421 | 0.0064538 | 0.0016175
38 | 0.99689 | -0.059788 | 0.0049727 | 0.0012463
39 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.11698 | 0.029533 | -0.11676 | -0.029391 | 0.00022224 | 0.00014198 | 0.17442 | 0.17442 | 0.17442 | 0.99842 | -0.030231 | 0.99635 | -0.06997 | 47.9169
1 | -0.15077 | -0.038002 | 0.15099 | 0.038141 | 0.00021843 | 0.00013919 | 0.22478 | 0.22478 | 0.22478 | 0.99842 | -0.030231 | 1 | 0 | 30.8766
2 | 0.09277 | 0.023379 | -0.092669 | -0.023315 | 0.00010074 | 6.4293e-05 | 0.13859 | 0.13859 | 0.13859 | 0.99635 | -0.06997 | 0.99517 | -0.092696 | 38.0752
3 | 0.066392 | 0.016654 | -0.066372 | -0.016641 | 2.0416e-05 | 1.2993e-05 | 0.098798 | 0.098798 | 0.098798 | 1 | 0 | 0.99966 | -0.0064525 | 27.1424
4 | 0.26218 | 0.066119 | -0.26196 | -0.06598 | 0.00021728 | 0.00013886 | 0.39027 | 0.39027 | 0.39027 | 1 | 0 | 0.9991 | -0.017329 | 53.6079
5 | 0.08681 | 0.021846 | -0.086746 | -0.021805 | 6.4314e-05 | 4.1029e-05 | 0.12983 | 0.12983 | 0.12983 | 0.99517 | -0.092696 | 0.99436 | -0.10821 | 35.6686
6 | 0.0058588 | 0.0014683 | -0.0058583 | -0.0014682 | 4.8853e-07 | 9.2122e-08 | 0.0087603 | 0.0087604 | 0.0087604 | 0.99517 | -0.092696 | 0.99508 | -0.094447 | 2.4067
7 | 0.051258 | 0.012854 | -0.05125 | -0.012848 | 8.2404e-06 | 5.2244e-06 | 0.076301 | 0.076301 | 0.076301 | 0.99966 | -0.0064525 | 0.99949 | -0.0098262 | 20.9619
8 | 0.24539 | 0.061828 | -0.24504 | -0.061603 | 0.00035276 | 0.0002254 | 0.36559 | 0.36559 | 0.36559 | 0.9991 | -0.017329 | 0.99753 | -0.047429 | 50.2187
9 | 0.061771 | 0.015546 | -0.061679 | -0.015488 | 9.1741e-05 | 5.8343e-05 | 0.09246 | 0.09246 | 0.09246 | 0.99436 | -0.10821 | 0.99275 | -0.13934 | 25.4011
10 | 0.041494 | 0.010403 | -0.041485 | -0.010398 | 9.0943e-06 | 5.7371e-06 | 0.061777 | 0.061777 | 0.061777 | 0.99949 | -0.0098262 | 0.99925 | -0.014427 | 16.9717
11 | 0.17111 | 0.043044 | -0.17107 | -0.043013 | 4.9107e-05 | 3.1323e-05 | 0.25531 | 0.25531 | 0.25531 | 0.99753 | -0.047429 | 0.99721 | -0.053438 | 35.0698
12 | 0.073924 | 0.018558 | -0.073887 | -0.018535 | 3.698e-05 | 2.3562e-05 | 0.11028 | 0.11028 | 0.11028 | 0.99753 | -0.047429 | 0.99698 | -0.057922 | 30.2978
13 | 0.061679 | 0.015488 | -0.061603 | -0.015439 | 7.6199e-05 | 4.8461e-05 | 0.09246 | 0.09246 | 0.09246 | 0.99275 | -0.13934 | 0.99141 | -0.16527 | 25.4011
14 | 0.027858 | 0.0069823 | -0.027858 | -0.006982 | 4.9466e-07 | 3.0654e-07 | 0.041484 | 0.041484 | 0.041484 | 0.99925 | -0.014427 | 0.99923 | -0.014799 | 11.3968
15 | 0.054484 | 0.013671 | -0.054458 | -0.013654 | 2.6501e-05 | 1.6821e-05 | 0.081306 | 0.081306 | 0.081306 | 0.99721 | -0.053438 | 0.99668 | -0.063644 | 22.3367
16 | 0.11658 | 0.029342 | -0.11636 | -0.029201 | 0.00022058 | 0.00014092 | 0.174 | 0.174 | 0.174 | 0.99721 | -0.053438 | 0.99515 | -0.093107 | 47.803
17 | 0.011427 | 0.0028642 | -0.011427 | -0.0028638 | 8.1618e-07 | 4.2479e-07 | 0.017056 | 0.017056 | 0.017056 | 0.99698 | -0.057922 | 0.9969 | -0.059421 | 4.6856
18 | 0.06246 | 0.015671 | -0.062451 | -0.015665 | 8.5886e-06 | 5.4623e-06 | 0.093228 | 0.093228 | 0.093228 | 0.99698 | -0.057922 | 0.99683 | -0.060807 | 25.6122
19 | -0.010818 | -0.0027115 | 0.010819 | 0.0027121 | 1.0954e-06 | 5.568e-07 | 0.016198 | 0.016198 | 0.016198 | 0.9938 | -0.11935 | 0.99391 | -0.11722 | 4.4499
20 | 0.010818 | 0.0027115 | -0.010816 | -0.0027109 | 1.3085e-06 | 6.6514e-07 | 0.016198 | 0.016198 | 0.016198 | 0.9938 | -0.11935 | 0.99367 | -0.12189 | 4.4499
21 | -0.010819 | -0.0027121 | 0.01082 | 0.0027128 | 1.3884e-06 | 7.0566e-07 | 0.016198 | 0.016198 | 0.016198 | 0.99391 | -0.11722 | 0.99405 | -0.11453 | 4.4499
22 | -0.020205 | -0.0050649 | 0.020207 | 0.0050663 | 2.3415e-06 | 1.4101e-06 | 0.030246 | 0.030246 | 0.030246 | 0.99405 | -0.11453 | 0.99417 | -0.1121 | 8.3093
23 | 0.013323 | 0.0033394 | -0.013322 | -0.0033388 | 1.0541e-06 | 5.823e-07 | 0.019903 | 0.019903 | 0.019903 | 0.99606 | -0.075755 | 0.99597 | -0.077416 | 5.468
24 | -0.013323 | -0.0033394 | 0.013325 | 0.0033407 | 2.3154e-06 | 1.2789e-06 | 0.019903 | 0.019903 | 0.019903 | 0.99606 | -0.075755 | 0.99625 | -0.072108 | 5.468
25 | 0.0071212 | 0.0017848 | -0.0071208 | -0.0017846 | 4.7058e-07 | 1.5691e-07 | 0.010639 | 0.010639 | 0.010639 | 0.99597 | -0.077416 | 0.9959 | -0.078803 | 2.9229
26 | -0.022165 | -0.0055561 | 0.022169 | 0.0055589 | 4.5339e-06 | 2.758e-06 | 0.033106 | 0.033106 | 0.033106 | 0.99625 | -0.072108 | 0.99647 | -0.067816 | 9.0952
27 | -0.091731 | -0.022992 | 0.091731 | 0.022992 | 1.5582e-07 | 9.9438e-08 | 0.1373 | 0.1373 | 0.1373 | 0.99417 | -0.1121 | 0.99417 | -0.11206 | 37.7193
28 | -0.0092108 | -0.0023084 | 0.0092111 | 0.0023086 | 3.3282e-07 | 1.5201e-07 | 0.013761 | 0.013761 | 0.013761 | 0.99597 | -0.077385 | 0.99601 | -0.076626 | 3.7805
29 | -0.023316 | -0.0058437 | 0.023318 | 0.0058444 | 1.2011e-06 | 7.3435e-07 | 0.034834 | 0.034834 | 0.034834 | 0.99601 | -0.076626 | 0.99607 | -0.075545 | 9.5698
30 | -0.013717 | -0.0034377 | 0.013718 | 0.0034383 | 9.4589e-07 | 5.262e-07 | 0.020428 | 0.020428 | 0.020428 | 0.99916 | -0.016247 | 0.99923 | -0.014799 | 5.6121
31 | -0.099728 | -0.024996 | 0.099772 | 0.025024 | 4.3821e-05 | 2.7978e-05 | 0.14927 | 0.14927 | 0.14927 | 0.99417 | -0.11206 | 0.99465 | -0.10284 | 41.0076
32 | -0.10959 | -0.027485 | 0.10964 | 0.027517 | 5.0877e-05 | 3.2495e-05 | 0.16396 | 0.16396 | 0.16396 | 0.99465 | -0.10284 | 0.99515 | -0.093107 | 45.0429
33 | -0.039773 | -0.0099708 | 0.039781 | 0.0099754 | 7.2454e-06 | 4.5657e-06 | 0.059394 | 0.059394 | 0.059394 | 0.99647 | -0.067816 | 0.99667 | -0.063993 | 16.317
34 | 0.045079 | 0.011304 | -0.045078 | -0.011303 | 7.4952e-07 | 4.7394e-07 | 0.067304 | 0.067304 | 0.067304 | 0.99668 | -0.063644 | 0.99667 | -0.063993 | 18.49
35 | -0.043963 | -0.011019 | 0.043971 | 0.011024 | 8.3995e-06 | 5.3081e-06 | 0.065676 | 0.065676 | 0.065676 | 0.99607 | -0.075545 | 0.99628 | -0.071536 | 18.0427
36 | -0.049866 | -0.012501 | 0.049891 | 0.012517 | 2.5508e-05 | 1.6165e-05 | 0.07448 | 0.07448 | 0.07448 | 0.99628 | -0.071536 | 0.99683 | -0.060807 | 20.4615
37 | 0.0049728 | 0.0012463 | -0.0049727 | -0.0012463 | 8.6798e-08 | 7.7638e-10 | 0.0074226 | 0.0074226 | 0.0074226 | 0.9969 | -0.059421 | 0.99689 | -0.059788 | 2.0392

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48121 | 0.12091

## res_load
| p_mw | q_mvar
0 | 0.033793 | 0.0084694
1 | 0.023987 | 0.0060117
2 | 0.015114 | 0.0037879
3 | 0.016567 | 0.004152
4 | 0.024975 | 0.0062593
5 | 0.0058583 | 0.0014682
6 | 0.0097558 | 0.002445
7 | 0.013627 | 0.0034153
8 | 0.010816 | 0.0027109
9 | 0.0093849 | 0.0023521
10 | 0.061603 | 0.015439
11 | 0.0062007 | 0.001554
12 | 0.0088396 | 0.0022154
13 | 0.071524 | 0.017926
14 | 0.0092108 | 0.0023084
15 | 0.014105 | 0.0035351
16 | 0.013717 | 0.0034377
17 | 0.01414 | 0.0035438
18 | 0.0079969 | 0.0020042
19 | 0.0098185 | 0.0024608
20 | 0.006719 | 0.0016839
21 | 0.0071208 | 0.0017846
22 | 0.017604 | 0.0044119
23 | 0.0093786 | 0.0023505
24 | 0.0052979 | 0.0013278
25 | 0.020645 | 0.0051741
26 | 0.0058947 | 0.0014774
27 | 0.01256 | 0.0031478
28 | 0.0064538 | 0.0016175
29 | 0.0049727 | 0.0012463

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1