## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-154_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-154_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-154_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-154_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-154_0_4_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_2701-154_0_4_node_39 | 0.4 | n |  | TRUE
6 | bus_LV_2701-154_0_4_node_38 | 0.4 | n |  | TRUE
7 | bus_LV_2701-154_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2701-154_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2701-154_0_4_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_2701-154_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2701-154_0_4_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_2701-154_0_4_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_2701-154_0_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_2701-154_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2701-154_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2701-154_0_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_2701-154_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2701-154_0_4_node_42 | 0.4 | n |  | TRUE
19 | bus_LV_2701-154_0_4_node_50 | 0.4 | n |  | TRUE
20 | bus_LV_2701-154_0_4_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_2701-154_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_2701-154_0_4_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_2701-154_0_4_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_2701-154_0_4_node_48 | 0.4 | n |  | TRUE
25 | bus_LV_2701-154_0_4_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_2701-154_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_2701-154_0_4_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_2701-154_0_4_node_41 | 0.4 | n |  | TRUE
29 | bus_LV_2701-154_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_2701-154_0_4_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_2701-154_0_4_node_44 | 0.4 | n |  | TRUE
32 | bus_LV_2701-154_0_4_node_40 | 0.4 | n |  | TRUE
33 | bus_LV_2701-154_0_4_node_47 | 0.4 | n |  | TRUE
34 | bus_LV_2701-154_0_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_2701-154_0_4_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_2701-154_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_2701-154_0_4_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_2701-154_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_2701-154_0_4_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_2701-154_0_4_node_49 | 0.4 | n |  | TRUE
41 | bus_LV_2701-154_0_4_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_2701-154_0_4_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_2701-154_0_4_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_2701-154_0_4_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_2701-154_0_4_node_46 | 0.4 | n |  | TRUE
46 | bus_MV_561_0_node_81 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-154_0_4_load_0 | 0 | 0.0049033 | 0.0012289 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-154_0_4_load_39 | 5 | 0.0071145 | 0.0017831 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-154_0_4_load_38 | 6 | 0.0080641 | 0.002021 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-154_0_4_load_22 | 9 | 0.016156 | 0.0040492 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-154_0_4_load_17 | 11 | 0.018318 | 0.004591 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-154_0_4_load_29 | 12 | 0.017549 | 0.0043981 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-154_0_4_load_12 | 13 | 0.034693 | 0.008695 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-154_0_4_load_15 | 15 | 0.037201 | 0.0093234 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-154_0_4_load_16 | 16 | 0.0086954 | 0.0021793 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-154_0_4_load_13 | 17 | 0.014298 | 0.0035833 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-154_0_4_load_42 | 18 | 0.010437 | 0.0026158 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-154_0_4_load_50 | 19 | 0.0097783 | 0.0024507 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-154_0_4_load_45 | 20 | 0.010007 | 0.002508 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-154_0_4_load_20 | 21 | 0.0129 | 0.0032331 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-154_0_4_load_48 | 24 | 0.035082 | 0.0087923 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-154_0_4_load_43 | 27 | 0.0070728 | 0.0017726 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-154_0_4_load_41 | 28 | 0.0074337 | 0.0018631 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-154_0_4_load_18 | 29 | 0.019124 | 0.0047929 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-154_0_4_load_44 | 31 | 0.0099863 | 0.0025028 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-154_0_4_load_40 | 32 | 0.015021 | 0.0037646 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-154_0_4_load_47 | 33 | 0.022069 | 0.005531 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-154_0_4_load_19 | 34 | 0.050206 | 0.012583 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-154_0_4_load_21 | 35 | 0.0048147 | 0.0012067 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-154_0_4_load_28 | 37 | 0.037246 | 0.0093348 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-154_0_4_load_24 | 38 | 0.021284 | 0.0053343 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-154_0_4_load_26 | 39 | 0.022459 | 0.0056287 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-154_0_4_load_49 | 40 | 0.040012 | 0.010028 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-154_0_4_load_30 | 41 | 0.017333 | 0.004344 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-154_0_4_load_34 | 43 | 0.0047768 | 0.0011972 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-154_0_4_load_46 | 45 | 0.025204 | 0.0063167 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-154_0_4_line_0 |  | 0 | 1 | 0.014879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-154_0_4_line_1 |  | 0 | 2 | 0.0080415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-154_0_4_line_2 |  | 1 | 3 | 0.036291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-154_0_4_line_3 |  | 2 | 4 | 0.008698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-154_0_4_line_4 |  | 3 | 5 | 0.020224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-154_0_4_line_5 |  | 3 | 6 | 0.015786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-154_0_4_line_6 |  | 4 | 13 | 0.062172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-154_0_4_line_7 |  | 5 | 18 | 0.010251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-154_0_4_line_8 |  | 7 | 8 | 0.036007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-154_0_4_line_9 |  | 7 | 9 | 0.0057132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-154_0_4_line_10 |  | 8 | 12 | 0.0052243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-154_0_4_line_11 |  | 9 | 21 | 0.012219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-154_0_4_line_12 |  | 10 | 11 | 0.047636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2701-154_0_4_line_13 |  | 11 | 26 | 0.029814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2701-154_0_4_line_14 |  | 14 | 15 | 0.020981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-154_0_4_line_15 |  | 14 | 16 | 0.016722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-154_0_4_line_16 |  | 14 | 17 | 0.028822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_2701-154_0_4_line_17 |  | 15 | 27 | 0.00098169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-154_0_4_line_18 |  | 16 | 28 | 0.010509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-154_0_4_line_19 |  | 17 | 26 | 0.011786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_2701-154_0_4_line_20 |  | 18 | 32 | 0.0015141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-154_0_4_line_21 |  | 19 | 20 | 0.0064923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-154_0_4_line_22 |  | 20 | 31 | 0.0080043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-154_0_4_line_23 |  | 21 | 34 | 0.015046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-154_0_4_line_24 |  | 22 | 23 | 0.014296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-154_0_4_line_25 |  | 22 | 24 | 0.01945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2701-154_0_4_line_26 |  | 22 | 25 | 0.028432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2701-154_0_4_line_27 |  | 23 | 41 | 0.018372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-154_0_4_line_28 |  | 24 | 33 | 0.021407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2701-154_0_4_line_29 |  | 25 | 39 | 0.016108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-154_0_4_line_30 |  | 25 | 38 | 0.014964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_2701-154_0_4_line_31 |  | 26 | 29 | 0.020224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2701-154_0_4_line_32 |  | 27 | 31 | 0.0081404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-154_0_4_line_33 |  | 28 | 32 | 0.0094323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-154_0_4_line_34 |  | 29 | 30 | 0.062943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2701-154_0_4_line_35 |  | 30 | 33 | 0.039139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2701-154_0_4_line_36 |  | 34 | 35 | 0.0042667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-154_0_4_line_37 |  | 35 | 36 | 0.002208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-154_0_4_line_38 |  | 36 | 37 | 0.023998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2701-154_0_4_line_39 |  | 36 | 38 | 0.016904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2701-154_0_4_line_40 |  | 39 | 40 | 0.0033631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2701-154_0_4_line_41 |  | 41 | 42 | 0.00074822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-154_0_4_line_42 |  | 42 | 43 | 0.017241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-154_0_4_line_43 |  | 42 | 44 | 0.027251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-154_0_4_line_44 |  | 44 | 45 | 0.016125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-154_0_4_trafo_7 | 0.63 MVA 20/0.4 kV | 46 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2611446.006 | 1268002.731 | 2611441.52 | 1268014.6975 | 2611440.7731 | 1268016.6596
1 | 2611437.9119 | 1268024.1749 | 2611440.7731 | 1268016.6596
2 | 2611446.006 | 1268002.731 | 2611452.3926 | 1268008.1027 | 2611477.9735 | 1268019.5601
3 | 2611437.9119 | 1268024.1749 | 2611434.54 | 1268032.1963
4 | 2611477.9735 | 1268019.5601 | 2611496.5326 | 1268027.5961
5 | 2611477.9735 | 1268019.5601 | 2611483.8671 | 1268004.9158
6 | 2611434.54 | 1268032.1963 | 2611490.1282 | 1268060.0398
7 | 2611505.9393 | 1268031.6693 | 2611496.5326 | 1268027.5961
8 | 2611735.384 | 1267937.95 | 2611737.8196 | 1267931.7727 | 2611739.2486 | 1267928.451 | 2611740.4733 | 1267925.6959 | 2611750.1537 | 1267932.2752 | 2611759.9802 | 1267937.2871
9 | 2611735.384 | 1267937.95 | 2611732.7976 | 1267943.0443
10 | 2611759.9802 | 1267937.2871 | 2611764.6569 | 1267939.6155
11 | 2611727.2658 | 1267953.9396 | 2611732.7976 | 1267943.0443
12 | 2611613.7744 | 1267994.384 | 2611606.3726 | 1268004.0097 | 2611602.6577 | 1268010.229 | 2611590.7882 | 1268035.8641
13 | 2611578.2615 | 1268062.9184 | 2611590.7882 | 1268035.8641
14 | 2611540.9798 | 1268046.8235 | 2611545.553 | 1268036.4695 | 2611549.4051 | 1268027.609
15 | 2611540.9798 | 1268046.8235 | 2611539.7164 | 1268046.2984 | 2611528.0838 | 1268041.2612 | 2611525.6282 | 1268040.1947
16 | 2611540.9798 | 1268046.8235 | 2611542.1979 | 1268047.3595 | 2611550.334 | 1268050.8667 | 2611567.4403 | 1268058.2487
17 | 2611549.7965 | 1268026.7087 | 2611549.4051 | 1268027.609
18 | 2611525.6282 | 1268040.1947 | 2611525.5121 | 1268040.1443 | 2611515.9844 | 1268036.0188
19 | 2611578.2615 | 1268062.9184 | 2611567.4403 | 1268058.2487
20 | 2611507.3287 | 1268032.2709 | 2611505.9393 | 1268031.6693
21 | 2611556.2335 | 1268011.9027 | 2611557.4973 | 1268008.9957 | 2611558.9568 | 1268006.0109
22 | 2611556.2335 | 1268011.9027 | 2611553.0422 | 1268019.2433
23 | 2611720.4544 | 1267967.3552 | 2611727.2658 | 1267953.9396
24 | 2611689.9404 | 1268026.7672 | 2611703.1449 | 1268032.3416
25 | 2611689.9404 | 1268026.7672 | 2611686.2015 | 1268033.7203 | 2611680.9267 | 1268044.0014
26 | 2611689.9404 | 1268026.7672 | 2611693.3621 | 1268020.4584 | 2611703.0927 | 1268001.5421
27 | 2611703.1449 | 1268032.3416 | 2611720.0738 | 1268039.4797
28 | 2611671.1549 | 1268063.0474 | 2611680.9267 | 1268044.0014
29 | 2611703.0927 | 1268001.5421 | 2611688.4438 | 1267994.8425
30 | 2611703.0927 | 1268001.5421 | 2611709.8686 | 1267988.2004
31 | 2611578.2615 | 1268062.9184 | 2611596.5965 | 1268071.4531
32 | 2611549.7965 | 1268026.7087 | 2611553.0422 | 1268019.2433
33 | 2611507.3287 | 1268032.2709 | 2611515.9844 | 1268036.0188
34 | 2611653.6463 | 1268098.046 | 2611642.8116 | 1268092.9656 | 2611596.5965 | 1268071.4531
35 | 2611653.6463 | 1268098.046 | 2611658.0146 | 1268088.6591 | 2611671.1549 | 1268063.0474
36 | 2611720.4544 | 1267967.3552 | 2611718.5228 | 1267971.1596
37 | 2611717.5232 | 1267973.1284 | 2611718.5228 | 1267971.1596
38 | 2611717.5232 | 1267973.1284 | 2611695.7287 | 1267963.0841
39 | 2611717.5232 | 1267973.1284 | 2611709.8686 | 1267988.2004
40 | 2611685.3853 | 1267993.4437 | 2611688.4438 | 1267994.8425
41 | 2611720.0738 | 1268039.4797 | 2611720.7633 | 1268039.7704
42 | 2611720.7633 | 1268039.7704 | 2611736.4086 | 1268047.0148
43 | 2611707.8468 | 1268063.7729 | 2611719.1252 | 1268042.3023 | 2611720.7633 | 1268039.7704
44 | 2611707.8468 | 1268063.7729 | 2611700.2978 | 1268078.0214

## bus_geodata
| x | y | coords
0 | 2611440.7731 | 1268016.6596
1 | 2611446.006 | 1268002.731
2 | 2611437.9119 | 1268024.1749
3 | 2611477.9735 | 1268019.5601
4 | 2611434.54 | 1268032.1963
5 | 2611496.5326 | 1268027.5961
6 | 2611483.8671 | 1268004.9158
7 | 2611735.384 | 1267937.95
8 | 2611759.9802 | 1267937.2871
9 | 2611732.7976 | 1267943.0443
10 | 2611613.7744 | 1267994.384
11 | 2611590.7882 | 1268035.8641
12 | 2611764.6569 | 1267939.6155
13 | 2611490.1282 | 1268060.0398
14 | 2611540.9798 | 1268046.8235
15 | 2611549.4051 | 1268027.609
16 | 2611525.6282 | 1268040.1947
17 | 2611567.4403 | 1268058.2487
18 | 2611505.9393 | 1268031.6693
19 | 2611558.9568 | 1268006.0109
20 | 2611556.2335 | 1268011.9027
21 | 2611727.2658 | 1267953.9396
22 | 2611689.9404 | 1268026.7672
23 | 2611703.1449 | 1268032.3416
24 | 2611680.9267 | 1268044.0014
25 | 2611703.0927 | 1268001.5421
26 | 2611578.2615 | 1268062.9184
27 | 2611549.7965 | 1268026.7087
28 | 2611515.9844 | 1268036.0188
29 | 2611596.5965 | 1268071.4531
30 | 2611653.6463 | 1268098.046
31 | 2611553.0422 | 1268019.2433
32 | 2611507.3287 | 1268032.2709
33 | 2611671.1549 | 1268063.0474
34 | 2611720.4544 | 1267967.3552
35 | 2611718.5228 | 1267971.1596
36 | 2611717.5232 | 1267973.1284
37 | 2611695.7287 | 1267963.0841
38 | 2611709.8686 | 1267988.2004
39 | 2611688.4438 | 1267994.8425
40 | 2611685.3853 | 1267993.4437
41 | 2611720.0738 | 1268039.4797
42 | 2611720.7633 | 1268039.7704
43 | 2611736.4086 | 1268047.0148
44 | 2611707.8468 | 1268063.7729
45 | 2611700.2978 | 1268078.0214
46 | 2611584.6245 | 1267968.42

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98108 | -0.36312 | 0.0049033 | 0.0012289
1 | 0.98162 | -0.35246 | 0 | 0
2 | 0.98082 | -0.36818 | 0 | 0
3 | 0.98295 | -0.3265 | 0 | 0
4 | 0.98054 | -0.37365 | 0 | 0
5 | 0.98385 | -0.30913 | 0.0071145 | 0.0017831
6 | 0.98284 | -0.3288 | 0.0080641 | 0.002021
7 | 0.97161 | -0.54751 | 0 | 0
8 | 0.97102 | -0.55918 | 0 | 0
9 | 0.97171 | -0.54566 | 0.016156 | 0.0040492
10 | 1 | 0 | -0.56156 | -0.14446
11 | 0.99393 | -0.11471 | 0.018318 | 0.004591
12 | 0.97094 | -0.56088 | 0.017549 | 0.0043981
13 | 0.97854 | -0.41283 | 0.034693 | 0.008695
14 | 0.9875 | -0.23827 | 0 | 0
15 | 0.98607 | -0.26607 | 0.037201 | 0.0093234
16 | 0.98601 | -0.26711 | 0.0086954 | 0.0021793
17 | 0.98976 | -0.19447 | 0.014298 | 0.0035833
18 | 0.98437 | -0.29902 | 0.010437 | 0.0026158
19 | 0.98561 | -0.27505 | 0.0097783 | 0.0024507
20 | 0.98567 | -0.27391 | 0.010007 | 0.002508
21 | 0.97209 | -0.53806 | 0.0129 | 0.0032331
22 | 0.97812 | -0.41951 | 0 | 0
23 | 0.97749 | -0.43184 | 0 | 0
24 | 0.97934 | -0.39563 | 0.035082 | 0.0087923
25 | 0.97665 | -0.44838 | 0 | 0
26 | 0.99026 | -0.18479 | 0 | 0
27 | 0.98603 | -0.26672 | 0.0070728 | 0.0017726
28 | 0.98516 | -0.28364 | 0.0074337 | 0.0018631
29 | 0.98863 | -0.21596 | 0.019124 | 0.0047929
30 | 0.98384 | -0.3082 | 0 | 0
31 | 0.98581 | -0.27107 | 0.0099863 | 0.0025028
32 | 0.98446 | -0.29725 | 0.015021 | 0.0037646
33 | 0.98086 | -0.36601 | 0.022069 | 0.005531
34 | 0.97275 | -0.52513 | 0.050206 | 0.012583
35 | 0.97313 | -0.51753 | 0.0048147 | 0.0012067
36 | 0.97334 | -0.5134 | 0 | 0
37 | 0.97251 | -0.52986 | 0.037246 | 0.0093348
38 | 0.97553 | -0.47031 | 0.021284 | 0.0053343
39 | 0.97571 | -0.46679 | 0.022459 | 0.0056287
40 | 0.97559 | -0.46925 | 0.040012 | 0.010028
41 | 0.97669 | -0.44771 | 0.017333 | 0.004344
42 | 0.97666 | -0.44812 | 0 | 0
43 | 0.97659 | -0.44963 | 0.0047768 | 0.0011972
44 | 0.97603 | -0.46068 | 0 | 0
45 | 0.97565 | -0.46812 | 0.025204 | 0.0063167
46 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.039679 | -0.0099756 | 0.039699 | 0.0099883 | 2.0216e-05 | 1.275e-05 | 0.060193 | 0.060193 | 0.060193 | 0.98108 | -0.36312 | 0.98162 | -0.35246 | 16.5365
1 | 0.034776 | 0.0087467 | -0.034767 | -0.0087414 | 8.3929e-06 | 5.27e-06 | 0.052756 | 0.052756 | 0.052756 | 0.98108 | -0.36312 | 0.98082 | -0.36818 | 14.4934
2 | -0.039699 | -0.0099883 | 0.039749 | 0.010019 | 4.9308e-05 | 3.1098e-05 | 0.060193 | 0.060193 | 0.060193 | 0.98162 | -0.35246 | 0.98295 | -0.3265 | 16.5365
3 | 0.034767 | 0.0087414 | -0.034758 | -0.0087357 | 9.0781e-06 | 5.7002e-06 | 0.052756 | 0.052756 | 0.052756 | 0.98082 | -0.36818 | 0.98054 | -0.37365 | 14.4934
4 | -0.047813 | -0.012041 | 0.047853 | 0.012066 | 3.9756e-05 | 2.5187e-05 | 0.072402 | 0.072402 | 0.072402 | 0.98295 | -0.3265 | 0.98385 | -0.30913 | 19.8906
5 | 0.008065 | 0.0020214 | -0.0080641 | -0.002021 | 8.8238e-07 | 3.6465e-07 | 0.012209 | 0.012209 | 0.012209 | 0.98295 | -0.3265 | 0.98284 | -0.3288 | 3.3541
6 | 0.034758 | 0.0087357 | -0.034693 | -0.008695 | 6.4889e-05 | 4.0746e-05 | 0.052756 | 0.052756 | 0.052756 | 0.98054 | -0.37365 | 0.97854 | -0.41283 | 14.4935
7 | -0.054968 | -0.013849 | 0.054994 | 0.013866 | 2.6585e-05 | 1.6884e-05 | 0.083162 | 0.083162 | 0.083162 | 0.98385 | -0.30913 | 0.98437 | -0.29902 | 22.8467
8 | 0.01756 | 0.0044047 | -0.01755 | -0.0043989 | 9.7662e-06 | 5.8047e-06 | 0.026894 | 0.026894 | 0.026894 | 0.97161 | -0.54751 | 0.97102 | -0.55918 | 7.3885
9 | -0.01756 | -0.0044047 | 0.017561 | 0.0044057 | 1.5496e-06 | 9.2098e-07 | 0.026894 | 0.026894 | 0.026894 | 0.97161 | -0.54751 | 0.97171 | -0.54566 | 7.3885
10 | 0.01755 | 0.0043989 | -0.017549 | -0.0043981 | 1.417e-06 | 8.4227e-07 | 0.026894 | 0.026894 | 0.026894 | 0.97102 | -0.55918 | 0.97094 | -0.56088 | 7.3885
11 | -0.033718 | -0.0084548 | 0.03373 | 0.0084625 | 1.2217e-05 | 7.6674e-06 | 0.051635 | 0.051635 | 0.051635 | 0.97171 | -0.54566 | 0.97209 | -0.53806 | 14.1854
12 | 0.55991 | 0.14446 | -0.5568 | -0.14247 | 0.003111 | 0.0019886 | 0.83463 | 0.83463 | 0.83463 | 1 | 0 | 0.99393 | -0.11471 | 57.3237
13 | 0.53848 | 0.13788 | -0.53666 | -0.13672 | 0.0018212 | 0.001164 | 0.80721 | 0.80721 | 0.80721 | 0.99393 | -0.11471 | 0.99026 | -0.18479 | 55.4402
14 | 0.074154 | 0.018627 | -0.074056 | -0.018564 | 9.8261e-05 | 6.2619e-05 | 0.11175 | 0.11175 | 0.11175 | 0.9875 | -0.23827 | 0.98607 | -0.26607 | 30.7018
15 | 0.096843 | 0.024455 | -0.096709 | -0.02437 | 0.00013365 | 8.5325e-05 | 0.14599 | 0.14599 | 0.14599 | 0.9875 | -0.23827 | 0.98601 | -0.26711 | 40.1083
16 | -0.171 | -0.043082 | 0.17136 | 0.043311 | 0.00035902 | 0.00022903 | 0.25775 | 0.25775 | 0.25775 | 0.9875 | -0.23827 | 0.98976 | -0.19447 | 35.405
17 | 0.036855 | 0.0092405 | -0.036854 | -0.0092398 | 1.1387e-06 | 7.1627e-07 | 0.055617 | 0.055617 | 0.055617 | 0.98607 | -0.26607 | 0.98603 | -0.26672 | 15.2794
18 | 0.088014 | 0.022191 | -0.087944 | -0.022146 | 6.9577e-05 | 4.4395e-05 | 0.13287 | 0.13287 | 0.13287 | 0.98601 | -0.26711 | 0.98516 | -0.28364 | 36.5032
19 | -0.18565 | -0.046894 | 0.18574 | 0.046949 | 8.6158e-05 | 5.4535e-05 | 0.27924 | 0.27924 | 0.27924 | 0.98976 | -0.19447 | 0.99026 | -0.18479 | 19.1788
20 | -0.065432 | -0.016482 | 0.065437 | 0.016485 | 5.5579e-06 | 3.5378e-06 | 0.098939 | 0.098939 | 0.098939 | 0.98437 | -0.29902 | 0.98446 | -0.29725 | 27.1811
21 | -0.0097783 | -0.0024507 | 0.0097788 | 0.0024509 | 5.306e-07 | 2.5684e-07 | 0.014763 | 0.014763 | 0.014763 | 0.98561 | -0.27505 | 0.98567 | -0.27391 | 4.0557
22 | -0.019786 | -0.0049589 | 0.019789 | 0.0049605 | 2.6781e-06 | 1.6119e-06 | 0.02987 | 0.02987 | 0.02987 | 0.98567 | -0.27391 | 0.98581 | -0.27107 | 8.206
23 | -0.04663 | -0.011696 | 0.046659 | 0.011714 | 2.8748e-05 | 1.8212e-05 | 0.071382 | 0.071382 | 0.071382 | 0.97209 | -0.53806 | 0.97275 | -0.52513 | 19.6103
24 | 0.047402 | 0.011913 | -0.047374 | -0.011896 | 2.7888e-05 | 1.7669e-05 | 0.072125 | 0.072125 | 0.072125 | 0.97812 | -0.41951 | 0.97749 | -0.43184 | 19.8146
25 | -0.27099 | -0.068321 | 0.2713 | 0.068518 | 0.00031012 | 0.0001975 | 0.4124 | 0.4124 | 0.4124 | 0.97812 | -0.41951 | 0.97934 | -0.39563 | 28.3244
26 | 0.22359 | 0.056407 | -0.22328 | -0.056211 | 0.00030864 | 0.0001961 | 0.34028 | 0.34028 | 0.34028 | 0.97812 | -0.41951 | 0.97665 | -0.44838 | 23.3708
27 | 0.047374 | 0.011896 | -0.047339 | -0.011873 | 3.584e-05 | 2.2708e-05 | 0.072125 | 0.072125 | 0.072125 | 0.97749 | -0.43184 | 0.97669 | -0.44771 | 19.8146
28 | -0.30638 | -0.07731 | 0.30682 | 0.077588 | 0.00043525 | 0.00027748 | 0.46571 | 0.46571 | 0.46571 | 0.97934 | -0.39563 | 0.98086 | -0.36601 | 31.9853
29 | 0.062531 | 0.015695 | -0.062476 | -0.01566 | 5.4838e-05 | 3.4895e-05 | 0.09528 | 0.09528 | 0.09528 | 0.97665 | -0.44838 | 0.97571 | -0.46679 | 26.1757
30 | 0.16075 | 0.040516 | -0.16058 | -0.040409 | 0.00016841 | 0.00010741 | 0.245 | 0.245 | 0.245 | 0.97665 | -0.44838 | 0.97553 | -0.47031 | 33.6537
31 | 0.35092 | 0.08977 | -0.35039 | -0.089433 | 0.00052851 | 0.00033721 | 0.52797 | 0.52797 | 0.52797 | 0.99026 | -0.18479 | 0.98863 | -0.21596 | 36.2615
32 | 0.029781 | 0.0074672 | -0.029775 | -0.0074633 | 6.1661e-06 | 3.8425e-06 | 0.044943 | 0.044944 | 0.044944 | 0.98603 | -0.26672 | 0.98581 | -0.27107 | 12.3471
33 | 0.08051 | 0.020283 | -0.080458 | -0.02025 | 5.2339e-05 | 3.3377e-05 | 0.12164 | 0.12164 | 0.12164 | 0.98516 | -0.28364 | 0.98446 | -0.29725 | 33.4186
34 | 0.33127 | 0.08464 | -0.3298 | -0.083702 | 0.0014704 | 0.00093786 | 0.49918 | 0.49918 | 0.49918 | 0.98863 | -0.21596 | 0.98384 | -0.3082 | 34.2846
35 | 0.3298 | 0.083702 | -0.32889 | -0.083119 | 0.00091434 | 0.0005832 | 0.49918 | 0.49919 | 0.49919 | 0.98384 | -0.3082 | 0.98086 | -0.36601 | 34.2847
36 | -0.096865 | -0.024297 | 0.0969 | 0.024319 | 3.5133e-05 | 2.2432e-05 | 0.14818 | 0.14818 | 0.14818 | 0.97275 | -0.52513 | 0.97313 | -0.51753 | 40.7093
37 | -0.10171 | -0.025526 | 0.10173 | 0.025538 | 2.0032e-05 | 1.2793e-05 | 0.15554 | 0.15554 | 0.15554 | 0.97313 | -0.51753 | 0.97334 | -0.5134 | 42.7319
38 | 0.037275 | 0.0093532 | -0.037246 | -0.0093348 | 2.9228e-05 | 1.8408e-05 | 0.05699 | 0.05699 | 0.05699 | 0.97334 | -0.5134 | 0.97251 | -0.52986 | 15.6565
39 | -0.13901 | -0.034892 | 0.1393 | 0.035075 | 0.00028634 | 0.00018305 | 0.21253 | 0.21253 | 0.21253 | 0.97334 | -0.5134 | 0.97553 | -0.47031 | 58.3884
40 | 0.040017 | 0.010031 | -0.040012 | -0.010028 | 4.6972e-06 | 2.9642e-06 | 0.061028 | 0.061028 | 0.061028 | 0.97571 | -0.46679 | 0.97559 | -0.46925 | 16.7661
41 | 0.030006 | 0.0075291 | -0.030005 | -0.0075287 | 5.8645e-07 | 3.6597e-07 | 0.045718 | 0.045718 | 0.045718 | 0.97669 | -0.44771 | 0.97666 | -0.44812 | 12.5599
42 | 0.0047771 | 0.0011972 | -0.0047768 | -0.0011972 | 3.425e-07 | 3.4558e-09 | 0.0072782 | 0.0072783 | 0.0072783 | 0.97666 | -0.44812 | 0.97659 | -0.44963 | 1.9995
43 | 0.025228 | 0.0063316 | -0.025213 | -0.0063222 | 1.51e-05 | 9.3232e-06 | 0.03844 | 0.03844 | 0.03844 | 0.97666 | -0.44812 | 0.97603 | -0.46068 | 10.5604
44 | 0.025213 | 0.0063222 | -0.025204 | -0.0063167 | 8.9349e-06 | 5.5169e-06 | 0.03844 | 0.03844 | 0.03844 | 0.97603 | -0.46068 | 0.97565 | -0.46812 | 10.5605

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56156 | 0.14446

## res_load
| p_mw | q_mvar
0 | 0.0049033 | 0.0012289
1 | 0.0071145 | 0.0017831
2 | 0.0080641 | 0.002021
3 | 0.016156 | 0.0040492
4 | 0.018318 | 0.004591
5 | 0.017549 | 0.0043981
6 | 0.034693 | 0.008695
7 | 0.037201 | 0.0093234
8 | 0.0086954 | 0.0021793
9 | 0.014298 | 0.0035833
10 | 0.010437 | 0.0026158
11 | 0.0097783 | 0.0024507
12 | 0.010007 | 0.002508
13 | 0.0129 | 0.0032331
14 | 0.035082 | 0.0087923
15 | 0.0070728 | 0.0017726
16 | 0.0074337 | 0.0018631
17 | 0.019124 | 0.0047929
18 | 0.0099863 | 0.0025028
19 | 0.015021 | 0.0037646
20 | 0.022069 | 0.005531
21 | 0.050206 | 0.012583
22 | 0.0048147 | 0.0012067
23 | 0.037246 | 0.0093348
24 | 0.021284 | 0.0053343
25 | 0.022459 | 0.0056287
26 | 0.040012 | 0.010028
27 | 0.017333 | 0.004344
28 | 0.0047768 | 0.0011972
29 | 0.025204 | 0.0063167

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1