## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-162_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-162_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2701-162_0_4_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_2701-162_0_4_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_2701-162_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2701-162_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2701-162_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2701-162_0_4_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_2701-162_0_4_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_2701-162_0_4_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_2701-162_0_4_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_2701-162_0_4_node_31 | 0.4 | n |  | TRUE
12 | bus_LV_2701-162_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_2701-162_0_4_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_2701-162_0_4_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_2701-162_0_4_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_2701-162_0_4_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_2701-162_0_4_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_2701-162_0_4_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_2701-162_0_4_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_2701-162_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2701-162_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2701-162_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2701-162_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_2701-162_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2701-162_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2701-162_0_4_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_2701-162_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_2701-162_0_4_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_2701-162_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_2701-162_0_4_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_2701-162_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_2701-162_0_4_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_2701-162_0_4_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_2701-162_0_4_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_2701-162_0_4_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_2701-162_0_4_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_2701-162_0_4_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_2701-162_0_4_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_2701-162_0_4_node_42 | 0.4 | n |  | TRUE
40 | bus_MV_562_0_node_20 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-162_0_4_load_0 | 0 | 0.025717 | 0.0064454 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-162_0_4_load_9 | 3 | 0.012092 | 0.0030305 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-162_0_4_load_44 | 7 | 0.012543 | 0.0031436 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-162_0_4_load_21 | 8 | 0.01118 | 0.0028021 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-162_0_4_load_19 | 9 | 0.01983 | 0.00497 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-162_0_4_load_20 | 10 | 0.032086 | 0.0080415 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-162_0_4_load_31 | 11 | 0.025083 | 0.0062863 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-162_0_4_load_28 | 12 | 0.0085655 | 0.0021467 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-162_0_4_load_45 | 13 | 0.011314 | 0.0028355 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-162_0_4_load_22 | 14 | 0.0067862 | 0.0017008 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-162_0_4_load_23 | 15 | 0.0066674 | 0.001671 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-162_0_4_load_18 | 16 | 0.012991 | 0.0032558 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-162_0_4_load_30 | 17 | 0.012772 | 0.003201 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-162_0_4_load_36 | 18 | 0.0040785 | 0.0010222 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-162_0_4_load_34 | 19 | 0.011006 | 0.0027585 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-162_0_4_load_11 | 20 | 0.012592 | 0.0031557 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-162_0_4_load_12 | 21 | 0.0087305 | 0.0021881 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-162_0_4_load_15 | 23 | 0.0075758 | 0.0018987 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-162_0_4_load_16 | 24 | 0.0072158 | 0.0018084 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-162_0_4_load_17 | 25 | 0.0097634 | 0.0024469 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-162_0_4_load_25 | 26 | 0.0063645 | 0.0015951 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-162_0_4_load_24 | 27 | 0.0064781 | 0.0016236 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-162_0_4_load_37 | 28 | 0.011889 | 0.0029796 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-162_0_4_load_26 | 29 | 0.0079918 | 0.0020029 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-162_0_4_load_38 | 30 | 0.0084427 | 0.0021159 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-162_0_4_load_27 | 31 | 0.0057893 | 0.0014509 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-162_0_4_load_29 | 32 | 0.014292 | 0.0035819 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-162_0_4_load_32 | 33 | 0.004341 | 0.001088 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-162_0_4_load_33 | 34 | 0.0042977 | 0.0010771 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-162_0_4_load_35 | 35 | 0.0064295 | 0.0016114 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-162_0_4_load_40 | 36 | 0.0068064 | 0.0017059 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-162_0_4_load_41 | 37 | 0.0062298 | 0.0015613 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-162_0_4_load_39 | 38 | 0.0075201 | 0.0018847 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-162_0_4_load_42 | 39 | 0.0062575 | 0.0015683 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-162_0_4_line_0 |  | 0 | 1 | 0.020148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-162_0_4_line_1 |  | 1 | 2 | 0.010911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-162_0_4_line_2 |  | 1 | 3 | 0.03819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-162_0_4_line_3 |  | 2 | 10 | 0.024464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-162_0_4_line_4 |  | 2 | 11 | 0.015234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2701-162_0_4_line_5 |  | 4 | 5 | 0.007233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-162_0_4_line_6 |  | 4 | 6 | 0.010652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-162_0_4_line_7 |  | 5 | 7 | 0.0092619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-162_0_4_line_8 |  | 6 | 8 | 0.012817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-162_0_4_line_9 |  | 6 | 9 | 0.012995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-162_0_4_line_10 |  | 7 | 13 | 0.014299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-162_0_4_line_11 |  | 8 | 12 | 0.011489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-162_0_4_line_12 |  | 9 | 16 | 0.016664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-162_0_4_line_13 |  | 10 | 16 | 0.024426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-162_0_4_line_14 |  | 11 | 17 | 0.015007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2701-162_0_4_line_15 |  | 14 | 15 | 0.0092287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-162_0_4_line_16 |  | 15 | 27 | 0.0088969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-162_0_4_line_17 |  | 17 | 32 | 0.0068871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2701-162_0_4_line_18 |  | 18 | 19 | 0.013256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-162_0_4_line_19 |  | 19 | 33 | 0.0030361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-162_0_4_line_20 |  | 20 | 21 | 0.0032595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-162_0_4_line_21 |  | 20 | 22 | 0.018946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-162_0_4_line_22 |  | 22 | 23 | 0.020113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-162_0_4_line_23 |  | 22 | 24 | 0.010587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-162_0_4_line_24 |  | 22 | 25 | 0.01331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-162_0_4_line_25 |  | 23 | 26 | 0.0078089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2701-162_0_4_line_26 |  | 24 | 27 | 0.0089268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-162_0_4_line_27 |  | 25 | 28 | 0.0070107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-162_0_4_line_28 |  | 26 | 29 | 0.0018315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_2701-162_0_4_line_29 |  | 28 | 30 | 0.0087455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-162_0_4_line_30 |  | 29 | 31 | 0.0071366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_2701-162_0_4_line_31 |  | 30 | 38 | 0.010394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-162_0_4_line_32 |  | 31 | 32 | 0.0045671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2701-162_0_4_line_33 |  | 33 | 34 | 0.0086331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-162_0_4_line_34 |  | 34 | 35 | 0.00091135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-162_0_4_line_35 |  | 35 | 36 | 0.0091188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-162_0_4_line_36 |  | 36 | 37 | 2.4646e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-162_0_4_line_37 |  | 37 | 39 | 0.009032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-162_0_4_line_38 |  | 38 | 39 | 0.000179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-162_0_4_trafo_29 | 0.63 MVA 20/0.4 kV | 40 | 32 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2610669.0905 | 1267199.7009 | 2610674.623 | 1267195.3967 | 2610684.9969 | 1267187.3339
1 | 2610660.678 | 1267206.6796 | 2610669.0905 | 1267199.7009
2 | 2610669.0905 | 1267199.7009 | 2610673.6562 | 1267205.6688 | 2610692.3116 | 1267230.0204
3 | 2610660.678 | 1267206.6796 | 2610673.0516 | 1267223.7582 | 2610675.0912 | 1267226.4466
4 | 2610660.678 | 1267206.6796 | 2610648.9528 | 1267216.4054
5 | 2610722.9908 | 1267258.0387 | 2610717.2024 | 1267262.3979
6 | 2610708.6705 | 1267268.7759 | 2610710.8185 | 1267267.2009 | 2610717.2024 | 1267262.3979
7 | 2610722.9908 | 1267258.0387 | 2610716.9111 | 1267251.0516
8 | 2610708.6705 | 1267268.7759 | 2610709.5571 | 1267273.8366 | 2610709.9353 | 1267281.5068
9 | 2610708.6705 | 1267268.7759 | 2610703.2461 | 1267263.2623 | 2610700.3771 | 1267259.7769 | 2610699.926 | 1267259.1823
10 | 2610707.5251 | 1267240.265 | 2610716.9111 | 1267251.0516
11 | 2610709.9353 | 1267281.5068 | 2610710.5011 | 1267292.9819
12 | 2610689.8544 | 1267245.9065 | 2610699.926 | 1267259.1823
13 | 2610675.0912 | 1267226.4466 | 2610689.8544 | 1267245.9065
14 | 2610637.4023 | 1267225.9863 | 2610648.9528 | 1267216.4054
15 | 2610619.3418 | 1267289.2554 | 2610614.6467 | 1267281.3103
16 | 2610610.1203 | 1267273.6508 | 2610614.6467 | 1267281.3103
17 | 2610637.4023 | 1267225.9863 | 2610632.1015 | 1267230.3832
18 | 2610556.8688 | 1267185.2932 | 2610563.7339 | 1267196.6331
19 | 2610565.3063 | 1267199.2304 | 2610563.7339 | 1267196.6331
20 | 2610585.5485 | 1267268.8718 | 2610583.0291 | 1267270.9399
21 | 2610600.1926 | 1267256.851 | 2610585.5485 | 1267268.8718
22 | 2610600.1926 | 1267256.851 | 2610615.6733 | 1267244.0101
23 | 2610600.1926 | 1267256.851 | 2610605.5788 | 1267265.9656
24 | 2610600.1926 | 1267256.851 | 2610595.5397 | 1267249.1706 | 2610593.2974 | 1267245.4667
25 | 2610615.6733 | 1267244.0101 | 2610621.6837 | 1267239.0246
26 | 2610610.1203 | 1267273.6508 | 2610605.5788 | 1267265.9656
27 | 2610589.6667 | 1267239.4694 | 2610593.2974 | 1267245.4667
28 | 2610623.0933 | 1267237.8553 | 2610621.6837 | 1267239.0246
29 | 2610589.6667 | 1267239.4694 | 2610585.1375 | 1267231.9881
30 | 2610623.0933 | 1267237.8553 | 2610628.5862 | 1267233.299
31 | 2610579.7546 | 1267223.0965 | 2610585.1375 | 1267231.9881
32 | 2610632.1015 | 1267230.3832 | 2610628.5862 | 1267233.299
33 | 2610565.3063 | 1267199.2304 | 2610569.7772 | 1267206.6155
34 | 2610570.2492 | 1267207.3951 | 2610569.7772 | 1267206.6155
35 | 2610574.9716 | 1267215.1959 | 2610570.2492 | 1267207.3951
36 | 2610574.9844 | 1267215.217 | 2610574.9716 | 1267215.1959
37 | 2610579.6619 | 1267222.9434 | 2610574.9844 | 1267215.217
38 | 2610579.7546 | 1267223.0965 | 2610579.6619 | 1267222.9434

## bus_geodata
| x | y | coords
0 | 2610684.9969 | 1267187.3339
1 | 2610669.0905 | 1267199.7009
2 | 2610660.678 | 1267206.6796
3 | 2610692.3116 | 1267230.0204
4 | 2610717.2024 | 1267262.3979
5 | 2610722.9908 | 1267258.0387
6 | 2610708.6705 | 1267268.7759
7 | 2610716.9111 | 1267251.0516
8 | 2610709.9353 | 1267281.5068
9 | 2610699.926 | 1267259.1823
10 | 2610675.0912 | 1267226.4466
11 | 2610648.9528 | 1267216.4054
12 | 2610710.5011 | 1267292.9819
13 | 2610707.5251 | 1267240.265
14 | 2610619.3418 | 1267289.2554
15 | 2610614.6467 | 1267281.3103
16 | 2610689.8544 | 1267245.9065
17 | 2610637.4023 | 1267225.9863
18 | 2610556.8688 | 1267185.2932
19 | 2610563.7339 | 1267196.6331
20 | 2610585.5485 | 1267268.8718
21 | 2610583.0291 | 1267270.9399
22 | 2610600.1926 | 1267256.851
23 | 2610615.6733 | 1267244.0101
24 | 2610605.5788 | 1267265.9656
25 | 2610593.2974 | 1267245.4667
26 | 2610621.6837 | 1267239.0246
27 | 2610610.1203 | 1267273.6508
28 | 2610589.6667 | 1267239.4694
29 | 2610623.0933 | 1267237.8553
30 | 2610585.1375 | 1267231.9881
31 | 2610628.5862 | 1267233.299
32 | 2610632.1015 | 1267230.3832
33 | 2610565.3063 | 1267199.2304
34 | 2610569.7772 | 1267206.6155
35 | 2610570.2492 | 1267207.3951
36 | 2610574.9716 | 1267215.1959
37 | 2610574.9844 | 1267215.217
38 | 2610579.7546 | 1267223.0965
39 | 2610579.6619 | 1267222.9434
40 | 2610660.678 | 1267206.6796

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99638 | -0.069371 | 0.025717 | 0.0064454
1 | 0.99686 | -0.060278 | 0 | 0
2 | 0.99723 | -0.053045 | 0 | 0
3 | 0.99644 | -0.068382 | 0.012092 | 0.0030305
4 | 0.99138 | -0.16587 | 0 | 0
5 | 0.99122 | -0.16893 | 0 | 0
6 | 0.99161 | -0.16136 | 0 | 0
7 | 0.99102 | -0.17285 | 0.012543 | 0.0031436
8 | 0.99138 | -0.16585 | 0.01118 | 0.0028021
9 | 0.99213 | -0.15132 | 0.01983 | 0.00497
10 | 0.99481 | -0.099687 | 0.032086 | 0.0080415
11 | 0.99825 | -0.033531 | 0.025083 | 0.0062863
12 | 0.99129 | -0.16759 | 0.0085655 | 0.0021467
13 | 0.99087 | -0.17572 | 0.011314 | 0.0028355
14 | 0.99544 | -0.087619 | 0.0067862 | 0.0017008
15 | 0.99549 | -0.086517 | 0.0066674 | 0.001671
16 | 0.9931 | -0.13262 | 0.012991 | 0.0032558
17 | 0.99942 | -0.011061 | 0.012772 | 0.003201
18 | 0.99253 | -0.14374 | 0.0040785 | 0.0010222
19 | 0.99258 | -0.14278 | 0.011006 | 0.0027585
20 | 0.99566 | -0.083333 | 0.012592 | 0.0031557
21 | 0.99563 | -0.083833 | 0.0087305 | 0.0021881
22 | 0.99603 | -0.076233 | 0 | 0
23 | 0.99851 | -0.028459 | 0.0075758 | 0.0018987
24 | 0.99577 | -0.081284 | 0.0072158 | 0.0018084
25 | 0.99497 | -0.096613 | 0.0097634 | 0.0024469
26 | 0.99902 | -0.018696 | 0.0063645 | 0.0015951
27 | 0.9956 | -0.084412 | 0.0064781 | 0.0016236
28 | 0.99447 | -0.10616 | 0.011889 | 0.0029796
29 | 0.99915 | -0.016305 | 0.0079918 | 0.0020029
30 | 0.99395 | -0.11625 | 0.0084427 | 0.0021159
31 | 0.99966 | -0.0065001 | 0.0057893 | 0.0014509
32 | 1 | 0 | -0.35073 | -0.088125
33 | 0.99262 | -0.14197 | 0.004341 | 0.001088
34 | 0.99278 | -0.13901 | 0.0042977 | 0.0010771
35 | 0.9928 | -0.13862 | 0.0064295 | 0.0016114
36 | 0.99305 | -0.13376 | 0.0068064 | 0.0017059
37 | 0.99305 | -0.13375 | 0.0062298 | 0.0015613
38 | 0.99341 | -0.1267 | 0.0075201 | 0.0018847
39 | 0.9934 | -0.12685 | 0.0062575 | 0.0015683
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.025717 | -0.0064454 | 0.025728 | 0.0064522 | 1.1145e-05 | 6.8703e-06 | 0.038407 | 0.038407 | 0.038407 | 0.99638 | -0.069371 | 0.99686 | -0.060278 | 10.5513
1 | -0.037825 | -0.0094853 | 0.037838 | 0.0094935 | 1.3045e-05 | 8.2063e-06 | 0.056464 | 0.056464 | 0.056464 | 0.99686 | -0.060278 | 0.99723 | -0.053045 | 15.512
2 | 0.012097 | 0.003033 | -0.012092 | -0.0030305 | 4.6697e-06 | 2.4909e-06 | 0.018057 | 0.018057 | 0.018057 | 0.99686 | -0.060278 | 0.99644 | -0.068382 | 4.9608
3 | 0.10897 | 0.027488 | -0.10873 | -0.027333 | 0.00024274 | 0.00015504 | 0.16266 | 0.16266 | 0.16266 | 0.99723 | -0.053045 | 0.99481 | -0.099687 | 44.6877
4 | -0.14681 | -0.036981 | 0.14695 | 0.037069 | 0.00013715 | 8.7379e-05 | 0.21913 | 0.21913 | 0.21913 | 0.99723 | -0.053045 | 0.99825 | -0.033531 | 30.0998
5 | 0.023867 | 0.0059848 | -0.023863 | -0.0059827 | 3.4809e-06 | 2.1346e-06 | 0.035824 | 0.035824 | 0.035824 | 0.99138 | -0.16587 | 0.99122 | -0.16893 | 9.8418
6 | -0.023867 | -0.0059848 | 0.023872 | 0.005988 | 5.1266e-06 | 3.1436e-06 | 0.035824 | 0.035824 | 0.035824 | 0.99138 | -0.16587 | 0.99161 | -0.16136 | 9.8417
7 | 0.023863 | 0.0059827 | -0.023859 | -0.00598 | 4.4574e-06 | 2.7333e-06 | 0.035824 | 0.035824 | 0.035824 | 0.99122 | -0.16893 | 0.99102 | -0.17285 | 9.8418
8 | 0.019751 | 0.0049516 | -0.019747 | -0.0049491 | 4.2223e-06 | 2.537e-06 | 0.029639 | 0.029639 | 0.029639 | 0.99161 | -0.16136 | 0.99138 | -0.16585 | 8.1425
9 | -0.043623 | -0.01094 | 0.043644 | 0.010953 | 2.0883e-05 | 1.3198e-05 | 0.065463 | 0.065463 | 0.065463 | 0.99161 | -0.16136 | 0.99213 | -0.15132 | 17.9842
10 | 0.011316 | 0.0028363 | -0.011314 | -0.0028355 | 1.5478e-06 | 8.0642e-07 | 0.01699 | 0.01699 | 0.01699 | 0.99102 | -0.17285 | 0.99087 | -0.17572 | 4.6677
11 | 0.0085662 | 0.002147 | -0.0085655 | -0.0021467 | 7.1225e-07 | 3.0771e-07 | 0.012857 | 0.012858 | 0.012858 | 0.99138 | -0.16585 | 0.99129 | -0.16759 | 3.5323
12 | -0.063474 | -0.015923 | 0.063531 | 0.015959 | 5.664e-05 | 3.6034e-05 | 0.095205 | 0.095205 | 0.095205 | 0.99213 | -0.15132 | 0.9931 | -0.13262 | 26.1551
13 | 0.076642 | 0.019291 | -0.076522 | -0.019215 | 0.00012044 | 7.6767e-05 | 0.11467 | 0.11467 | 0.11467 | 0.99481 | -0.099687 | 0.9931 | -0.13262 | 31.5026
14 | -0.17203 | -0.043355 | 0.17221 | 0.043473 | 0.00018515 | 0.0001181 | 0.25652 | 0.25652 | 0.25652 | 0.99825 | -0.033531 | 0.99942 | -0.011061 | 35.2357
15 | -0.0067862 | -0.0017008 | 0.0067866 | 0.0017009 | 3.5614e-07 | 1.0795e-07 | 0.010144 | 0.010144 | 0.010144 | 0.99544 | -0.087619 | 0.99549 | -0.086517 | 2.7869
16 | -0.013454 | -0.0033719 | 0.013455 | 0.0033727 | 1.3493e-06 | 7.4788e-07 | 0.02011 | 0.02011 | 0.02011 | 0.99549 | -0.086517 | 0.9956 | -0.084412 | 5.5248
17 | -0.18499 | -0.046674 | 0.18508 | 0.046737 | 9.8034e-05 | 6.2561e-05 | 0.27553 | 0.27553 | 0.27553 | 0.99942 | -0.011061 | 1 | 0 | 37.8477
18 | -0.0040785 | -0.0010222 | 0.0040787 | 0.0010221 | 1.8585e-07 | -5.2387e-08 | 0.0061145 | 0.0061144 | 0.0061145 | 0.99253 | -0.14374 | 0.99258 | -0.14278 | 1.6798
19 | -0.015085 | -0.0037806 | 0.015086 | 0.0037809 | 5.8227e-07 | 3.3341e-07 | 0.022615 | 0.022615 | 0.022615 | 0.99258 | -0.14278 | 0.99262 | -0.14197 | 6.2128
20 | 0.0087307 | 0.0021882 | -0.0087305 | -0.0021881 | 2.081e-07 | 9.0794e-08 | 0.013048 | 0.013048 | 0.013048 | 0.99566 | -0.083333 | 0.99563 | -0.083833 | 3.5846
21 | -0.021322 | -0.0053439 | 0.021329 | 0.0053483 | 7.2146e-06 | 4.3708e-06 | 0.031866 | 0.031866 | 0.031866 | 0.99566 | -0.083333 | 0.99603 | -0.076233 | 8.7545
22 | -0.13576 | -0.034109 | 0.13607 | 0.034307 | 0.00031033 | 0.00019835 | 0.20284 | 0.20284 | 0.20284 | 0.99603 | -0.076233 | 0.99851 | -0.028459 | 55.7259
23 | 0.027159 | 0.0068105 | -0.027152 | -0.0068065 | 6.5363e-06 | 4.0455e-06 | 0.040575 | 0.040575 | 0.040575 | 0.99603 | -0.076233 | 0.99577 | -0.081284 | 11.1471
24 | 0.087267 | 0.02195 | -0.087182 | -0.021896 | 8.4871e-05 | 5.4144e-05 | 0.1304 | 0.1304 | 0.1304 | 0.99603 | -0.076233 | 0.99497 | -0.096613 | 35.8244
25 | -0.14364 | -0.036206 | 0.14371 | 0.036249 | 6.7136e-05 | 4.2763e-05 | 0.21413 | 0.21413 | 0.21413 | 0.99851 | -0.028459 | 0.99902 | -0.018696 | 29.4137
26 | 0.019936 | 0.004998 | -0.019933 | -0.0049962 | 2.9713e-06 | 1.7855e-06 | 0.029792 | 0.029792 | 0.029792 | 0.99577 | -0.081284 | 0.9956 | -0.084412 | 8.1848
27 | 0.077419 | 0.019449 | -0.077384 | -0.019427 | 3.5253e-05 | 2.2471e-05 | 0.1158 | 0.1158 | 0.1158 | 0.99497 | -0.096613 | 0.99447 | -0.10616 | 31.813
28 | -0.15007 | -0.037844 | 0.15009 | 0.037855 | 1.7171e-05 | 1.0941e-05 | 0.22361 | 0.22361 | 0.22361 | 0.99902 | -0.018696 | 0.99915 | -0.016305 | 30.7159
29 | 0.065495 | 0.016447 | -0.065464 | -0.016427 | 3.1504e-05 | 2.0049e-05 | 0.098011 | 0.098011 | 0.098011 | 0.99447 | -0.10616 | 0.99395 | -0.11625 | 26.926
30 | -0.15808 | -0.039858 | 0.15816 | 0.039905 | 7.4221e-05 | 4.7314e-05 | 0.23551 | 0.23551 | 0.23551 | 0.99915 | -0.016305 | 0.99966 | -0.0065001 | 32.3507
31 | 0.057021 | 0.014311 | -0.056992 | -0.014293 | 2.8408e-05 | 1.8047e-05 | 0.085371 | 0.085371 | 0.085371 | 0.99395 | -0.11625 | 0.99341 | -0.1267 | 23.4537
32 | -0.16395 | -0.041356 | 0.164 | 0.041389 | 5.1038e-05 | 3.2544e-05 | 0.24413 | 0.24413 | 0.24413 | 0.99966 | -0.0065001 | 1 | 0 | 33.5345
33 | -0.019427 | -0.0048689 | 0.019429 | 0.0048705 | 2.7456e-06 | 1.6456e-06 | 0.029122 | 0.029122 | 0.029122 | 0.99262 | -0.14197 | 0.99278 | -0.13901 | 8.0006
34 | -0.023727 | -0.0059476 | 0.023728 | 0.0059479 | 4.3224e-07 | 2.6485e-07 | 0.035564 | 0.035564 | 0.035564 | 0.99278 | -0.13901 | 0.9928 | -0.13862 | 9.7702
35 | -0.030157 | -0.0075593 | 0.030164 | 0.0075636 | 6.9864e-06 | 4.3533e-06 | 0.0452 | 0.0452 | 0.0452 | 0.9928 | -0.13862 | 0.99305 | -0.13376 | 12.4177
36 | -0.03697 | -0.0092695 | 0.036971 | 0.0092695 | 2.8364e-08 | 1.7839e-08 | 0.055399 | 0.055399 | 0.055399 | 0.99305 | -0.13376 | 0.99305 | -0.13375 | 15.2196
37 | -0.0432 | -0.010831 | 0.043214 | 0.01084 | 1.4193e-05 | 8.9668e-06 | 0.064734 | 0.064734 | 0.064734 | 0.99305 | -0.13375 | 0.9934 | -0.12685 | 17.7841
38 | 0.049472 | 0.012408 | -0.049472 | -0.012408 | 3.6865e-07 | 2.3362e-07 | 0.074107 | 0.074107 | 0.074107 | 0.99341 | -0.1267 | 0.9934 | -0.12685 | 20.3591

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36502 | 0.091707

## res_load
| p_mw | q_mvar
0 | 0.025717 | 0.0064454
1 | 0.012092 | 0.0030305
2 | 0.012543 | 0.0031436
3 | 0.01118 | 0.0028021
4 | 0.01983 | 0.00497
5 | 0.032086 | 0.0080415
6 | 0.025083 | 0.0062863
7 | 0.0085655 | 0.0021467
8 | 0.011314 | 0.0028355
9 | 0.0067862 | 0.0017008
10 | 0.0066674 | 0.001671
11 | 0.012991 | 0.0032558
12 | 0.012772 | 0.003201
13 | 0.0040785 | 0.0010222
14 | 0.011006 | 0.0027585
15 | 0.012592 | 0.0031557
16 | 0.0087305 | 0.0021881
17 | 0.0075758 | 0.0018987
18 | 0.0072158 | 0.0018084
19 | 0.0097634 | 0.0024469
20 | 0.0063645 | 0.0015951
21 | 0.0064781 | 0.0016236
22 | 0.011889 | 0.0029796
23 | 0.0079918 | 0.0020029
24 | 0.0084427 | 0.0021159
25 | 0.0057893 | 0.0014509
26 | 0.014292 | 0.0035819
27 | 0.004341 | 0.001088
28 | 0.0042977 | 0.0010771
29 | 0.0064295 | 0.0016114
30 | 0.0068064 | 0.0017059
31 | 0.0062298 | 0.0015613
32 | 0.0075201 | 0.0018847
33 | 0.0062575 | 0.0015683

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1