## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-16_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-16_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-16_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2701-16_0_4_node_38 | 0.4 | n |  | TRUE
4 | bus_LV_2701-16_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2701-16_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_2701-16_0_4_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_2701-16_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2701-16_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_2701-16_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_2701-16_0_4_node_49 | 0.4 | n |  | TRUE
11 | bus_LV_2701-16_0_4_node_37 | 0.4 | n |  | TRUE
12 | bus_LV_2701-16_0_4_node_22 | 0.4 | n |  | TRUE
13 | bus_LV_2701-16_0_4_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_2701-16_0_4_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_2701-16_0_4_node_35 | 0.4 | n |  | TRUE
16 | bus_LV_2701-16_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2701-16_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2701-16_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2701-16_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2701-16_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2701-16_0_4_node_46 | 0.4 | n |  | TRUE
22 | bus_LV_2701-16_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_2701-16_0_4_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_2701-16_0_4_node_39 | 0.4 | n |  | TRUE
25 | bus_LV_2701-16_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2701-16_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2701-16_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_2701-16_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_2701-16_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2701-16_0_4_node_44 | 0.4 | n |  | TRUE
31 | bus_LV_2701-16_0_4_node_42 | 0.4 | n |  | TRUE
32 | bus_LV_2701-16_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_2701-16_0_4_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_2701-16_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_2701-16_0_4_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_2701-16_0_4_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_2701-16_0_4_node_47 | 0.4 | n |  | TRUE
38 | bus_LV_2701-16_0_4_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_2701-16_0_4_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_2701-16_0_4_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_2701-16_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_2701-16_0_4_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_2701-16_0_4_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_2701-16_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_2701-16_0_4_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_2701-16_0_4_node_41 | 0.4 | n |  | TRUE
47 | bus_MV_562_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-16_0_4_load_0 | 0 | 0.013982 | 0.0035043 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-16_0_4_load_3 | 2 | 0.0046274 | 0.0011597 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-16_0_4_load_38 | 3 | 0.0071245 | 0.0017856 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-16_0_4_load_31 | 6 | 0.0065801 | 0.0016491 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-16_0_4_load_8 | 7 | 0.025047 | 0.0062775 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-16_0_4_load_9 | 9 | 0.022937 | 0.0057486 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-16_0_4_load_49 | 10 | 0.013452 | 0.0033715 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-16_0_4_load_37 | 11 | 0.0044922 | 0.0011259 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-16_0_4_load_22 | 12 | 0.0073562 | 0.0018436 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-16_0_4_load_21 | 13 | 0.015664 | 0.0039256 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-16_0_4_load_29 | 14 | 0.009856 | 0.0024701 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-16_0_4_load_35 | 15 | 0.012214 | 0.0030611 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-16_0_4_load_10 | 16 | 0.0067897 | 0.0017017 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-16_0_4_load_11 | 17 | 0.0044174 | 0.0011071 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-16_0_4_load_12 | 18 | 0.0031224 | 0.00078254 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-16_0_4_load_13 | 19 | 0.0042648 | 0.0010689 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-16_0_4_load_14 | 20 | 0.0052892 | 0.0013256 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-16_0_4_load_46 | 21 | 0.0067114 | 0.001682 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-16_0_4_load_20 | 22 | 0.0031098 | 0.00077938 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-16_0_4_load_43 | 23 | 0.003688 | 0.0009243 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-16_0_4_load_39 | 24 | 0.0055846 | 0.0013996 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-16_0_4_load_15 | 25 | 0.0064957 | 0.001628 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-16_0_4_load_16 | 26 | 0.014865 | 0.0037254 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-16_0_4_load_17 | 27 | 0.0047701 | 0.0011955 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-16_0_4_load_18 | 28 | 0.0053156 | 0.0013322 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-16_0_4_load_19 | 29 | 0.0086761 | 0.0021744 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-16_0_4_load_44 | 30 | 0.0095628 | 0.0023967 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-16_0_4_load_23 | 32 | 0.016096 | 0.004034 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-16_0_4_load_24 | 33 | 0.0032113 | 0.00080482 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-16_0_4_load_25 | 34 | 0.010289 | 0.0025787 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-16_0_4_load_26 | 35 | 0.0047235 | 0.0011838 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-16_0_4_load_27 | 36 | 0.011094 | 0.0027804 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-16_0_4_load_47 | 37 | 0.0049436 | 0.001239 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-16_0_4_load_30 | 38 | 0.0047099 | 0.0011804 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-16_0_4_load_45 | 39 | 0.0048398 | 0.001213 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-16_0_4_load_28 | 40 | 0.0037054 | 0.00092866 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-16_0_4_load_32 | 41 | 0.030314 | 0.0075973 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-16_0_4_load_33 | 42 | 0.0032387 | 0.0008117 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-16_0_4_load_34 | 43 | 0.0032411 | 0.0008123 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-16_0_4_load_36 | 44 | 0.0052559 | 0.0013172 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-16_0_4_load_40 | 45 | 0.012959 | 0.0032479 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2701-16_0_4_load_41 | 46 | 0.0033305 | 0.0008347 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-16_0_4_line_0 |  | 0 | 1 | 0.021947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-16_0_4_line_1 |  | 1 | 2 | 0.015424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-16_0_4_line_2 |  | 2 | 3 | 0.023015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-16_0_4_line_3 |  | 3 | 11 | 0.0062954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-16_0_4_line_4 |  | 4 | 5 | 0.018049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-16_0_4_line_5 |  | 4 | 6 | 0.038228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-16_0_4_line_6 |  | 5 | 7 | 0.04637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-16_0_4_line_7 |  | 6 | 14 | 0.0063211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-16_0_4_line_8 |  | 7 | 9 | 0.022637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-16_0_4_line_9 |  | 8 | 9 | 0.030938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-16_0_4_line_10 |  | 8 | 10 | 0.017047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-16_0_4_line_11 |  | 10 | 15 | 0.026537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-16_0_4_line_12 |  | 11 | 24 | 0.0031745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-16_0_4_line_13 |  | 12 | 13 | 0.011058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-16_0_4_line_14 |  | 13 | 28 | 1.9073e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-16_0_4_line_15 |  | 14 | 40 | 0.00061211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-16_0_4_line_16 |  | 15 | 42 | 0.011031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-16_0_4_line_17 |  | 16 | 17 | 0.0026284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-16_0_4_line_18 |  | 16 | 18 | 0.006286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-16_0_4_line_19 |  | 17 | 19 | 0.0093746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-16_0_4_line_20 |  | 18 | 20 | 0.0050933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-16_0_4_line_21 |  | 19 | 21 | 0.0016586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-16_0_4_line_22 |  | 20 | 22 | 0.002434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-16_0_4_line_23 |  | 21 | 23 | 0.010419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-16_0_4_line_24 |  | 22 | 24 | 0.0067801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-16_0_4_line_25 |  | 23 | 46 | 0.0068187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-16_0_4_line_26 |  | 25 | 26 | 0.0026534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-16_0_4_line_27 |  | 25 | 27 | 0.0087834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-16_0_4_line_28 |  | 26 | 28 | 0.0062778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-16_0_4_line_29 |  | 27 | 29 | 0.0030073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-16_0_4_line_30 |  | 29 | 30 | 0.0097828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-16_0_4_line_31 |  | 30 | 31 | 0.005779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-16_0_4_line_32 |  | 31 | 39 | 0.0031128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2701-16_0_4_line_33 |  | 31 | 45 | 0.017378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-16_0_4_line_34 |  | 32 | 33 | 0.00019408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_2701-16_0_4_line_35 |  | 32 | 34 | 0.014934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_2701-16_0_4_line_36 |  | 33 | 35 | 0.00014233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_2701-16_0_4_line_37 |  | 34 | 36 | 0.012631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_2701-16_0_4_line_38 |  | 35 | 37 | 0.00718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_2701-16_0_4_line_39 |  | 36 | 38 | 0.012353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_2701-16_0_4_line_40 |  | 37 | 39 | 0.0071087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_2701-16_0_4_line_41 |  | 38 | 40 | 0.007549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-16_0_4_line_42 |  | 41 | 42 | 0.0037973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-16_0_4_line_43 |  | 41 | 43 | 0.0052971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-16_0_4_line_44 |  | 43 | 44 | 0.01065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2701-16_0_4_line_45 |  | 45 | 46 | 0.0022699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-16_0_4_trafo_25 | 0.63 MVA 20/0.4 kV | 47 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2610621.7218 | 1266960.7714 | 2610606.3314 | 1266976.4183
1 | 2610621.7218 | 1266960.7714 | 2610632.4326 | 1266971.87
2 | 2610648.4144 | 1266988.4306 | 2610632.4326 | 1266971.87
3 | 2610648.4144 | 1266988.4306 | 2610652.7861 | 1266992.9606
4 | 2610608.4751 | 1267120.2703 | 2610613.7733 | 1267116.5104 | 2610614.3486 | 1267110.485 | 2610612.0141 | 1267106.9339 | 2610611.331 | 1267105.8875
5 | 2610611.331 | 1267105.8875 | 2610620.4114 | 1267100.0886 | 2610643.5488 | 1267085.3104
6 | 2610608.4751 | 1267120.2703 | 2610619.7269 | 1267133.5329 | 2610637.0505 | 1267156.7615
7 | 2610648.8759 | 1267081.9078 | 2610643.5488 | 1267085.3104
8 | 2610637.0505 | 1267156.7615 | 2610650.5839 | 1267174.9079
9 | 2610669.0905 | 1267199.7009 | 2610665.3211 | 1267194.6684 | 2610650.5839 | 1267174.9079
10 | 2610669.0905 | 1267199.7009 | 2610674.623 | 1267195.3967 | 2610682.5481 | 1267189.2371
11 | 2610682.5481 | 1267189.2371 | 2610703.5009 | 1267172.952
12 | 2610654.9905 | 1266995.2448 | 2610652.7861 | 1266992.9606
13 | 2610744.5039 | 1267021.374 | 2610735.127 | 1267027.2358
14 | 2610735.127 | 1267027.2358 | 2610735.1108 | 1267027.2459
15 | 2610649.3918 | 1267081.5783 | 2610648.8759 | 1267081.9078
16 | 2610712.2104 | 1267166.1827 | 2610703.5009 | 1267172.952
17 | 2610669.291 | 1267010.0632 | 2610671.1162 | 1267011.9545
18 | 2610669.291 | 1267010.0632 | 2610664.9259 | 1267005.54
19 | 2610677.6262 | 1267018.7002 | 2610671.1162 | 1267011.9545
20 | 2610661.389 | 1267001.875 | 2610664.9259 | 1267005.54
21 | 2610677.6262 | 1267018.7002 | 2610678.7779 | 1267019.8936
22 | 2610659.6988 | 1267000.1236 | 2610661.389 | 1267001.875
23 | 2610678.7779 | 1267019.8936 | 2610686.0133 | 1267027.391
24 | 2610659.6988 | 1267000.1236 | 2610654.9905 | 1266995.2448
25 | 2610690.7483 | 1267032.2975 | 2610686.0133 | 1267027.391
26 | 2610727.5376 | 1267031.9803 | 2610729.7876 | 1267030.5737
27 | 2610720.0898 | 1267036.6362 | 2610727.5376 | 1267031.9803
28 | 2610735.1108 | 1267027.2459 | 2610729.7876 | 1267030.5737
29 | 2610720.0898 | 1267036.6362 | 2610717.5397 | 1267038.2303
30 | 2610709.2444 | 1267043.416 | 2610717.5397 | 1267038.2303
31 | 2610704.3441 | 1267046.4794 | 2610709.2444 | 1267043.416
32 | 2610704.3441 | 1267046.4794 | 2610701.7208 | 1267048.155
33 | 2610704.3441 | 1267046.4794 | 2610703.5104 | 1267045.5217 | 2610692.3246 | 1267033.9308
34 | 2610689.5588 | 1267055.923 | 2610689.3953 | 1267056.0275
35 | 2610676.8091 | 1267064.0664 | 2610689.3953 | 1267056.0275
36 | 2610689.6788 | 1267055.8464 | 2610689.5588 | 1267055.923
37 | 2610666.1642 | 1267070.8656 | 2610676.8091 | 1267064.0664
38 | 2610689.6788 | 1267055.8464 | 2610695.7298 | 1267051.9815
39 | 2610666.1642 | 1267070.8656 | 2610655.7538 | 1267077.5148
40 | 2610701.7208 | 1267048.155 | 2610695.7298 | 1267051.9815
41 | 2610655.7538 | 1267077.5148 | 2610649.3918 | 1267081.5783
42 | 2610712.2104 | 1267166.1827 | 2610715.2086 | 1267163.8525
43 | 2610719.391 | 1267160.6018 | 2610715.2086 | 1267163.8525
44 | 2610727.7998 | 1267154.0662 | 2610719.391 | 1267160.6018
45 | 2610692.3246 | 1267033.9308 | 2610690.7483 | 1267032.2975

## bus_geodata
| x | y | coords
0 | 2610606.3314 | 1266976.4183
1 | 2610621.7218 | 1266960.7714
2 | 2610632.4326 | 1266971.87
3 | 2610648.4144 | 1266988.4306
4 | 2610611.331 | 1267105.8875
5 | 2610608.4751 | 1267120.2703
6 | 2610643.5488 | 1267085.3104
7 | 2610637.0505 | 1267156.7615
8 | 2610669.0905 | 1267199.7009
9 | 2610650.5839 | 1267174.9079
10 | 2610682.5481 | 1267189.2371
11 | 2610652.7861 | 1266992.9606
12 | 2610744.5039 | 1267021.374
13 | 2610735.127 | 1267027.2358
14 | 2610648.8759 | 1267081.9078
15 | 2610703.5009 | 1267172.952
16 | 2610669.291 | 1267010.0632
17 | 2610671.1162 | 1267011.9545
18 | 2610664.9259 | 1267005.54
19 | 2610677.6262 | 1267018.7002
20 | 2610661.389 | 1267001.875
21 | 2610678.7779 | 1267019.8936
22 | 2610659.6988 | 1267000.1236
23 | 2610686.0133 | 1267027.391
24 | 2610654.9905 | 1266995.2448
25 | 2610727.5376 | 1267031.9803
26 | 2610729.7876 | 1267030.5737
27 | 2610720.0898 | 1267036.6362
28 | 2610735.1108 | 1267027.2459
29 | 2610717.5397 | 1267038.2303
30 | 2610709.2444 | 1267043.416
31 | 2610704.3441 | 1267046.4794
32 | 2610689.3953 | 1267056.0275
33 | 2610689.5588 | 1267055.923
34 | 2610676.8091 | 1267064.0664
35 | 2610689.6788 | 1267055.8464
36 | 2610666.1642 | 1267070.8656
37 | 2610695.7298 | 1267051.9815
38 | 2610655.7538 | 1267077.5148
39 | 2610701.7208 | 1267048.155
40 | 2610649.3918 | 1267081.5783
41 | 2610715.2086 | 1267163.8525
42 | 2610712.2104 | 1267166.1827
43 | 2610719.391 | 1267160.6018
44 | 2610727.7998 | 1267154.0662
45 | 2610692.3246 | 1267033.9308
46 | 2610690.7483 | 1267032.2975
47 | 2610704.3441 | 1267046.4794

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99199 | -0.15417 | 0.013982 | 0.0035043
1 | 0.99227 | -0.14873 | 0 | 0
2 | 0.99247 | -0.14491 | 0.0046274 | 0.0011597
3 | 0.99286 | -0.13734 | 0.0071245 | 0.0017856
4 | 0.99249 | -0.14275 | 0 | 0
5 | 0.99056 | -0.17977 | 0 | 0
6 | 0.99658 | -0.064803 | 0.0065801 | 0.0016491
7 | 0.9856 | -0.27555 | 0.025047 | 0.0062775
8 | 0.98176 | -0.35026 | 0 | 0
9 | 0.9837 | -0.31245 | 0.022937 | 0.0057486
10 | 0.98069 | -0.37116 | 0.013452 | 0.0033715
11 | 0.99301 | -0.13447 | 0.0044922 | 0.0011259
12 | 0.99547 | -0.087016 | 0.0073562 | 0.0018436
13 | 0.99555 | -0.085585 | 0.015664 | 0.0039256
14 | 0.9973 | -0.051247 | 0.009856 | 0.0024701
15 | 0.97936 | -0.39729 | 0.012214 | 0.0030611
16 | 0.99388 | -0.11759 | 0.0067897 | 0.0017017
17 | 0.99401 | -0.11508 | 0.0044174 | 0.0011071
18 | 0.99361 | -0.12284 | 0.0031224 | 0.00078254
19 | 0.99452 | -0.1054 | 0.0042648 | 0.0010689
20 | 0.99341 | -0.12681 | 0.0052892 | 0.0013256
21 | 0.99461 | -0.10356 | 0.0067114 | 0.001682
22 | 0.99332 | -0.12849 | 0.0031098 | 0.00077938
23 | 0.99527 | -0.090811 | 0.003688 | 0.0009243
24 | 0.9931 | -0.13278 | 0.0055846 | 0.0013996
25 | 0.99581 | -0.080435 | 0.0064957 | 0.001628
26 | 0.99571 | -0.08245 | 0.014865 | 0.0037254
27 | 0.99621 | -0.072766 | 0.0047701 | 0.0011955
28 | 0.99555 | -0.085578 | 0.0053156 | 0.0013322
29 | 0.99636 | -0.06989 | 0.0086761 | 0.0021744
30 | 0.99692 | -0.059051 | 0.0095628 | 0.0023967
31 | 0.9973 | -0.051685 | 0 | 0
32 | 0.99867 | -0.025546 | 0.016096 | 0.004034
33 | 0.99865 | -0.025851 | 0.0032113 | 0.00080482
34 | 1 | 0 | -0.35221 | -0.088979
35 | 0.99864 | -0.026071 | 0.0047235 | 0.0011838
36 | 0.99912 | -0.016708 | 0.011094 | 0.0027804
37 | 0.99808 | -0.036868 | 0.0049436 | 0.001239
38 | 0.99832 | -0.031878 | 0.0047099 | 0.0011804
39 | 0.99753 | -0.047262 | 0.0048398 | 0.001213
40 | 0.99737 | -0.04983 | 0.0037054 | 0.00092866
41 | 0.97879 | -0.4084 | 0.030314 | 0.0075973
42 | 0.97893 | -0.40572 | 0.0032387 | 0.0008117
43 | 0.97875 | -0.40922 | 0.0032411 | 0.0008123
44 | 0.9787 | -0.41024 | 0.0052559 | 0.0013172
45 | 0.99589 | -0.078978 | 0.012959 | 0.0032479
46 | 0.99573 | -0.082032 | 0.0033305 | 0.0008347
47 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.013982 | -0.0035043 | 0.013986 | 0.0035064 | 3.6206e-06 | 2.0337e-06 | 0.020974 | 0.020974 | 0.020974 | 0.99199 | -0.15417 | 0.99227 | -0.14873 | 5.7621
1 | -0.013986 | -0.0035064 | 0.013989 | 0.0035078 | 2.5444e-06 | 1.4292e-06 | 0.020974 | 0.020974 | 0.020974 | 0.99227 | -0.14873 | 0.99247 | -0.14491 | 5.7621
2 | -0.018616 | -0.0046675 | 0.018623 | 0.0046715 | 6.7237e-06 | 4.0056e-06 | 0.027912 | 0.027912 | 0.027912 | 0.99247 | -0.14491 | 0.99286 | -0.13734 | 7.6681
3 | -0.025747 | -0.0064571 | 0.025751 | 0.0064593 | 3.5155e-06 | 2.1685e-06 | 0.038589 | 0.038589 | 0.038589 | 0.99286 | -0.13734 | 0.99301 | -0.13447 | 10.6014
4 | 0.11688 | 0.029753 | -0.11668 | -0.02962 | 0.00020824 | 0.00013304 | 0.17541 | 0.17541 | 0.17541 | 0.99249 | -0.14275 | 0.99056 | -0.17977 | 48.1884
5 | -0.11688 | -0.029753 | 0.11733 | 0.030035 | 0.00044107 | 0.00028179 | 0.17541 | 0.17541 | 0.17541 | 0.99249 | -0.14275 | 0.99658 | -0.064803 | 48.1884
6 | 0.11668 | 0.02962 | -0.11614 | -0.029278 | 0.000535 | 0.00034181 | 0.17541 | 0.17541 | 0.17541 | 0.99056 | -0.17977 | 0.9856 | -0.27555 | 48.1885
7 | -0.12391 | -0.031684 | 0.12399 | 0.031736 | 8.1329e-05 | 5.1968e-05 | 0.18523 | 0.18523 | 0.18523 | 0.99658 | -0.064803 | 0.9973 | -0.051247 | 50.8874
8 | 0.091094 | 0.023001 | -0.090933 | -0.022898 | 0.00016071 | 0.00010256 | 0.13759 | 0.13759 | 0.13759 | 0.9856 | -0.27555 | 0.9837 | -0.31245 | 37.7996
9 | -0.067873 | -0.017071 | 0.067996 | 0.017149 | 0.00012283 | 7.8221e-05 | 0.10289 | 0.10289 | 0.10289 | 0.98176 | -0.35026 | 0.9837 | -0.31245 | 28.2677
10 | 0.067873 | 0.017071 | -0.067806 | -0.017028 | 6.768e-05 | 4.31e-05 | 0.10289 | 0.10289 | 0.10289 | 0.98176 | -0.35026 | 0.98069 | -0.37116 | 28.2677
11 | 0.054353 | 0.013657 | -0.054286 | -0.013614 | 6.7705e-05 | 4.2997e-05 | 0.082483 | 0.082483 | 0.082483 | 0.98069 | -0.37116 | 0.97936 | -0.39729 | 22.6603
12 | -0.030243 | -0.0075851 | 0.030245 | 0.0075866 | 2.4451e-06 | 1.5238e-06 | 0.045321 | 0.045321 | 0.045321 | 0.99301 | -0.13447 | 0.9931 | -0.13278 | 12.4507
13 | -0.0073562 | -0.0018436 | 0.0073567 | 0.0018438 | 5.014e-07 | 1.7712e-07 | 0.010996 | 0.010996 | 0.010996 | 0.99547 | -0.087016 | 0.99555 | -0.085585 | 3.0209
14 | -0.02302 | -0.0057695 | 0.02302 | 0.0057695 | 8.4675e-09 | 5.1731e-09 | 0.034408 | 0.034408 | 0.034408 | 0.99555 | -0.085585 | 0.99555 | -0.085578 | 9.4527
15 | -0.13384 | -0.034206 | 0.13385 | 0.034212 | 9.1758e-06 | 5.8645e-06 | 0.19994 | 0.19994 | 0.19994 | 0.9973 | -0.051247 | 0.99737 | -0.04983 | 54.9274
16 | 0.042072 | 0.010553 | -0.042055 | -0.010542 | 1.6904e-05 | 1.068e-05 | 0.063926 | 0.063926 | 0.063926 | 0.97936 | -0.39729 | 0.97893 | -0.40572 | 17.5621
17 | -0.054172 | -0.013595 | 0.054178 | 0.013599 | 6.4845e-06 | 4.116e-06 | 0.081111 | 0.081111 | 0.081111 | 0.99388 | -0.11759 | 0.99401 | -0.11508 | 22.2832
18 | 0.047382 | 0.011893 | -0.04737 | -0.011886 | 1.1865e-05 | 7.5119e-06 | 0.070946 | 0.070946 | 0.070946 | 0.99388 | -0.11759 | 0.99361 | -0.12284 | 19.4905
19 | -0.058596 | -0.014706 | 0.058623 | 0.014723 | 2.7053e-05 | 1.7192e-05 | 0.087724 | 0.087724 | 0.087724 | 0.99401 | -0.11508 | 0.99452 | -0.1054 | 24.0999
20 | 0.044248 | 0.011103 | -0.044239 | -0.011098 | 8.388e-06 | 5.3024e-06 | 0.06627 | 0.06627 | 0.06627 | 0.99361 | -0.12284 | 0.99341 | -0.12681 | 18.2059
21 | -0.062888 | -0.015792 | 0.062893 | 0.015796 | 5.5079e-06 | 3.5035e-06 | 0.094105 | 0.094105 | 0.094105 | 0.99452 | -0.1054 | 0.99461 | -0.10356 | 25.8529
22 | 0.03895 | 0.0097722 | -0.038947 | -0.0097703 | 3.1073e-06 | 1.9572e-06 | 0.058347 | 0.058347 | 0.058347 | 0.99341 | -0.12681 | 0.99332 | -0.12849 | 16.0294
23 | -0.069604 | -0.017478 | 0.069647 | 0.017505 | 4.2379e-05 | 2.6987e-05 | 0.10415 | 0.10415 | 0.10415 | 0.99461 | -0.10356 | 0.99527 | -0.090811 | 28.6114
24 | 0.035837 | 0.0089909 | -0.03583 | -0.0089863 | 7.3288e-06 | 4.6027e-06 | 0.053688 | 0.053688 | 0.053688 | 0.99332 | -0.12849 | 0.9931 | -0.13278 | 14.7496
25 | -0.073335 | -0.018429 | 0.073366 | 0.018449 | 3.0748e-05 | 1.959e-05 | 0.10966 | 0.10966 | 0.10966 | 0.99527 | -0.090811 | 0.99573 | -0.082032 | 30.1262
26 | 0.043209 | 0.010832 | -0.043205 | -0.01083 | 4.1482e-06 | 2.6203e-06 | 0.064567 | 0.064567 | 0.064567 | 0.99581 | -0.080435 | 0.99571 | -0.08245 | 17.7382
27 | -0.049705 | -0.01246 | 0.049723 | 0.012472 | 1.817e-05 | 1.1515e-05 | 0.074273 | 0.074273 | 0.074273 | 0.99581 | -0.080435 | 0.99621 | -0.072766 | 20.4047
28 | 0.02834 | 0.0071043 | -0.028336 | -0.0071017 | 4.2229e-06 | 2.621e-06 | 0.042353 | 0.042353 | 0.042353 | 0.99571 | -0.08245 | 0.99555 | -0.085578 | 11.6354
29 | -0.054493 | -0.013667 | 0.0545 | 0.013672 | 7.472e-06 | 4.7429e-06 | 0.081398 | 0.081398 | 0.081398 | 0.99621 | -0.072766 | 0.99636 | -0.06989 | 22.3622
30 | -0.063176 | -0.015847 | 0.063209 | 0.015867 | 3.2661e-05 | 2.0776e-05 | 0.094356 | 0.094355 | 0.094356 | 0.99636 | -0.06989 | 0.99692 | -0.059051 | 25.9218
31 | -0.072772 | -0.018264 | 0.072797 | 0.01828 | 2.5573e-05 | 1.6291e-05 | 0.10863 | 0.10863 | 0.10863 | 0.99692 | -0.059051 | 0.9973 | -0.051685 | 29.8431
32 | -0.16258 | -0.040893 | 0.16262 | 0.040915 | 3.4359e-05 | 2.1908e-05 | 0.24263 | 0.24263 | 0.24263 | 0.9973 | -0.051685 | 0.99753 | -0.047262 | 33.3281
33 | 0.089783 | 0.022613 | -0.089666 | -0.022538 | 0.00011701 | 7.4662e-05 | 0.134 | 0.134 | 0.134 | 0.9973 | -0.051685 | 0.99589 | -0.078978 | 36.813
34 | 0.18051 | 0.045468 | -0.18051 | -0.045467 | 2.6341e-06 | 1.6807e-06 | 0.26904 | 0.26904 | 0.26904 | 0.99867 | -0.025546 | 0.99865 | -0.025851 | 36.9562
35 | -0.19661 | -0.049502 | 0.19685 | 0.049656 | 0.00024043 | 0.00015349 | 0.29302 | 0.29302 | 0.29302 | 0.99867 | -0.025546 | 1 | 0 | 40.2506
36 | 0.1773 | 0.044662 | -0.17729 | -0.044661 | 1.8635e-06 | 1.1889e-06 | 0.26426 | 0.26426 | 0.26426 | 0.99865 | -0.025851 | 0.99864 | -0.026071 | 36.2989
37 | 0.15371 | 0.039323 | -0.15359 | -0.039244 | 0.0001242 | 7.9159e-05 | 0.22901 | 0.22901 | 0.22901 | 1 | 0 | 0.99912 | -0.016708 | 31.4568
38 | 0.17257 | 0.043477 | -0.17248 | -0.04342 | 8.9069e-05 | 5.6816e-05 | 0.25722 | 0.25722 | 0.25722 | 0.99864 | -0.026071 | 0.99808 | -0.036868 | 35.3322
39 | 0.14249 | 0.036464 | -0.14239 | -0.036397 | 0.00010457 | 6.6603e-05 | 0.21248 | 0.21248 | 0.21248 | 0.99912 | -0.016708 | 0.99832 | -0.031878 | 29.1874
40 | 0.16754 | 0.042181 | -0.16745 | -0.042128 | 8.3204e-05 | 5.3065e-05 | 0.24985 | 0.24985 | 0.24985 | 0.99808 | -0.036868 | 0.99753 | -0.047262 | 34.3198
41 | 0.13768 | 0.035217 | -0.13756 | -0.03514 | 0.00011951 | 7.6385e-05 | 0.20546 | 0.20546 | 0.20546 | 0.99832 | -0.031878 | 0.99737 | -0.04983 | 56.4461
42 | -0.038811 | -0.009727 | 0.038816 | 0.0097301 | 4.9574e-06 | 3.125e-06 | 0.059003 | 0.059003 | 0.059003 | 0.97879 | -0.4084 | 0.97893 | -0.40572 | 16.2096
43 | 0.0084975 | 0.0021297 | -0.0084972 | -0.0021296 | 3.3151e-07 | 1.4559e-07 | 0.012918 | 0.012918 | 0.012918 | 0.97879 | -0.4084 | 0.97875 | -0.40922 | 3.549
44 | 0.0052561 | 0.0013173 | -0.0052559 | -0.0013172 | 2.5502e-07 | 2.9377e-08 | 0.007991 | 0.007991 | 0.007991 | 0.97875 | -0.40922 | 0.9787 | -0.41024 | 2.1953
45 | 0.076707 | 0.01929 | -0.076696 | -0.019283 | 1.1186e-05 | 7.1295e-06 | 0.11464 | 0.11464 | 0.11464 | 0.99589 | -0.078978 | 0.99573 | -0.082032 | 31.4935

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36249 | 0.091558

## res_load
| p_mw | q_mvar
0 | 0.013982 | 0.0035043
1 | 0.0046274 | 0.0011597
2 | 0.0071245 | 0.0017856
3 | 0.0065801 | 0.0016491
4 | 0.025047 | 0.0062775
5 | 0.022937 | 0.0057486
6 | 0.013452 | 0.0033715
7 | 0.0044922 | 0.0011259
8 | 0.0073562 | 0.0018436
9 | 0.015664 | 0.0039256
10 | 0.009856 | 0.0024701
11 | 0.012214 | 0.0030611
12 | 0.0067897 | 0.0017017
13 | 0.0044174 | 0.0011071
14 | 0.0031224 | 0.00078254
15 | 0.0042648 | 0.0010689
16 | 0.0052892 | 0.0013256
17 | 0.0067114 | 0.001682
18 | 0.0031098 | 0.00077938
19 | 0.003688 | 0.0009243
20 | 0.0055846 | 0.0013996
21 | 0.0064957 | 0.001628
22 | 0.014865 | 0.0037254
23 | 0.0047701 | 0.0011955
24 | 0.0053156 | 0.0013322
25 | 0.0086761 | 0.0021744
26 | 0.0095628 | 0.0023967
27 | 0.016096 | 0.004034
28 | 0.0032113 | 0.00080482
29 | 0.010289 | 0.0025787
30 | 0.0047235 | 0.0011838
31 | 0.011094 | 0.0027804
32 | 0.0049436 | 0.001239
33 | 0.0047099 | 0.0011804
34 | 0.0048398 | 0.001213
35 | 0.0037054 | 0.00092866
36 | 0.030314 | 0.0075973
37 | 0.0032387 | 0.0008117
38 | 0.0032411 | 0.0008123
39 | 0.0052559 | 0.0013172
40 | 0.012959 | 0.0032479
41 | 0.0033305 | 0.0008347

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1