## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-176_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-176_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-176_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-176_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2701-176_0_4_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_2701-176_0_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_2701-176_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2701-176_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2701-176_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_2701-176_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2701-176_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_2701-176_0_4_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_2701-176_0_4_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_2701-176_0_4_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_2701-176_0_4_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_2701-176_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2701-176_0_4_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_2701-176_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2701-176_0_4_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_2701-176_0_4_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_2701-176_0_4_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_2701-176_0_4_node_42 | 0.4 | n |  | TRUE
22 | bus_LV_2701-176_0_4_node_31 | 0.4 | n |  | TRUE
23 | bus_LV_2701-176_0_4_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_2701-176_0_4_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_2701-176_0_4_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_2701-176_0_4_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_2701-176_0_4_node_145 | 0.4 | n |  | TRUE
28 | bus_LV_2701-176_0_4_node_83 | 0.4 | n |  | TRUE
29 | bus_LV_2701-176_0_4_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_2701-176_0_4_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_2701-176_0_4_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_2701-176_0_4_node_117 | 0.4 | n |  | TRUE
33 | bus_LV_2701-176_0_4_node_107 | 0.4 | n |  | TRUE
34 | bus_LV_2701-176_0_4_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_2701-176_0_4_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2701-176_0_4_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_2701-176_0_4_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_2701-176_0_4_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_2701-176_0_4_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_2701-176_0_4_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_2701-176_0_4_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_2701-176_0_4_node_65 | 0.4 | n |  | TRUE
43 | bus_LV_2701-176_0_4_node_82 | 0.4 | n |  | TRUE
44 | bus_LV_2701-176_0_4_node_24 | 0.4 | n |  | TRUE
45 | bus_LV_2701-176_0_4_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_2701-176_0_4_node_112 | 0.4 | n |  | TRUE
47 | bus_LV_2701-176_0_4_node_128 | 0.4 | n |  | TRUE
48 | bus_LV_2701-176_0_4_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_2701-176_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_2701-176_0_4_node_119 | 0.4 | n |  | TRUE
51 | bus_LV_2701-176_0_4_node_115 | 0.4 | n |  | TRUE
52 | bus_LV_2701-176_0_4_node_58 | 0.4 | n |  | TRUE
53 | bus_LV_2701-176_0_4_node_57 | 0.4 | n |  | TRUE
54 | bus_LV_2701-176_0_4_node_105 | 0.4 | n |  | TRUE
55 | bus_LV_2701-176_0_4_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_2701-176_0_4_node_108 | 0.4 | n |  | TRUE
57 | bus_LV_2701-176_0_4_node_126 | 0.4 | n |  | TRUE
58 | bus_LV_2701-176_0_4_node_44 | 0.4 | n |  | TRUE
59 | bus_LV_2701-176_0_4_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_2701-176_0_4_node_46 | 0.4 | n |  | TRUE
61 | bus_LV_2701-176_0_4_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_2701-176_0_4_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_2701-176_0_4_node_68 | 0.4 | n |  | TRUE
64 | bus_LV_2701-176_0_4_node_66 | 0.4 | n |  | TRUE
65 | bus_LV_2701-176_0_4_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_2701-176_0_4_node_93 | 0.4 | n |  | TRUE
67 | bus_LV_2701-176_0_4_node_109 | 0.4 | n |  | TRUE
68 | bus_LV_2701-176_0_4_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_2701-176_0_4_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_2701-176_0_4_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_2701-176_0_4_node_50 | 0.4 | n |  | TRUE
72 | bus_LV_2701-176_0_4_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_2701-176_0_4_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_2701-176_0_4_node_53 | 0.4 | n |  | TRUE
75 | bus_LV_2701-176_0_4_node_54 | 0.4 | n |  | TRUE
76 | bus_LV_2701-176_0_4_node_94 | 0.4 | n |  | TRUE
77 | bus_LV_2701-176_0_4_node_95 | 0.4 | n |  | TRUE
78 | bus_LV_2701-176_0_4_node_91 | 0.4 | n |  | TRUE
79 | bus_LV_2701-176_0_4_node_116 | 0.4 | n |  | TRUE
80 | bus_LV_2701-176_0_4_node_137 | 0.4 | n |  | TRUE
81 | bus_LV_2701-176_0_4_node_59 | 0.4 | n |  | TRUE
82 | bus_LV_2701-176_0_4_node_60 | 0.4 | n |  | TRUE
83 | bus_LV_2701-176_0_4_node_61 | 0.4 | n |  | TRUE
84 | bus_LV_2701-176_0_4_node_62 | 0.4 | n |  | TRUE
85 | bus_LV_2701-176_0_4_node_64 | 0.4 | n |  | TRUE
86 | bus_LV_2701-176_0_4_node_74 | 0.4 | n |  | TRUE
87 | bus_LV_2701-176_0_4_node_63 | 0.4 | n |  | TRUE
88 | bus_LV_2701-176_0_4_node_84 | 0.4 | n |  | TRUE
89 | bus_LV_2701-176_0_4_node_75 | 0.4 | n |  | TRUE
90 | bus_LV_2701-176_0_4_node_81 | 0.4 | n |  | TRUE
91 | bus_LV_2701-176_0_4_node_92 | 0.4 | n |  | TRUE
92 | bus_LV_2701-176_0_4_node_110 | 0.4 | n |  | TRUE
93 | bus_LV_2701-176_0_4_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_2701-176_0_4_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_2701-176_0_4_node_71 | 0.4 | n |  | TRUE
96 | bus_LV_2701-176_0_4_node_72 | 0.4 | n |  | TRUE
97 | bus_LV_2701-176_0_4_node_73 | 0.4 | n |  | TRUE
98 | bus_LV_2701-176_0_4_node_80 | 0.4 | n |  | TRUE
99 | bus_LV_2701-176_0_4_node_77 | 0.4 | n |  | TRUE
100 | bus_LV_2701-176_0_4_node_78 | 0.4 | n |  | TRUE
101 | bus_LV_2701-176_0_4_node_76 | 0.4 | n |  | TRUE
102 | bus_LV_2701-176_0_4_node_79 | 0.4 | n |  | TRUE
103 | bus_LV_2701-176_0_4_node_120 | 0.4 | n |  | TRUE
104 | bus_LV_2701-176_0_4_node_113 | 0.4 | n |  | TRUE
105 | bus_LV_2701-176_0_4_node_86 | 0.4 | n |  | TRUE
106 | bus_LV_2701-176_0_4_node_87 | 0.4 | n |  | TRUE
107 | bus_LV_2701-176_0_4_node_88 | 0.4 | n |  | TRUE
108 | bus_LV_2701-176_0_4_node_89 | 0.4 | n |  | TRUE
109 | bus_LV_2701-176_0_4_node_90 | 0.4 | n |  | TRUE
110 | bus_LV_2701-176_0_4_node_125 | 0.4 | n |  | TRUE
111 | bus_LV_2701-176_0_4_node_139 | 0.4 | n |  | TRUE
112 | bus_LV_2701-176_0_4_node_123 | 0.4 | n |  | TRUE
113 | bus_LV_2701-176_0_4_node_138 | 0.4 | n |  | TRUE
114 | bus_LV_2701-176_0_4_node_114 | 0.4 | n |  | TRUE
115 | bus_LV_2701-176_0_4_node_136 | 0.4 | n |  | TRUE
116 | bus_LV_2701-176_0_4_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_2701-176_0_4_node_97 | 0.4 | n |  | TRUE
118 | bus_LV_2701-176_0_4_node_98 | 0.4 | n |  | TRUE
119 | bus_LV_2701-176_0_4_node_99 | 0.4 | n |  | TRUE
120 | bus_LV_2701-176_0_4_node_100 | 0.4 | n |  | TRUE
121 | bus_LV_2701-176_0_4_node_118 | 0.4 | n |  | TRUE
122 | bus_LV_2701-176_0_4_node_102 | 0.4 | n |  | TRUE
123 | bus_LV_2701-176_0_4_node_144 | 0.4 | n |  | TRUE
124 | bus_LV_2701-176_0_4_node_101 | 0.4 | n |  | TRUE
125 | bus_LV_2701-176_0_4_node_103 | 0.4 | n |  | TRUE
126 | bus_LV_2701-176_0_4_node_104 | 0.4 | n |  | TRUE
127 | bus_LV_2701-176_0_4_node_106 | 0.4 | n |  | TRUE
128 | bus_LV_2701-176_0_4_node_111 | 0.4 | n |  | TRUE
129 | bus_LV_2701-176_0_4_node_142 | 0.4 | n |  | TRUE
130 | bus_LV_2701-176_0_4_node_121 | 0.4 | n |  | TRUE
131 | bus_LV_2701-176_0_4_node_122 | 0.4 | n |  | TRUE
132 | bus_LV_2701-176_0_4_node_124 | 0.4 | n |  | TRUE
133 | bus_LV_2701-176_0_4_node_135 | 0.4 | n |  | TRUE
134 | bus_LV_2701-176_0_4_node_127 | 0.4 | n |  | TRUE
135 | bus_LV_2701-176_0_4_node_129 | 0.4 | n |  | TRUE
136 | bus_LV_2701-176_0_4_node_130 | 0.4 | n |  | TRUE
137 | bus_LV_2701-176_0_4_node_131 | 0.4 | n |  | TRUE
138 | bus_LV_2701-176_0_4_node_132 | 0.4 | n |  | TRUE
139 | bus_LV_2701-176_0_4_node_133 | 0.4 | n |  | TRUE
140 | bus_LV_2701-176_0_4_node_134 | 0.4 | n |  | TRUE
141 | bus_LV_2701-176_0_4_node_143 | 0.4 | n |  | TRUE
142 | bus_MV_566_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-176_0_4_load_0 | 0 | 0.010158 | 0.0025459 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-176_0_4_load_1 | 1 | 0.0079375 | 0.0019893 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-176_0_4_load_2 | 2 | 0.0082057 | 0.0020565 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-176_0_4_load_4 | 3 | 0.0040249 | 0.0010087 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-176_0_4_load_10 | 4 | 0.0091645 | 0.0022968 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-176_0_4_load_5 | 6 | 0.0035952 | 0.00090104 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-176_0_4_load_6 | 7 | 0.0035019 | 0.00087766 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-176_0_4_load_7 | 8 | 0.0027339 | 0.00068517 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-176_0_4_load_8 | 9 | 0.0089042 | 0.0022316 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-176_0_4_load_9 | 10 | 0.0036025 | 0.00090287 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-176_0_4_load_15 | 11 | 0.0026518 | 0.00066461 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-176_0_4_load_26 | 12 | 0.0027928 | 0.00069995 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-176_0_4_load_14 | 13 | 0.0089102 | 0.0022331 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-176_0_4_load_25 | 14 | 0.0036058 | 0.00090371 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-176_0_4_load_12 | 15 | 0.0091909 | 0.0023035 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-176_0_4_load_22 | 16 | 0.0071766 | 0.0017986 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-176_0_4_load_30 | 18 | 0.0045972 | 0.0011522 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-176_0_4_load_27 | 19 | 0.0014686 | 0.00036807 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-176_0_4_load_23 | 20 | 0.0033027 | 0.00082774 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-176_0_4_load_42 | 21 | 0.0046169 | 0.0011571 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-176_0_4_load_38 | 24 | 0.0044052 | 0.0011041 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-176_0_4_load_145 | 27 | 0.013609 | 0.0034107 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-176_0_4_load_37 | 29 | 0.0050246 | 0.0012593 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-176_0_4_load_28 | 30 | 0.0014712 | 0.00036872 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-176_0_4_load_117 | 32 | 0.0025075 | 0.00062843 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-176_0_4_load_107 | 33 | 0.0018881 | 0.00047321 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-176_0_4_load_17 | 35 | 0.00892 | 0.0022356 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-176_0_4_load_18 | 36 | 0.0064242 | 0.0016101 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-176_0_4_load_19 | 37 | 0.0056864 | 0.0014251 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-176_0_4_load_43 | 38 | 0.0047466 | 0.0011896 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-176_0_4_load_20 | 39 | 0.0063295 | 0.0015863 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-176_0_4_load_40 | 40 | 0.0021855 | 0.00054773 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-176_0_4_load_21 | 41 | 0.0041088 | 0.0010298 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-176_0_4_load_65 | 42 | 0.0024369 | 0.00061075 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-176_0_4_load_82 | 43 | 0.0014908 | 0.00037364 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-176_0_4_load_24 | 44 | 0.0036711 | 0.00092006 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-176_0_4_load_112 | 46 | 0.0053934 | 0.0013517 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-176_0_4_load_128 | 47 | 0.0050959 | 0.0012771 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-176_0_4_load_36 | 48 | 0.0025407 | 0.00063676 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-176_0_4_load_39 | 49 | 0.0063119 | 0.0015819 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-176_0_4_load_119 | 50 | 0.00098801 | 0.00024762 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2701-176_0_4_load_115 | 51 | 0.0044847 | 0.001124 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2701-176_0_4_load_58 | 52 | 0.0051432 | 0.001289 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2701-176_0_4_load_57 | 53 | 0.007226 | 0.001811 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2701-176_0_4_load_105 | 54 | 0.0018914 | 0.00047402 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2701-176_0_4_load_35 | 55 | 0.0017514 | 0.00043894 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2701-176_0_4_load_108 | 56 | 0.0018894 | 0.00047354 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2701-176_0_4_load_126 | 57 | 0.012138 | 0.0030422 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2701-176_0_4_load_44 | 58 | 0.0026912 | 0.00067447 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2701-176_0_4_load_45 | 59 | 0.0029028 | 0.00072751 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2701-176_0_4_load_46 | 60 | 0.0029321 | 0.00073486 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2701-176_0_4_load_48 | 62 | 0.0040008 | 0.0010027 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2701-176_0_4_load_66 | 64 | 0.0031995 | 0.00080187 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2701-176_0_4_load_55 | 65 | 0.0059276 | 0.0014856 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2701-176_0_4_load_93 | 66 | 0.0035464 | 0.0008888 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2701-176_0_4_load_109 | 67 | 0.0016282 | 0.00040807 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2701-176_0_4_load_67 | 68 | 0.0023232 | 0.00058225 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2701-176_0_4_load_56 | 69 | 0.0038651 | 0.00096868 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2701-176_0_4_load_49 | 70 | 0.0045108 | 0.0011305 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2701-176_0_4_load_50 | 71 | 0.0092387 | 0.0023154 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2701-176_0_4_load_52 | 73 | 0.0070666 | 0.0017711 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2701-176_0_4_load_54 | 75 | 0.0059355 | 0.0014876 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2701-176_0_4_load_94 | 76 | 0.001836 | 0.00046014 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2701-176_0_4_load_95 | 77 | 0.0018367 | 0.00046032 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2701-176_0_4_load_91 | 78 | 0.0017009 | 0.00042628 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2701-176_0_4_load_116 | 79 | 0.0022541 | 0.00056492 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2701-176_0_4_load_137 | 80 | 0.0016634 | 0.0004169 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2701-176_0_4_load_59 | 81 | 0.0063651 | 0.0015952 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2701-176_0_4_load_62 | 84 | 0.0032391 | 0.0008118 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2701-176_0_4_load_74 | 86 | 0.0050982 | 0.0012777 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2701-176_0_4_load_63 | 87 | 0.0023009 | 0.00057667 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2701-176_0_4_load_84 | 88 | 0.0018086 | 0.00045328 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2701-176_0_4_load_75 | 89 | 0.0051008 | 0.0012784 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2701-176_0_4_load_81 | 90 | 0.0024401 | 0.00061156 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2701-176_0_4_load_92 | 91 | 0.0082794 | 0.002075 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2701-176_0_4_load_110 | 92 | 0.0016743 | 0.00041963 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2701-176_0_4_load_69 | 93 | 0.0024428 | 0.00061222 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2701-176_0_4_load_70 | 94 | 0.0020836 | 0.00052221 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2701-176_0_4_load_71 | 95 | 0.0027532 | 0.00069002 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2701-176_0_4_load_72 | 96 | 0.0024426 | 0.00061217 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2701-176_0_4_load_73 | 97 | 0.0013226 | 0.00033148 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2701-176_0_4_load_80 | 98 | 0.0024412 | 0.00061181 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2701-176_0_4_load_77 | 99 | 0.0027547 | 0.00069039 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2701-176_0_4_load_78 | 100 | 0.0024692 | 0.00061884 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2701-176_0_4_load_76 | 101 | 0.0017923 | 0.0004492 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2701-176_0_4_load_79 | 102 | 0.002471 | 0.00061928 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2701-176_0_4_load_120 | 103 | 0.00097602 | 0.00024461 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2701-176_0_4_load_113 | 104 | 0.0018457 | 0.00046257 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2701-176_0_4_load_86 | 105 | 0.0012622 | 0.00031635 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2701-176_0_4_load_87 | 106 | 0.0011425 | 0.00028633 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2701-176_0_4_load_88 | 107 | 0.0012105 | 0.00030339 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2701-176_0_4_load_89 | 108 | 0.0010815 | 0.00027105 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2701-176_0_4_load_90 | 109 | 0.0011996 | 0.00030066 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2701-176_0_4_load_125 | 110 | 0.0010904 | 0.00027328 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2701-176_0_4_load_139 | 111 | 0.0010064 | 0.00025224 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2701-176_0_4_load_123 | 112 | 0.0010309 | 0.00025836 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2701-176_0_4_load_138 | 113 | 0.0011976 | 0.00030016 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2701-176_0_4_load_114 | 114 | 0.0043918 | 0.0011007 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2701-176_0_4_load_136 | 115 | 0.0018389 | 0.00046088 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2701-176_0_4_load_96 | 116 | 0.0053905 | 0.001351 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2701-176_0_4_load_97 | 117 | 0.0027053 | 0.00067801 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2701-176_0_4_load_98 | 118 | 0.0018658 | 0.00046762 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2701-176_0_4_load_99 | 119 | 0.0019062 | 0.00047774 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2701-176_0_4_load_100 | 120 | 0.0018559 | 0.00046514 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2701-176_0_4_load_118 | 121 | 0.0017668 | 0.00044279 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2701-176_0_4_load_102 | 122 | 0.0043849 | 0.001099 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2701-176_0_4_load_101 | 124 | 0.0033628 | 0.00084281 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2701-176_0_4_load_103 | 125 | 0.0013725 | 0.00034398 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2701-176_0_4_load_104 | 126 | 0.0011568 | 0.00028993 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2701-176_0_4_load_106 | 127 | 0.0018927 | 0.00047435 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2701-176_0_4_load_111 | 128 | 0.0016589 | 0.00041576 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2701-176_0_4_load_142 | 129 | 0.001621 | 0.00040627 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2701-176_0_4_load_121 | 130 | 0.0018381 | 0.00046067 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2701-176_0_4_load_122 | 131 | 0.0016629 | 0.00041677 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2701-176_0_4_load_124 | 132 | 0.0018383 | 0.00046072 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2701-176_0_4_load_135 | 133 | 0.0016618 | 0.00041648 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2701-176_0_4_load_127 | 134 | 0.012152 | 0.0030456 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2701-176_0_4_load_129 | 135 | 0.012459 | 0.0031226 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2701-176_0_4_load_130 | 136 | 0.0010389 | 0.00026037 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2701-176_0_4_load_131 | 137 | 0.00099961 | 0.00025053 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2701-176_0_4_load_132 | 138 | 0.001125 | 0.00028196 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2701-176_0_4_load_133 | 139 | 0.00099941 | 0.00025048 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2701-176_0_4_load_143 | 141 | 0.0011913 | 0.00029857 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-176_0_4_line_0 |  | 0 | 1 | 0.0031947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-176_0_4_line_1 |  | 0 | 2 | 0.010888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-176_0_4_line_2 |  | 2 | 3 | 0.0035615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-176_0_4_line_3 |  | 3 | 4 | 0.0095803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-176_0_4_line_4 |  | 4 | 5 | 0.0082672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-176_0_4_line_5 |  | 5 | 15 | 0.0056175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-176_0_4_line_6 |  | 6 | 7 | 0.010799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-176_0_4_line_7 |  | 6 | 8 | 0.0020417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-176_0_4_line_8 |  | 7 | 9 | 0.0032824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-176_0_4_line_9 |  | 8 | 10 | 0.0058623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-176_0_4_line_10 |  | 9 | 11 | 0.014463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-176_0_4_line_11 |  | 10 | 12 | 0.0055928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-176_0_4_line_12 |  | 11 | 13 | 0.0056106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-176_0_4_line_13 |  | 12 | 14 | 0.002506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-176_0_4_line_14 |  | 13 | 34 | 0.0078138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-176_0_4_line_15 |  | 14 | 44 | 0.0079415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-176_0_4_line_16 |  | 15 | 16 | 0.012828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-176_0_4_line_17 |  | 16 | 20 | 0.0082463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-176_0_4_line_18 |  | 17 | 18 | 0.0040552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-176_0_4_line_19 |  | 17 | 19 | 0.010164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-176_0_4_line_20 |  | 18 | 21 | 0.0072582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-176_0_4_line_21 |  | 19 | 30 | 0.0075232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-176_0_4_line_22 |  | 20 | 44 | 0.0019882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-176_0_4_line_23 |  | 22 | 23 | 0.010761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2701-176_0_4_line_24 |  | 22 | 24 | 0.02375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_2701-176_0_4_line_25 |  | 22 | 25 | 0.019692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-176_0_4_line_26 |  | 23 | 26 | 0.024243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2701-176_0_4_line_27 |  | 23 | 27 | 0.0080934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2701-176_0_4_line_28 |  | 24 | 49 | 0.014457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2701-176_0_4_line_29 |  | 25 | 29 | 0.018295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-176_0_4_line_30 |  | 25 | 30 | 0.041306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-176_0_4_line_31 |  | 26 | 28 | 0.008638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_2701-176_0_4_line_32 |  | 28 | 50 | 0.015777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-176_0_4_line_33 |  | 28 | 51 | 0.020021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-176_0_4_line_34 |  | 28 | 32 | 0.013588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-176_0_4_line_35 |  | 29 | 48 | 0.025615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-176_0_4_line_36 |  | 31 | 32 | 0.0053092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-176_0_4_line_37 |  | 31 | 33 | 0.0054871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-176_0_4_line_38 |  | 33 | 54 | 0.013386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2701-176_0_4_line_39 |  | 34 | 35 | 0.012349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2701-176_0_4_line_40 |  | 34 | 36 | 0.014936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_2701-176_0_4_line_41 |  | 35 | 37 | 0.020079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-176_0_4_line_42 |  | 36 | 38 | 0.014056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2701-176_0_4_line_43 |  | 37 | 39 | 0.0098688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-176_0_4_line_44 |  | 38 | 40 | 0.0093572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2701-176_0_4_line_45 |  | 39 | 41 | 0.011985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2701-176_0_4_line_46 |  | 40 | 49 | 0.0045765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2701-176_0_4_line_47 |  | 41 | 42 | 0.002585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2701-176_0_4_line_48 |  | 42 | 43 | 0.007365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2701-176_0_4_line_49 |  | 43 | 90 | 0.00033545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2701-176_0_4_line_50 |  | 45 | 46 | 0.014986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2701-176_0_4_line_51 |  | 45 | 47 | 0.036004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2701-176_0_4_line_52 |  | 46 | 56 | 0.01181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2701-176_0_4_line_53 |  | 47 | 57 | 0.021889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2701-176_0_4_line_54 |  | 48 | 55 | 0.010889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2701-176_0_4_line_55 |  | 50 | 103 | 0.011632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2701-176_0_4_line_56 |  | 51 | 104 | 0.014712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2701-176_0_4_line_57 |  | 52 | 53 | 0.0048958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2701-176_0_4_line_58 |  | 53 | 73 | 0.013346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2701-176_0_4_line_59 |  | 54 | 127 | 0.0092195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2701-176_0_4_line_60 |  | 56 | 127 | 0.0089821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2701-176_0_4_line_61 |  | 57 | 134 | 0.026192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2701-176_0_4_line_62 |  | 58 | 59 | 0.0079594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2701-176_0_4_line_63 |  | 58 | 60 | 0.0085878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2701-176_0_4_line_64 |  | 59 | 61 | 0.022207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2701-176_0_4_line_65 |  | 60 | 62 | 0.012854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2701-176_0_4_line_66 |  | 61 | 63 | 0.008723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2701-176_0_4_line_67 |  | 61 | 64 | 0.01589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2701-176_0_4_line_68 |  | 62 | 65 | 0.0029048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2701-176_0_4_line_69 |  | 63 | 66 | 0.013363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2701-176_0_4_line_70 |  | 63 | 67 | 0.016003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2701-176_0_4_line_71 |  | 64 | 68 | 0.023098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2701-176_0_4_line_72 |  | 65 | 69 | 0.01025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2701-176_0_4_line_73 |  | 66 | 91 | 0.017754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2701-176_0_4_line_74 |  | 67 | 92 | 0.020018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2701-176_0_4_line_75 |  | 68 | 87 | 0.012761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2701-176_0_4_line_76 |  | 69 | 75 | 0.005374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2701-176_0_4_line_77 |  | 70 | 71 | 0.011566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2701-176_0_4_line_78 |  | 70 | 72 | 0.0042244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2701-176_0_4_line_79 |  | 71 | 73 | 0.018137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2701-176_0_4_line_80 |  | 72 | 74 | 0.009298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2701-176_0_4_line_81 |  | 72 | 75 | 0.0032477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2701-176_0_4_line_82 |  | 74 | 76 | 0.014116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2701-176_0_4_line_83 |  | 74 | 77 | 0.015051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2701-176_0_4_line_84 |  | 74 | 78 | 0.013245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2701-176_0_4_line_85 |  | 76 | 79 | 0.002016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2701-176_0_4_line_86 |  | 77 | 80 | 0.0028472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2701-176_0_4_line_87 |  | 79 | 114 | 0.023004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2701-176_0_4_line_88 |  | 80 | 115 | 0.0021516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2701-176_0_4_line_89 |  | 81 | 82 | 0.014218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2701-176_0_4_line_90 |  | 81 | 83 | 0.036276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2701-176_0_4_line_91 |  | 82 | 84 | 0.012377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2701-176_0_4_line_92 |  | 83 | 85 | 0.10656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2701-176_0_4_line_93 |  | 84 | 86 | 0.0061672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2701-176_0_4_line_94 |  | 85 | 88 | 0.027848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2701-176_0_4_line_95 |  | 86 | 89 | 0.0085965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2701-176_0_4_line_96 |  | 89 | 101 | 0.0078202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2701-176_0_4_line_97 |  | 90 | 98 | 0.0085935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2701-176_0_4_line_98 |  | 92 | 128 | 0.0062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2701-176_0_4_line_99 |  | 93 | 94 | 0.00020147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2701-176_0_4_line_100 |  | 93 | 95 | 0.0089257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2701-176_0_4_line_101 |  | 94 | 96 | 0.0083952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2701-176_0_4_line_102 |  | 95 | 97 | 0.0013196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2701-176_0_4_line_103 |  | 96 | 98 | 0.0086041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2701-176_0_4_line_104 |  | 97 | 99 | 0.013067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2701-176_0_4_line_105 |  | 99 | 100 | 0.0088874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2701-176_0_4_line_106 |  | 100 | 102 | 0.0086059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2701-176_0_4_line_107 |  | 101 | 102 | 0.00077852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2701-176_0_4_line_108 |  | 103 | 126 | 0.0056105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2701-176_0_4_line_109 |  | 104 | 114 | 0.010244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2701-176_0_4_line_110 |  | 105 | 106 | 0.0049104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2701-176_0_4_line_111 |  | 105 | 107 | 0.0049488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2701-176_0_4_line_112 |  | 106 | 108 | 0.00015179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2701-176_0_4_line_113 |  | 107 | 109 | 0.0008872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2701-176_0_4_line_114 |  | 108 | 110 | 0.0048936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2701-176_0_4_line_115 |  | 109 | 111 | 0.0053663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2701-176_0_4_line_116 |  | 110 | 112 | 0.00012507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2701-176_0_4_line_117 |  | 111 | 113 | 0.0012295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2701-176_0_4_line_118 |  | 112 | 130 | 0.0048762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2701-176_0_4_line_119 |  | 113 | 139 | 0.0058032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2701-176_0_4_line_120 |  | 115 | 133 | 0.003698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2701-176_0_4_line_121 |  | 116 | 117 | 0.011901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2701-176_0_4_line_122 |  | 116 | 118 | 0.0010693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2701-176_0_4_line_123 |  | 117 | 119 | 0.0070287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2701-176_0_4_line_124 |  | 118 | 120 | 0.0066176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2701-176_0_4_line_125 |  | 119 | 121 | 0.00014347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2701-176_0_4_line_126 |  | 120 | 122 | 0.0063576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2701-176_0_4_line_127 |  | 121 | 123 | 0.022965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2701-176_0_4_line_128 |  | 122 | 124 | 0.014054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2701-176_0_4_line_129 |  | 123 | 129 | 0.010137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2701-176_0_4_line_130 |  | 124 | 125 | 0.0051115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2701-176_0_4_line_131 |  | 125 | 126 | 0.0066715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2701-176_0_4_line_132 |  | 130 | 131 | 0.00045514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2701-176_0_4_line_133 |  | 131 | 132 | 0.004546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2701-176_0_4_line_134 |  | 132 | 133 | 0.0013025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2701-176_0_4_line_135 |  | 134 | 135 | 0.026845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2701-176_0_4_line_136 |  | 136 | 137 | 0.0050974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2701-176_0_4_line_137 |  | 136 | 138 | 0.0029108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2701-176_0_4_line_138 |  | 137 | 139 | 0.005001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2701-176_0_4_line_139 |  | 138 | 140 | 0.017162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2701-176_0_4_line_140 |  | 140 | 141 | 0.016832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-176_0_4_trafo_145 | 0.63 MVA 20/0.4 kV | 142 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2608843.5969 | 1266017.929 | 2608841.7036 | 1266017.4142 | 2608840.5571 | 1266016.9613
1 | 2608843.5969 | 1266017.929 | 2608854.1035 | 1266020.7857
2 | 2608854.1035 | 1266020.7857 | 2608857.5402 | 1266021.7202
3 | 2608866.7849 | 1266024.2338 | 2608857.5402 | 1266021.7202
4 | 2608874.7625 | 1266026.4029 | 2608866.7849 | 1266024.2338
5 | 2608874.7625 | 1266026.4029 | 2608880.2485 | 1266027.6109
6 | 2608926.1555 | 1266037.7192 | 2608936.702 | 1266040.0415
7 | 2608926.1555 | 1266037.7192 | 2608924.1615 | 1266037.2802
8 | 2608936.702 | 1266040.0415 | 2608939.9076 | 1266040.7473
9 | 2608918.4363 | 1266036.0195 | 2608924.1615 | 1266037.2802
10 | 2608954.0326 | 1266043.8575 | 2608939.9076 | 1266040.7473
11 | 2608918.4363 | 1266036.0195 | 2608912.9744 | 1266034.8169
12 | 2608954.0326 | 1266043.8575 | 2608959.5119 | 1266045.064
13 | 2608912.9744 | 1266034.8169 | 2608910.527 | 1266034.278
14 | 2608967.1429 | 1266046.7443 | 2608959.5119 | 1266045.064
15 | 2608902.7713 | 1266032.5702 | 2608910.527 | 1266034.278
16 | 2608892.7763 | 1266030.3694 | 2608880.2485 | 1266027.6109
17 | 2608892.7763 | 1266030.3694 | 2608900.8297 | 1266032.1427
18 | 2608886.035 | 1266100.3155 | 2608882.5387 | 1266098.2611
19 | 2608886.035 | 1266100.3155 | 2608894.8004 | 1266105.4619
20 | 2608876.2809 | 1266094.584 | 2608882.5387 | 1266098.2611
21 | 2608894.8004 | 1266105.4619 | 2608901.288 | 1266109.271
22 | 2608900.8297 | 1266032.1427 | 2608902.7713 | 1266032.5702
23 | 2608950.4261 | 1266129.3433 | 2608945.5672 | 1266126.4673 | 2608944.8086 | 1266125.2876 | 2608941.8911 | 1266122.9593
24 | 2608941.8911 | 1266122.9593 | 2608953.6171 | 1266102.3054
25 | 2608931.6962 | 1266134.0962 | 2608936.3377 | 1266136.3492 | 2608939.0371 | 1266128.5367 | 2608939.8375 | 1266126.9257 | 2608940.6832 | 1266125.2146 | 2608941.1816 | 1266124.2036 | 2608941.8911 | 1266122.9593
26 | 2608950.4261 | 1266129.3433 | 2608949.1511 | 1266131.1871 | 2608948.4193 | 1266132.2423 | 2608958.746 | 1266138.5844 | 2608960.7366 | 1266141.4783 | 2608960.9548 | 1266146.56
27 | 2608950.4261 | 1266129.3433 | 2608957.385 | 1266133.4757
28 | 2608953.6171 | 1266102.3054 | 2608955.9687 | 1266098.1632 | 2608958.0272 | 1266088.691
29 | 2608931.6962 | 1266134.0962 | 2608930.1264 | 1266136.729 | 2608924.2191 | 1266140.1448 | 2608915.9495 | 1266141.655
30 | 2608931.6962 | 1266134.0962 | 2608931.8436 | 1266131.1833 | 2608931.0194 | 1266128.558 | 2608928.4945 | 1266125.541 | 2608921.7856 | 1266121.3058 | 2608901.288 | 1266109.271
31 | 2608960.9548 | 1266146.56 | 2608959.8804 | 1266155.131
32 | 2608959.8804 | 1266155.131 | 2608960.3996 | 1266160.3354 | 2608962.4111 | 1266170.6886
33 | 2608959.8804 | 1266155.131 | 2608979.6929 | 1266158.014
34 | 2608959.8804 | 1266155.131 | 2608946.4043 | 1266153.3918
35 | 2608915.9495 | 1266141.655 | 2608902.6598 | 1266144.0819 | 2608890.7553 | 1266146.2805
36 | 2608941.1388 | 1266152.7122 | 2608946.4043 | 1266153.3918
37 | 2608941.1388 | 1266152.7122 | 2608935.7324 | 1266151.7748
38 | 2608922.5475 | 1266150.5302 | 2608925.4841 | 1266149.998 | 2608935.7324 | 1266151.7748
39 | 2608967.1429 | 1266046.7443 | 2608979.2196 | 1266049.3219
40 | 2608967.1429 | 1266046.7443 | 2608963.9711 | 1266061.3396
41 | 2608998.856 | 1266053.513 | 2608979.2196 | 1266049.3219
42 | 2608960.9861 | 1266075.0751 | 2608963.9711 | 1266061.3396
43 | 2609008.5074 | 1266055.573 | 2608998.856 | 1266053.513
44 | 2608958.999 | 1266084.2189 | 2608960.9861 | 1266075.0751
45 | 2609008.5074 | 1266055.573 | 2609020.2281 | 1266058.0746
46 | 2608958.999 | 1266084.2189 | 2608958.0272 | 1266088.691
47 | 2609022.7561 | 1266058.6142 | 2609020.2281 | 1266058.0746
48 | 2609022.7561 | 1266058.6142 | 2609029.9589 | 1266060.1515
49 | 2609030.2869 | 1266060.2215 | 2609029.9589 | 1266060.1515
50 | 2608878.3365 | 1266158.8781 | 2608886.2363 | 1266157.1109 | 2608893.0167 | 1266155.8821
51 | 2608878.3365 | 1266158.8781 | 2608886.7035 | 1266193.8969
52 | 2608893.0167 | 1266155.8821 | 2608904.6377 | 1266153.776
53 | 2608886.7035 | 1266193.8969 | 2608891.7902 | 1266215.1866
54 | 2608880.0478 | 1266148.2581 | 2608890.7553 | 1266146.2805
55 | 2608964.6295 | 1266182.1068 | 2608962.4111 | 1266170.6886
56 | 2608994.2519 | 1266160.1325 | 2608979.6929 | 1266158.014
57 | 2608995.2869 | 1266151.3604 | 2608990.4397 | 1266150.6726
58 | 2609008.5007 | 1266153.2353 | 2608995.2869 | 1266151.3604
59 | 2608922.5475 | 1266150.5302 | 2608913.4758 | 1266152.1742
60 | 2608913.4758 | 1266152.1742 | 2608904.6377 | 1266153.776
61 | 2608891.7902 | 1266215.1866 | 2608897.8769 | 1266240.6618
62 | 2609084.8354 | 1266164.387 | 2609092.7075 | 1266165.563
63 | 2609084.8354 | 1266164.387 | 2609076.3419 | 1266163.1182
64 | 2609114.6549 | 1266168.9421 | 2609108.9424 | 1266167.9883 | 2609092.7075 | 1266165.563
65 | 2609063.6289 | 1266161.219 | 2609076.3419 | 1266163.1182
66 | 2609114.6549 | 1266168.9421 | 2609114.7126 | 1266170.5322 | 2609115.7859 | 1266177.5832
67 | 2609114.6549 | 1266168.9421 | 2609114.7929 | 1266167.3079 | 2609116.7203 | 1266153.189
68 | 2609063.6289 | 1266161.219 | 2609060.7561 | 1266160.7899
69 | 2609115.7859 | 1266177.5832 | 2609102.5563 | 1266175.7008
70 | 2609115.7859 | 1266177.5832 | 2609118.1936 | 1266193.4043
71 | 2609116.7203 | 1266153.189 | 2609119.8445 | 1266130.3029
72 | 2609060.7561 | 1266160.7899 | 2609050.619 | 1266159.2755
73 | 2609102.5563 | 1266175.7008 | 2609084.979 | 1266173.1997
74 | 2609121.2053 | 1266213.1948 | 2609118.1936 | 1266193.4043
75 | 2609122.4219 | 1266117.8102 | 2609120.1149 | 1266128.3223 | 2609119.8445 | 1266130.3029
76 | 2609045.304 | 1266158.4815 | 2609050.619 | 1266159.2755
77 | 2609037.9095 | 1266157.4082 | 2609026.4582 | 1266155.7834
78 | 2609042.0919 | 1266158.0017 | 2609037.9095 | 1266157.4082
79 | 2609008.5007 | 1266153.2353 | 2609026.4582 | 1266155.7834
80 | 2609042.0919 | 1266158.0017 | 2609042.3073 | 1266159.97 | 2609043.1168 | 1266167.243
81 | 2609042.0919 | 1266158.0017 | 2609045.304 | 1266158.4815
82 | 2609043.1168 | 1266167.243 | 2609029.148 | 1266165.2103
83 | 2609043.1168 | 1266167.243 | 2609044.7739 | 1266182.2022
84 | 2609043.1168 | 1266167.243 | 2609056.2301 | 1266169.1089
85 | 2609027.153 | 1266164.92 | 2609029.148 | 1266165.2103
86 | 2609044.7739 | 1266182.2022 | 2609045.0874 | 1266185.0321
87 | 2609027.153 | 1266164.92 | 2609004.389 | 1266161.6076
88 | 2609045.3243 | 1266187.1706 | 2609045.0874 | 1266185.0321
89 | 2609130.3723 | 1266081.5833 | 2609131.1375 | 1266078.4267 | 2609133.6361 | 1266067.7452
90 | 2609141.8985 | 1266032.4223 | 2609133.6361 | 1266067.7452
91 | 2609130.3723 | 1266081.5833 | 2609118.2677 | 1266078.9997
92 | 2609050.2657 | 1266000.8715 | 2609118.5056 | 1266014.1627 | 2609142.0835 | 1266019.7805 | 2609141.1047 | 1266024.7714 | 2609141.1007 | 1266027.3843 | 2609141.8985 | 1266032.4223
93 | 2609118.2677 | 1266078.9997 | 2609112.2363 | 1266077.7124
94 | 2609050.2657 | 1266000.8715 | 2609023.2141 | 1265994.2607
95 | 2609112.2363 | 1266077.7124 | 2609103.8292 | 1266075.918
96 | 2609103.8292 | 1266075.918 | 2609096.1812 | 1266074.2857
97 | 2609038.6912 | 1266062.0153 | 2609030.2869 | 1266060.2215
98 | 2609121.2053 | 1266213.1948 | 2609122.138 | 1266219.3242
99 | 2609055.5131 | 1266065.6056 | 2609055.316 | 1266065.5636
100 | 2609055.5131 | 1266065.6056 | 2609064.2421 | 1266067.4687
101 | 2609047.1058 | 1266063.8112 | 2609055.316 | 1266065.5636
102 | 2609065.5327 | 1266067.7442 | 2609064.2421 | 1266067.4687
103 | 2609047.1058 | 1266063.8112 | 2609038.6912 | 1266062.0153
104 | 2609065.5327 | 1266067.7442 | 2609078.3119 | 1266070.4717
105 | 2609087.0036 | 1266072.3268 | 2609078.3119 | 1266070.4717
106 | 2609095.4198 | 1266074.1232 | 2609087.0036 | 1266072.3268
107 | 2609096.1812 | 1266074.2857 | 2609095.4198 | 1266074.1232
108 | 2608964.6295 | 1266182.1068 | 2608965.6996 | 1266187.6143
109 | 2608994.2519 | 1266160.1325 | 2609004.389 | 1266161.6076
110 | 2609047.5317 | 1266207.097 | 2609048.0724 | 1266211.9775
111 | 2609048.6172 | 1266216.8962 | 2609048.0724 | 1266211.9775
112 | 2609047.515 | 1266206.9461 | 2609047.5317 | 1266207.097
113 | 2609048.6172 | 1266216.8962 | 2609048.7149 | 1266217.778
114 | 2609047.515 | 1266206.9461 | 2609046.9762 | 1266202.0823
115 | 2609048.7149 | 1266217.778 | 2609049.3058 | 1266223.1117
116 | 2609046.9624 | 1266201.958 | 2609046.9762 | 1266202.0823
117 | 2609049.4411 | 1266224.3337 | 2609049.3058 | 1266223.1117
118 | 2609046.9624 | 1266201.958 | 2609046.4255 | 1266197.1114
119 | 2609050.0801 | 1266230.1016 | 2609049.4411 | 1266224.3337
120 | 2609045.7315 | 1266190.8461 | 2609045.3243 | 1266187.1706
121 | 2608973.306 | 1266226.7642 | 2608975.5757 | 1266238.4463
122 | 2608973.306 | 1266226.7642 | 2608973.102 | 1266225.7145
123 | 2608976.9162 | 1266245.346 | 2608975.5757 | 1266238.4463
124 | 2608973.102 | 1266225.7145 | 2608971.8399 | 1266219.2184
125 | 2608976.9436 | 1266245.4868 | 2608976.9162 | 1266245.346
126 | 2608970.6274 | 1266212.9775 | 2608971.8399 | 1266219.2184
127 | 2608981.3236 | 1266268.0307 | 2608976.9436 | 1266245.4868
128 | 2608967.9469 | 1266199.181 | 2608970.6274 | 1266212.9775
129 | 2608981.3236 | 1266268.0307 | 2608991.3996 | 1266266.9206
130 | 2608966.972 | 1266194.1634 | 2608967.9469 | 1266199.181
131 | 2608966.972 | 1266194.1634 | 2608965.6996 | 1266187.6143
132 | 2609046.3754 | 1266196.659 | 2609046.4255 | 1266197.1114
133 | 2609046.3754 | 1266196.659 | 2609045.8749 | 1266192.1407
134 | 2609045.7315 | 1266190.8461 | 2609045.8749 | 1266192.1407
135 | 2608904.1601 | 1266266.7609 | 2608903.4291 | 1266263.8997 | 2608897.8769 | 1266240.6618
136 | 2609051.192 | 1266240.1386 | 2609050.6307 | 1266235.0722
137 | 2609051.5124 | 1266243.0318 | 2609051.192 | 1266240.1386
138 | 2609050.0801 | 1266230.1016 | 2609050.6307 | 1266235.0722
139 | 2609053.4021 | 1266260.0899 | 2609051.5124 | 1266243.0318
140 | 2609053.4021 | 1266260.0899 | 2609036.6713 | 1266261.9331

## bus_geodata
| x | y | coords
0 | 2608843.5969 | 1266017.929
1 | 2608840.5571 | 1266016.9613
2 | 2608854.1035 | 1266020.7857
3 | 2608857.5402 | 1266021.7202
4 | 2608866.7849 | 1266024.2338
5 | 2608874.7625 | 1266026.4029
6 | 2608926.1555 | 1266037.7192
7 | 2608936.702 | 1266040.0415
8 | 2608924.1615 | 1266037.2802
9 | 2608939.9076 | 1266040.7473
10 | 2608918.4363 | 1266036.0195
11 | 2608954.0326 | 1266043.8575
12 | 2608912.9744 | 1266034.8169
13 | 2608959.5119 | 1266045.064
14 | 2608910.527 | 1266034.278
15 | 2608880.2485 | 1266027.6109
16 | 2608892.7763 | 1266030.3694
17 | 2608886.035 | 1266100.3155
18 | 2608882.5387 | 1266098.2611
19 | 2608894.8004 | 1266105.4619
20 | 2608900.8297 | 1266032.1427
21 | 2608876.2809 | 1266094.584
22 | 2608941.8911 | 1266122.9593
23 | 2608950.4261 | 1266129.3433
24 | 2608953.6171 | 1266102.3054
25 | 2608931.6962 | 1266134.0962
26 | 2608960.9548 | 1266146.56
27 | 2608957.385 | 1266133.4757
28 | 2608959.8804 | 1266155.131
29 | 2608915.9495 | 1266141.655
30 | 2608901.288 | 1266109.271
31 | 2608941.1388 | 1266152.7122
32 | 2608946.4043 | 1266153.3918
33 | 2608935.7324 | 1266151.7748
34 | 2608967.1429 | 1266046.7443
35 | 2608979.2196 | 1266049.3219
36 | 2608963.9711 | 1266061.3396
37 | 2608998.856 | 1266053.513
38 | 2608960.9861 | 1266075.0751
39 | 2609008.5074 | 1266055.573
40 | 2608958.999 | 1266084.2189
41 | 2609020.2281 | 1266058.0746
42 | 2609022.7561 | 1266058.6142
43 | 2609029.9589 | 1266060.1515
44 | 2608902.7713 | 1266032.5702
45 | 2608878.3365 | 1266158.8781
46 | 2608893.0167 | 1266155.8821
47 | 2608886.7035 | 1266193.8969
48 | 2608890.7553 | 1266146.2805
49 | 2608958.0272 | 1266088.691
50 | 2608962.4111 | 1266170.6886
51 | 2608979.6929 | 1266158.014
52 | 2608990.4397 | 1266150.6726
53 | 2608995.2869 | 1266151.3604
54 | 2608922.5475 | 1266150.5302
55 | 2608880.0478 | 1266148.2581
56 | 2608904.6377 | 1266153.776
57 | 2608891.7902 | 1266215.1866
58 | 2609084.8354 | 1266164.387
59 | 2609092.7075 | 1266165.563
60 | 2609076.3419 | 1266163.1182
61 | 2609114.6549 | 1266168.9421
62 | 2609063.6289 | 1266161.219
63 | 2609115.7859 | 1266177.5832
64 | 2609116.7203 | 1266153.189
65 | 2609060.7561 | 1266160.7899
66 | 2609102.5563 | 1266175.7008
67 | 2609118.1936 | 1266193.4043
68 | 2609119.8445 | 1266130.3029
69 | 2609050.619 | 1266159.2755
70 | 2609037.9095 | 1266157.4082
71 | 2609026.4582 | 1266155.7834
72 | 2609042.0919 | 1266158.0017
73 | 2609008.5007 | 1266153.2353
74 | 2609043.1168 | 1266167.243
75 | 2609045.304 | 1266158.4815
76 | 2609029.148 | 1266165.2103
77 | 2609044.7739 | 1266182.2022
78 | 2609056.2301 | 1266169.1089
79 | 2609027.153 | 1266164.92
80 | 2609045.0874 | 1266185.0321
81 | 2609133.6361 | 1266067.7452
82 | 2609130.3723 | 1266081.5833
83 | 2609141.8985 | 1266032.4223
84 | 2609118.2677 | 1266078.9997
85 | 2609050.2657 | 1266000.8715
86 | 2609112.2363 | 1266077.7124
87 | 2609122.4219 | 1266117.8102
88 | 2609023.2141 | 1265994.2607
89 | 2609103.8292 | 1266075.918
90 | 2609030.2869 | 1266060.2215
91 | 2609084.979 | 1266173.1997
92 | 2609121.2053 | 1266213.1948
93 | 2609055.5131 | 1266065.6056
94 | 2609055.316 | 1266065.5636
95 | 2609064.2421 | 1266067.4687
96 | 2609047.1058 | 1266063.8112
97 | 2609065.5327 | 1266067.7442
98 | 2609038.6912 | 1266062.0153
99 | 2609078.3119 | 1266070.4717
100 | 2609087.0036 | 1266072.3268
101 | 2609096.1812 | 1266074.2857
102 | 2609095.4198 | 1266074.1232
103 | 2608964.6295 | 1266182.1068
104 | 2608994.2519 | 1266160.1325
105 | 2609048.0724 | 1266211.9775
106 | 2609047.5317 | 1266207.097
107 | 2609048.6172 | 1266216.8962
108 | 2609047.515 | 1266206.9461
109 | 2609048.7149 | 1266217.778
110 | 2609046.9762 | 1266202.0823
111 | 2609049.3058 | 1266223.1117
112 | 2609046.9624 | 1266201.958
113 | 2609049.4411 | 1266224.3337
114 | 2609004.389 | 1266161.6076
115 | 2609045.3243 | 1266187.1706
116 | 2608973.306 | 1266226.7642
117 | 2608975.5757 | 1266238.4463
118 | 2608973.102 | 1266225.7145
119 | 2608976.9162 | 1266245.346
120 | 2608971.8399 | 1266219.2184
121 | 2608976.9436 | 1266245.4868
122 | 2608970.6274 | 1266212.9775
123 | 2608981.3236 | 1266268.0307
124 | 2608967.9469 | 1266199.181
125 | 2608966.972 | 1266194.1634
126 | 2608965.6996 | 1266187.6143
127 | 2608913.4758 | 1266152.1742
128 | 2609122.138 | 1266219.3242
129 | 2608991.3996 | 1266266.9206
130 | 2609046.4255 | 1266197.1114
131 | 2609046.3754 | 1266196.659
132 | 2609045.8749 | 1266192.1407
133 | 2609045.7315 | 1266190.8461
134 | 2608897.8769 | 1266240.6618
135 | 2608904.1601 | 1266266.7609
136 | 2609051.192 | 1266240.1386
137 | 2609050.6307 | 1266235.0722
138 | 2609051.5124 | 1266243.0318
139 | 2609050.0801 | 1266230.1016
140 | 2609053.4021 | 1266260.0899
141 | 2609036.6713 | 1266261.9331
142 | 2608950.4261 | 1266129.3433

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98732 | -0.24416 | 0.010158 | 0.0025459
1 | 0.9873 | -0.24461 | 0.0079375 | 0.0019893
2 | 0.9875 | -0.24063 | 0.0082057 | 0.0020565
3 | 0.98759 | -0.23896 | 0.0040249 | 0.0010087
4 | 0.98785 | -0.23377 | 0.0091645 | 0.0022968
5 | 0.98815 | -0.22794 | 0 | 0
6 | 0.99096 | -0.1735 | 0.0035952 | 0.00090104
7 | 0.99174 | -0.15834 | 0.0035019 | 0.00087766
8 | 0.99082 | -0.17624 | 0.0027339 | 0.00068517
9 | 0.99199 | -0.15353 | 0.0089042 | 0.0022316
10 | 0.99043 | -0.18382 | 0.0036025 | 0.00090287
11 | 0.99321 | -0.1301 | 0.0026518 | 0.00066461
12 | 0.99007 | -0.1907 | 0.0027928 | 0.00069995
13 | 0.99369 | -0.12076 | 0.0089102 | 0.0022331
14 | 0.98992 | -0.19367 | 0.0036058 | 0.00090371
15 | 0.98836 | -0.22398 | 0.0091909 | 0.0023035
16 | 0.98893 | -0.21284 | 0.0071766 | 0.0017986
17 | 0.99763 | -0.045383 | 0 | 0
18 | 0.9976 | -0.046037 | 0.0045972 | 0.0011522
19 | 0.99771 | -0.043742 | 0.0014686 | 0.00036807
20 | 0.98935 | -0.20464 | 0.0033027 | 0.00082774
21 | 0.99756 | -0.046624 | 0.0046169 | 0.0011571
22 | 0.99863 | -0.026155 | 0 | 0
23 | 0.99918 | -0.015596 | 0 | 0
24 | 0.99752 | -0.047268 | 0.0044052 | 0.0011041
25 | 0.99824 | -0.033549 | 0 | 0
26 | 0.99797 | -0.038602 | 0 | 0
27 | 1 | 0 | -0.44744 | -0.11325
28 | 0.99711 | -0.055031 | 0 | 0
29 | 0.99809 | -0.036531 | 0.0050246 | 0.0012593
30 | 0.99779 | -0.042335 | 0.0014712 | 0.00036872
31 | 0.99614 | -0.073803 | 0 | 0
32 | 0.9964 | -0.068693 | 0.0025075 | 0.00062843
33 | 0.99586 | -0.079087 | 0.0018881 | 0.00047321
34 | 0.99443 | -0.10655 | 0 | 0
35 | 0.99357 | -0.12311 | 0.00892 | 0.0022356
36 | 0.99566 | -0.083 | 0.0064242 | 0.0016101
37 | 0.99234 | -0.14692 | 0.0056864 | 0.0014251
38 | 0.99625 | -0.071541 | 0.0047466 | 0.0011896
39 | 0.99178 | -0.15765 | 0.0063295 | 0.0015863
40 | 0.99666 | -0.063726 | 0.0021855 | 0.00054773
41 | 0.99118 | -0.16935 | 0.0041088 | 0.0010298
42 | 0.99106 | -0.17169 | 0.0024369 | 0.00061075
43 | 0.99073 | -0.17804 | 0.0014908 | 0.00037364
44 | 0.98946 | -0.20254 | 0.0036711 | 0.00092006
45 | 0.99329 | -0.12851 | 0 | 0
46 | 0.99387 | -0.11744 | 0.0053934 | 0.0013517
47 | 0.99192 | -0.15517 | 0.0050959 | 0.0012771
48 | 0.99799 | -0.038456 | 0.0025407 | 0.00063676
49 | 0.99686 | -0.059863 | 0.0063119 | 0.0015819
50 | 0.99669 | -0.063154 | 0.00098801 | 0.00024762
51 | 0.99471 | -0.10094 | 0.0044847 | 0.001124
52 | 0.98591 | -0.27095 | 0.0051432 | 0.001289
53 | 0.98594 | -0.2705 | 0.007226 | 0.001811
54 | 0.99521 | -0.091543 | 0.0018914 | 0.00047402
55 | 0.99797 | -0.038789 | 0.0017514 | 0.00043894
56 | 0.99438 | -0.1076 | 0.0018894 | 0.00047354
57 | 0.99118 | -0.16943 | 0.012138 | 0.0030422
58 | 0.98532 | -0.28251 | 0.0026912 | 0.00067447
59 | 0.98512 | -0.28644 | 0.0029028 | 0.00072751
60 | 0.98556 | -0.27785 | 0.0029321 | 0.00073486
61 | 0.98461 | -0.29626 | 0 | 0
62 | 0.98595 | -0.27021 | 0.0040008 | 0.0010027
63 | 0.98448 | -0.29889 | 0 | 0
64 | 0.9845 | -0.2985 | 0.0031995 | 0.00080187
65 | 0.98605 | -0.26827 | 0.0059276 | 0.0014856
66 | 0.98433 | -0.30174 | 0.0035464 | 0.0008888
67 | 0.98441 | -0.30032 | 0.0016282 | 0.00040807
68 | 0.9844 | -0.30042 | 0.0023232 | 0.00058225
69 | 0.98646 | -0.26036 | 0.0038651 | 0.00096868
70 | 0.98672 | -0.25528 | 0.0045108 | 0.0011305
71 | 0.98641 | -0.26122 | 0.0092387 | 0.0023154
72 | 0.98685 | -0.25277 | 0 | 0
73 | 0.98609 | -0.26754 | 0.0070666 | 0.0017711
74 | 0.98758 | -0.23846 | 0 | 0
75 | 0.98669 | -0.25585 | 0.0059355 | 0.0014876
76 | 0.98908 | -0.20933 | 0.001836 | 0.00046014
77 | 0.9872 | -0.24597 | 0.0018367 | 0.00046032
78 | 0.98756 | -0.23887 | 0.0017009 | 0.00042628
79 | 0.9893 | -0.20511 | 0.0022541 | 0.00056492
80 | 0.98713 | -0.2473 | 0.0016634 | 0.0004169
81 | 0.98802 | -0.2307 | 0.0063651 | 0.0015952
82 | 0.98812 | -0.22863 | 0 | 0
83 | 0.98796 | -0.23188 | 0 | 0
84 | 0.98822 | -0.22682 | 0.0032391 | 0.0008118
85 | 0.98778 | -0.23533 | 0 | 0
86 | 0.98828 | -0.22556 | 0.0050982 | 0.0012777
87 | 0.98437 | -0.30095 | 0.0023009 | 0.00057667
88 | 0.98773 | -0.23623 | 0.0018086 | 0.00045328
89 | 0.98841 | -0.22303 | 0.0051008 | 0.0012784
90 | 0.99071 | -0.17832 | 0.0024401 | 0.00061156
91 | 0.9842 | -0.30438 | 0.0082794 | 0.002075
92 | 0.98434 | -0.30152 | 0.0016743 | 0.00041963
93 | 0.98972 | -0.19763 | 0.0024428 | 0.00061222
94 | 0.98973 | -0.1975 | 0.0020836 | 0.00052221
95 | 0.98943 | -0.20322 | 0.0027532 | 0.00069002
96 | 0.99003 | -0.19157 | 0.0024426 | 0.00061217
97 | 0.98939 | -0.20399 | 0.0013226 | 0.00033148
98 | 0.99036 | -0.18512 | 0.0024412 | 0.00061181
99 | 0.98902 | -0.21123 | 0.0027547 | 0.00069039
100 | 0.98879 | -0.21572 | 0.0024692 | 0.00061884
101 | 0.98857 | -0.22001 | 0.0017923 | 0.0004492
102 | 0.98858 | -0.21969 | 0.002471 | 0.00061928
103 | 0.99639 | -0.068945 | 0.00097602 | 0.00024461
104 | 0.99301 | -0.13366 | 0.0018457 | 0.00046257
105 | 0.98671 | -0.25551 | 0.0012622 | 0.00031635
106 | 0.98676 | -0.25452 | 0.0011425 | 0.00028633
107 | 0.98666 | -0.25639 | 0.0012105 | 0.00030339
108 | 0.98676 | -0.25449 | 0.0010815 | 0.00027105
109 | 0.98665 | -0.25653 | 0.0011996 | 0.00030066
110 | 0.98682 | -0.25331 | 0.0010904 | 0.00027328
111 | 0.98662 | -0.25726 | 0.0010064 | 0.00025224
112 | 0.98682 | -0.25328 | 0.0010309 | 0.00025836
113 | 0.98661 | -0.2574 | 0.0011976 | 0.00030016
114 | 0.99184 | -0.15616 | 0.0043918 | 0.0011007
115 | 0.98708 | -0.24824 | 0.0018389 | 0.00046088
116 | 0.9955 | -0.086201 | 0.0053905 | 0.001351
117 | 0.99541 | -0.087876 | 0.0027053 | 0.00067801
118 | 0.99551 | -0.085949 | 0.0018658 | 0.00046762
119 | 0.99538 | -0.08853 | 0.0019062 | 0.00047774
120 | 0.9956 | -0.084174 | 0.0018559 | 0.00046514
121 | 0.99538 | -0.088539 | 0.0017668 | 0.00044279
122 | 0.9957 | -0.082261 | 0.0043849 | 0.001099
123 | 0.99534 | -0.089194 | 0 | 0
124 | 0.99598 | -0.07695 | 0.0033628 | 0.00084281
125 | 0.99609 | -0.074717 | 0.0013725 | 0.00034398
126 | 0.99625 | -0.071643 | 0.0011568 | 0.00028993
127 | 0.99478 | -0.099826 | 0.0018927 | 0.00047435
128 | 0.98433 | -0.30171 | 0.0016589 | 0.00041576
129 | 0.99533 | -0.089483 | 0.001621 | 0.00040627
130 | 0.98689 | -0.25192 | 0.0018381 | 0.00046067
131 | 0.9869 | -0.25178 | 0.0016629 | 0.00041677
132 | 0.98698 | -0.25022 | 0.0018383 | 0.00046072
133 | 0.987 | -0.24974 | 0.0016618 | 0.00041648
134 | 0.99059 | -0.18087 | 0.012152 | 0.0030456
135 | 0.99028 | -0.18682 | 0.012459 | 0.0031226
136 | 0.98654 | -0.25866 | 0.0010389 | 0.00026037
137 | 0.98656 | -0.25835 | 0.00099961 | 0.00025053
138 | 0.98654 | -0.25878 | 0.001125 | 0.00028196
139 | 0.98658 | -0.25796 | 0.00099941 | 0.00025048
140 | 0.98652 | -0.25914 | 0 | 0
141 | 0.9865 | -0.2595 | 0.0011913 | 0.00029857
142 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0079377 | 0.0019894 | -0.0079375 | -0.0019893 | 1.7146e-07 | 6.8877e-08 | 0.011963 | 0.011963 | 0.011963 | 0.98732 | -0.24416 | 0.9873 | -0.24461 | 3.2866
1 | -0.018096 | -0.0045353 | 0.018099 | 0.0045371 | 3.037e-06 | 1.8044e-06 | 0.027273 | 0.027273 | 0.027273 | 0.98732 | -0.24416 | 0.9875 | -0.24063 | 7.4926
2 | -0.026305 | -0.0065936 | 0.026307 | 0.0065949 | 2.0983e-06 | 1.2974e-06 | 0.039638 | 0.039638 | 0.039638 | 0.9875 | -0.24063 | 0.98759 | -0.23896 | 10.8895
3 | -0.030332 | -0.0076037 | 0.030339 | 0.0076084 | 7.5038e-06 | 4.6798e-06 | 0.045702 | 0.045702 | 0.045702 | 0.98759 | -0.23896 | 0.98785 | -0.23377 | 12.5555
4 | -0.039504 | -0.0099052 | 0.039515 | 0.0099121 | 1.0978e-05 | 6.92e-06 | 0.059507 | 0.059507 | 0.059507 | 0.98785 | -0.23377 | 0.98815 | -0.22794 | 16.348
5 | -0.039515 | -0.0099121 | 0.039522 | 0.0099168 | 7.4594e-06 | 4.702e-06 | 0.059507 | 0.059507 | 0.059507 | 0.98815 | -0.22794 | 0.98836 | -0.22398 | 16.348
6 | -0.079343 | -0.019954 | 0.0794 | 0.019991 | 5.7506e-05 | 3.6665e-05 | 0.11916 | 0.11916 | 0.11916 | 0.99096 | -0.1735 | 0.99174 | -0.15834 | 32.7375
7 | 0.075747 | 0.019053 | -0.075738 | -0.019047 | 9.9096e-06 | 6.3158e-06 | 0.11377 | 0.11377 | 0.11377 | 0.99096 | -0.1735 | 0.99082 | -0.17624 | 31.2544
8 | -0.082902 | -0.020868 | 0.082921 | 0.020881 | 1.9055e-05 | 1.2153e-05 | 0.12442 | 0.12442 | 0.12442 | 0.99174 | -0.15834 | 0.99199 | -0.15353 | 34.181
9 | 0.073004 | 0.018362 | -0.072977 | -0.018345 | 2.6436e-05 | 1.6844e-05 | 0.10966 | 0.10966 | 0.10966 | 0.99082 | -0.17624 | 0.99043 | -0.18382 | 30.1265
10 | -0.091825 | -0.023112 | 0.091928 | 0.023178 | 0.00010295 | 6.5703e-05 | 0.13778 | 0.13778 | 0.13778 | 0.99199 | -0.15353 | 0.99321 | -0.1301 | 37.8504
11 | 0.069375 | 0.017442 | -0.069352 | -0.017427 | 2.2793e-05 | 1.4515e-05 | 0.10425 | 0.10425 | 0.10425 | 0.99043 | -0.18382 | 0.99007 | -0.1907 | 28.6396
12 | -0.09458 | -0.023843 | 0.094622 | 0.02387 | 4.2274e-05 | 2.6983e-05 | 0.14175 | 0.14175 | 0.14175 | 0.99321 | -0.1301 | 0.99369 | -0.12076 | 38.9418
13 | 0.066559 | 0.016727 | -0.06655 | -0.016721 | 9.4071e-06 | 5.9883e-06 | 0.10005 | 0.10005 | 0.10005 | 0.99007 | -0.1907 | 0.98992 | -0.19367 | 27.4864
14 | -0.10353 | -0.026103 | 0.1036 | 0.026148 | 7.048e-05 | 4.5006e-05 | 0.15509 | 0.15509 | 0.15509 | 0.99369 | -0.12076 | 0.99443 | -0.10655 | 42.6074
15 | 0.062944 | 0.015818 | -0.062917 | -0.015801 | 2.6668e-05 | 1.6966e-05 | 0.09463 | 0.094631 | 0.094631 | 0.98992 | -0.19367 | 0.98946 | -0.20254 | 25.9974
16 | -0.048713 | -0.01222 | 0.048739 | 0.012237 | 2.5877e-05 | 1.6397e-05 | 0.073344 | 0.073344 | 0.073344 | 0.98836 | -0.22398 | 0.98893 | -0.21284 | 20.1494
17 | -0.055916 | -0.014035 | 0.055938 | 0.014049 | 2.1894e-05 | 1.3906e-05 | 0.084142 | 0.084142 | 0.084142 | 0.98893 | -0.21284 | 0.98935 | -0.20464 | 23.116
18 | 0.0092146 | 0.0023094 | -0.0092143 | -0.0023093 | 2.8726e-07 | 1.309e-07 | 0.013744 | 0.013744 | 0.013744 | 0.99763 | -0.045383 | 0.9976 | -0.046037 | 3.7758
19 | -0.0092146 | -0.0023094 | 0.0092153 | 0.0023097 | 7.2002e-07 | 3.2808e-07 | 0.013744 | 0.013744 | 0.013744 | 0.99763 | -0.045383 | 0.99771 | -0.043742 | 3.7758
20 | 0.004617 | 0.0011571 | -0.0046169 | -0.0011571 | 1.2909e-07 | -1.2144e-08 | 0.0068868 | 0.0068868 | 0.0068868 | 0.9976 | -0.046037 | 0.99756 | -0.046624 | 1.892
21 | -0.010684 | -0.0026778 | 0.010685 | 0.0026782 | 7.1631e-07 | 3.6018e-07 | 0.015934 | 0.015934 | 0.015934 | 0.99771 | -0.043742 | 0.99779 | -0.042335 | 4.3776
22 | -0.05924 | -0.014877 | 0.059246 | 0.014881 | 5.9202e-06 | 3.7634e-06 | 0.08911 | 0.08911 | 0.08911 | 0.98935 | -0.20464 | 0.98946 | -0.20254 | 24.4807
23 | -0.2262 | -0.057275 | 0.22632 | 0.057348 | 0.00011475 | 7.2877e-05 | 0.33726 | 0.33726 | 0.33726 | 0.99863 | -0.026155 | 0.99918 | -0.015596 | 23.1636
24 | 0.20472 | 0.051886 | -0.20451 | -0.051754 | 0.00020746 | 0.00013153 | 0.30524 | 0.30524 | 0.30524 | 0.99863 | -0.026155 | 0.99752 | -0.047268 | 20.9645
25 | 0.021487 | 0.0053896 | -0.021479 | -0.005385 | 7.5705e-06 | 4.5876e-06 | 0.032018 | 0.032019 | 0.032019 | 0.99863 | -0.026155 | 0.99824 | -0.033549 | 8.7963
26 | 0.21914 | 0.055688 | -0.2189 | -0.055534 | 0.00024247 | 0.00015391 | 0.32662 | 0.32662 | 0.32662 | 0.99918 | -0.015596 | 0.99797 | -0.038602 | 22.4329
27 | -0.44546 | -0.11304 | 0.44579 | 0.11325 | 0.00033442 | 0.0002136 | 0.66388 | 0.66388 | 0.66388 | 0.99918 | -0.015596 | 1 | 0 | 45.5964
28 | 0.2001 | 0.05065 | -0.19998 | -0.050574 | 0.0001209 | 7.6621e-05 | 0.29867 | 0.29867 | 0.29867 | 0.99752 | -0.047268 | 0.99686 | -0.059863 | 20.5132
29 | 0.0093184 | 0.0023354 | -0.0093171 | -0.0023348 | 1.3237e-06 | 6.0805e-07 | 0.01389 | 0.01389 | 0.01389 | 0.99824 | -0.033549 | 0.99809 | -0.036531 | 3.8161
30 | 0.012161 | 0.0030496 | -0.012156 | -0.0030469 | 5.0904e-06 | 2.7181e-06 | 0.018128 | 0.018128 | 0.018128 | 0.99824 | -0.033549 | 0.99779 | -0.042335 | 4.9803
31 | 0.2189 | 0.055534 | -0.21872 | -0.055424 | 0.00017279 | 0.00011036 | 0.32662 | 0.32662 | 0.32662 | 0.99797 | -0.038602 | 0.99711 | -0.055031 | 44.8658
32 | 0.029391 | 0.0073795 | -0.02938 | -0.0073725 | 1.1384e-05 | 7.0804e-06 | 0.043866 | 0.043866 | 0.043866 | 0.99711 | -0.055031 | 0.99669 | -0.063154 | 12.0511
33 | 0.13175 | 0.033508 | -0.13146 | -0.033322 | 0.00029075 | 0.00018582 | 0.19679 | 0.19679 | 0.19679 | 0.99711 | -0.055031 | 0.99471 | -0.10094 | 54.0624
34 | 0.057583 | 0.014536 | -0.057546 | -0.014512 | 3.766e-05 | 2.3925e-05 | 0.08597 | 0.08597 | 0.08597 | 0.99711 | -0.055031 | 0.9964 | -0.068693 | 23.6181
35 | 0.0042925 | 0.0010755 | -0.0042921 | -0.0010756 | 3.9339e-07 | -8.2969e-08 | 0.0063994 | 0.0063996 | 0.0063996 | 0.99809 | -0.036531 | 0.99799 | -0.038456 | 1.7581
36 | -0.055025 | -0.013875 | 0.055038 | 0.013884 | 1.3461e-05 | 8.5458e-06 | 0.082225 | 0.082225 | 0.082225 | 0.99614 | -0.073803 | 0.9964 | -0.068693 | 22.5894
37 | 0.055025 | 0.013875 | -0.055011 | -0.013867 | 1.3912e-05 | 8.8321e-06 | 0.082225 | 0.082225 | 0.082225 | 0.99614 | -0.073803 | 0.99586 | -0.079087 | 22.5894
38 | 0.053123 | 0.013393 | -0.053091 | -0.013373 | 3.1649e-05 | 2.0081e-05 | 0.079404 | 0.079404 | 0.079404 | 0.99586 | -0.079087 | 0.99521 | -0.091543 | 21.8143
39 | 0.076297 | 0.019234 | -0.076237 | -0.019196 | 6.04e-05 | 3.8496e-05 | 0.11421 | 0.11421 | 0.11421 | 0.99443 | -0.10655 | 0.99357 | -0.12311 | 31.3756
40 | -0.1799 | -0.045382 | 0.1801 | 0.045511 | 0.0002031 | 0.00012959 | 0.2693 | 0.2693 | 0.2693 | 0.99443 | -0.10655 | 0.99566 | -0.083 | 36.9915
41 | 0.067317 | 0.01696 | -0.06724 | -0.016911 | 7.6578e-05 | 4.875e-05 | 0.10085 | 0.10085 | 0.10085 | 0.99357 | -0.12311 | 0.99234 | -0.14692 | 27.7055
42 | -0.18653 | -0.047121 | 0.18663 | 0.047186 | 0.0001025 | 6.4869e-05 | 0.2789 | 0.2789 | 0.2789 | 0.99566 | -0.083 | 0.99625 | -0.071541 | 19.1551
43 | 0.061554 | 0.015486 | -0.061522 | -0.015466 | 3.1543e-05 | 2.006e-05 | 0.092321 | 0.092321 | 0.092321 | 0.99234 | -0.14692 | 0.99178 | -0.15765 | 25.363
44 | -0.19138 | -0.048376 | 0.19145 | 0.048421 | 7.1749e-05 | 4.5432e-05 | 0.28599 | 0.28599 | 0.28599 | 0.99625 | -0.071541 | 0.99666 | -0.063726 | 19.642
45 | 0.055193 | 0.01388 | -0.055162 | -0.01386 | 3.0831e-05 | 1.9577e-05 | 0.082825 | 0.082825 | 0.082825 | 0.99178 | -0.15765 | 0.99118 | -0.16935 | 22.7542
46 | -0.19363 | -0.048969 | 0.19367 | 0.048992 | 3.5896e-05 | 2.2735e-05 | 0.28925 | 0.28925 | 0.28925 | 0.99666 | -0.063726 | 0.99686 | -0.059863 | 19.8661
47 | 0.051053 | 0.01283 | -0.051048 | -0.012827 | 5.6963e-06 | 3.6123e-06 | 0.076657 | 0.076657 | 0.076657 | 0.99118 | -0.16935 | 0.99106 | -0.17169 | 21.0596
48 | 0.048611 | 0.012216 | -0.048596 | -0.012207 | 1.4717e-05 | 9.3241e-06 | 0.072998 | 0.072998 | 0.072998 | 0.99106 | -0.17169 | 0.99073 | -0.17804 | 20.0544
49 | 0.047105 | 0.011833 | -0.047104 | -0.011833 | 6.2982e-07 | 3.9877e-07 | 0.070759 | 0.070759 | 0.070759 | 0.99073 | -0.17804 | 0.99071 | -0.17832 | 19.4392
50 | -0.041941 | -0.010547 | 0.041963 | 0.010561 | 2.2194e-05 | 1.401e-05 | 0.062843 | 0.062843 | 0.062843 | 0.99329 | -0.12851 | 0.99387 | -0.11744 | 17.2646
51 | 0.041941 | 0.010547 | -0.041888 | -0.010513 | 5.3322e-05 | 3.366e-05 | 0.062843 | 0.062843 | 0.062843 | 0.99329 | -0.12851 | 0.99192 | -0.15517 | 17.2646
52 | -0.047357 | -0.011913 | 0.047379 | 0.011927 | 2.2274e-05 | 1.4102e-05 | 0.070918 | 0.070918 | 0.070918 | 0.99387 | -0.11744 | 0.99438 | -0.1076 | 19.4829
53 | 0.036792 | 0.0092363 | -0.036767 | -0.0092206 | 2.501e-05 | 1.5724e-05 | 0.055199 | 0.055199 | 0.055199 | 0.99192 | -0.15517 | 0.99118 | -0.16943 | 15.1645
54 | 0.0017514 | 0.00043881 | -0.0017514 | -0.00043894 | 2.7844e-08 | -1.2445e-07 | 0.0026113 | 0.0026114 | 0.0026114 | 0.99799 | -0.038456 | 0.99797 | -0.038789 | 0.71741
55 | 0.028392 | 0.0071248 | -0.028384 | -0.00712 | 7.8383e-06 | 4.865e-06 | 0.042391 | 0.042391 | 0.042391 | 0.99669 | -0.063154 | 0.99639 | -0.068945 | 11.6459
56 | 0.12697 | 0.032198 | -0.12678 | -0.032071 | 0.00019933 | 0.00012738 | 0.19008 | 0.19008 | 0.19008 | 0.99471 | -0.10094 | 0.99301 | -0.13366 | 52.2194
57 | -0.0051432 | -0.001289 | 0.0051433 | 0.001289 | 1.1063e-07 | 8.3668e-09 | 0.0077625 | 0.0077625 | 0.0077625 | 0.98591 | -0.27095 | 0.98594 | -0.2705 | 2.1326
58 | -0.012369 | -0.0031 | 0.012371 | 0.003101 | 1.7442e-06 | 9.4605e-07 | 0.018668 | 0.018668 | 0.018668 | 0.98594 | -0.2705 | 0.98609 | -0.26754 | 5.1286
59 | 0.0512 | 0.012899 | -0.051179 | -0.012886 | 2.0273e-05 | 1.2855e-05 | 0.076576 | 0.076576 | 0.076576 | 0.99521 | -0.091543 | 0.99478 | -0.099826 | 21.0374
60 | -0.049268 | -0.0124 | 0.049287 | 0.012412 | 1.8318e-05 | 1.1607e-05 | 0.073745 | 0.073745 | 0.073745 | 0.99438 | -0.1076 | 0.99478 | -0.099826 | 20.2597
61 | 0.024628 | 0.0061784 | -0.024615 | -0.0061701 | 1.3429e-05 | 8.2571e-06 | 0.036976 | 0.036976 | 0.036976 | 0.99118 | -0.16943 | 0.99059 | -0.18087 | 10.1582
62 | 0.027537 | 0.0069084 | -0.027532 | -0.0069052 | 5.1625e-06 | 3.2026e-06 | 0.041588 | 0.041588 | 0.041588 | 0.98532 | -0.28251 | 0.98512 | -0.28644 | 11.4254
63 | -0.030228 | -0.0075829 | 0.030235 | 0.0075871 | 6.7118e-06 | 4.1862e-06 | 0.045653 | 0.045653 | 0.045653 | 0.98532 | -0.28251 | 0.98556 | -0.27785 | 12.5419
64 | 0.024629 | 0.0061777 | -0.024617 | -0.0061706 | 1.1526e-05 | 7.0942e-06 | 0.037204 | 0.037204 | 0.037204 | 0.98512 | -0.28644 | 0.98461 | -0.29626 | 10.2209
65 | -0.033167 | -0.0083219 | 0.033179 | 0.0083295 | 1.2089e-05 | 7.5731e-06 | 0.05008 | 0.05008 | 0.05008 | 0.98556 | -0.27785 | 0.98595 | -0.27021 | 13.7581
66 | 0.016793 | 0.0042096 | -0.01679 | -0.0042084 | 2.1068e-06 | 1.2374e-06 | 0.025378 | 0.025378 | 0.025378 | 0.98461 | -0.29626 | 0.98448 | -0.29889 | 6.9721
67 | 0.0078249 | 0.001961 | -0.0078241 | -0.0019606 | 8.3329e-07 | 3.3123e-07 | 0.011826 | 0.011826 | 0.011826 | 0.98461 | -0.29626 | 0.9845 | -0.2985 | 3.2488
68 | -0.03718 | -0.0093322 | 0.037183 | 0.0093343 | 3.4304e-06 | 2.1584e-06 | 0.056118 | 0.056118 | 0.056118 | 0.98595 | -0.27021 | 0.98605 | -0.26827 | 15.4169
69 | 0.011828 | 0.0029651 | -0.011827 | -0.0029643 | 1.6018e-06 | 8.5525e-07 | 0.017879 | 0.017879 | 0.017879 | 0.98448 | -0.29889 | 0.98433 | -0.30174 | 4.9117
70 | 0.004962 | 0.0012433 | -0.0049616 | -0.0012433 | 3.3755e-07 | 1.2565e-08 | 0.0074998 | 0.0074999 | 0.0074999 | 0.98448 | -0.29889 | 0.98441 | -0.30032 | 2.0604
71 | 0.0046246 | 0.0011588 | -0.0046242 | -0.0011588 | 4.232e-07 | -2.2838e-08 | 0.0069897 | 0.0069898 | 0.0069898 | 0.9845 | -0.2985 | 0.9844 | -0.30042 | 1.9203
72 | -0.043111 | -0.01082 | 0.043127 | 0.01083 | 1.627e-05 | 1.0282e-05 | 0.065063 | 0.065063 | 0.065063 | 0.98605 | -0.26827 | 0.98646 | -0.26036 | 17.8744
73 | 0.0082805 | 0.0020755 | -0.0082794 | -0.002075 | 1.0432e-06 | 4.4202e-07 | 0.012518 | 0.012518 | 0.012518 | 0.98433 | -0.30174 | 0.9842 | -0.30438 | 3.4389
74 | 0.0033334 | 0.00083518 | -0.0033332 | -0.00083531 | 1.9059e-07 | -1.3251e-07 | 0.0050387 | 0.0050388 | 0.0050388 | 0.98441 | -0.30032 | 0.98434 | -0.30152 | 1.3843
75 | 0.002301 | 0.00057654 | -0.0023009 | -0.00057667 | 5.7893e-08 | -1.2518e-07 | 0.0034781 | 0.0034782 | 0.0034782 | 0.9844 | -0.30042 | 0.98437 | -0.30095 | 0.95554
76 | -0.046992 | -0.011799 | 0.047002 | 0.011805 | 1.0128e-05 | 6.4135e-06 | 0.070893 | 0.070893 | 0.070893 | 0.98646 | -0.26036 | 0.98669 | -0.25585 | 19.4761
77 | 0.02869 | 0.007196 | -0.028682 | -0.007191 | 8.1199e-06 | 5.0491e-06 | 0.043268 | 0.043268 | 0.043268 | 0.98672 | -0.25528 | 0.98641 | -0.26122 | 11.8869
78 | -0.033201 | -0.0083265 | 0.033205 | 0.008329 | 3.9716e-06 | 2.4878e-06 | 0.050071 | 0.050071 | 0.050071 | 0.98672 | -0.25528 | 0.98685 | -0.25277 | 13.7557
79 | 0.019444 | 0.0048755 | -0.019438 | -0.004872 | 5.8517e-06 | 3.5137e-06 | 0.029332 | 0.029332 | 0.029332 | 0.98641 | -0.26122 | 0.98609 | -0.26754 | 8.0582
80 | -0.086151 | -0.021627 | 0.086209 | 0.021664 | 5.8849e-05 | 3.7544e-05 | 0.12991 | 0.12991 | 0.12991 | 0.98685 | -0.25277 | 0.98758 | -0.23846 | 35.6909
81 | 0.052946 | 0.013298 | -0.052938 | -0.013293 | 7.7641e-06 | 4.9276e-06 | 0.079844 | 0.079844 | 0.079844 | 0.98685 | -0.25277 | 0.98669 | -0.25585 | 21.9352
82 | -0.11585 | -0.029098 | 0.11601 | 0.029201 | 0.00016132 | 0.00010306 | 0.17457 | 0.17457 | 0.17457 | 0.98758 | -0.23846 | 0.98908 | -0.20933 | 47.9592
83 | 0.027936 | 0.0070077 | -0.027926 | -0.0070015 | 1.0001e-05 | 6.2079e-06 | 0.042094 | 0.042094 | 0.042094 | 0.98758 | -0.23846 | 0.9872 | -0.24597 | 11.5643
84 | 0.0017009 | 0.00042613 | -0.0017009 | -0.00042628 | 3.2623e-08 | -1.486e-07 | 0.0025628 | 0.0025628 | 0.0025628 | 0.98758 | -0.23846 | 0.98756 | -0.23887 | 0.70407
85 | -0.11784 | -0.029661 | 0.11787 | 0.029677 | 2.3774e-05 | 1.5189e-05 | 0.17733 | 0.17733 | 0.17733 | 0.98908 | -0.20933 | 0.9893 | -0.20511 | 48.718
86 | 0.026089 | 0.0065412 | -0.026088 | -0.0065402 | 1.6512e-06 | 1.0204e-06 | 0.039326 | 0.039326 | 0.039326 | 0.9872 | -0.24597 | 0.98713 | -0.2473 | 10.8037
87 | -0.12012 | -0.030242 | 0.1204 | 0.030422 | 0.00028175 | 0.00018002 | 0.18072 | 0.18072 | 0.18072 | 0.9893 | -0.20511 | 0.99184 | -0.15616 | 49.6495
88 | 0.024424 | 0.0061233 | -0.024423 | -0.0061226 | 1.0937e-06 | 6.7249e-07 | 0.036818 | 0.036818 | 0.036818 | 0.98713 | -0.2473 | 0.98708 | -0.24824 | 10.1149
89 | -0.0081742 | -0.0020466 | 0.008175 | 0.002047 | 8.0795e-07 | 3.3499e-07 | 0.01231 | 0.01231 | 0.01231 | 0.98802 | -0.2307 | 0.98812 | -0.22863 | 3.3819
90 | 0.0018091 | 0.0004514 | -0.001809 | -0.0004518 | 1.0094e-07 | -3.9995e-07 | 0.0027239 | 0.0027241 | 0.0027241 | 0.98802 | -0.2307 | 0.98796 | -0.23188 | 0.74837
91 | -0.008175 | -0.002047 | 0.0081757 | 0.0020473 | 7.0335e-07 | 2.9158e-07 | 0.01231 | 0.01231 | 0.01231 | 0.98812 | -0.22863 | 0.98822 | -0.22682 | 3.3819
92 | 0.001809 | 0.0004518 | -0.0018087 | -0.00045297 | 2.9657e-07 | -1.1745e-06 | 0.0027241 | 0.0027245 | 0.0027245 | 0.98796 | -0.23188 | 0.98778 | -0.23533 | 0.7485
93 | -0.011415 | -0.0028591 | 0.011415 | 0.0028594 | 6.8318e-07 | 3.5822e-07 | 0.017187 | 0.017187 | 0.017187 | 0.98822 | -0.22682 | 0.98828 | -0.22556 | 4.7218
94 | 0.0018087 | 0.00045297 | -0.0018086 | -0.00045328 | 7.7522e-08 | -3.0684e-07 | 0.0027245 | 0.0027247 | 0.0027247 | 0.98778 | -0.23533 | 0.98773 | -0.23623 | 0.74853
95 | -0.016514 | -0.0041371 | 0.016516 | 0.0041383 | 1.9928e-06 | 1.1652e-06 | 0.024863 | 0.024863 | 0.024863 | 0.98828 | -0.22556 | 0.98841 | -0.22303 | 6.8306
96 | -0.021616 | -0.0054167 | 0.02162 | 0.0054186 | 3.1056e-06 | 1.8874e-06 | 0.032542 | 0.032542 | 0.032542 | 0.98841 | -0.22303 | 0.98857 | -0.22001 | 8.9402
97 | 0.044664 | 0.011221 | -0.04465 | -0.011212 | 1.4507e-05 | 9.1737e-06 | 0.067094 | 0.067094 | 0.067094 | 0.99071 | -0.17832 | 0.99036 | -0.18512 | 18.4324
98 | 0.0016589 | 0.00041569 | -0.0016589 | -0.00041576 | 1.4621e-08 | -6.9455e-08 | 0.0025077 | 0.0025077 | 0.0025077 | 0.98434 | -0.30152 | 0.98433 | -0.30171 | 0.68894
99 | -0.037658 | -0.0094504 | 0.037658 | 0.0094505 | 2.4223e-07 | 1.5244e-07 | 0.056622 | 0.056622 | 0.056622 | 0.98972 | -0.19763 | 0.98973 | -0.1975 | 15.5556
100 | 0.035215 | 0.0088382 | -0.035206 | -0.0088323 | 9.3842e-06 | 5.8912e-06 | 0.05295 | 0.05295 | 0.05295 | 0.98972 | -0.19763 | 0.98943 | -0.20322 | 14.5466
101 | -0.039742 | -0.0099727 | 0.039753 | 0.0099798 | 1.1241e-05 | 7.0864e-06 | 0.059755 | 0.059755 | 0.059755 | 0.98973 | -0.1975 | 0.99003 | -0.19157 | 16.4162
102 | 0.032453 | 0.0081422 | -0.032451 | -0.0081415 | 1.1789e-06 | 7.3755e-07 | 0.048809 | 0.048809 | 0.048809 | 0.98943 | -0.20322 | 0.98939 | -0.20399 | 13.4091
103 | -0.042196 | -0.010592 | 0.042209 | 0.0106 | 1.298e-05 | 8.1965e-06 | 0.063426 | 0.063426 | 0.063426 | 0.99003 | -0.19157 | 0.99036 | -0.18512 | 17.4247
104 | 0.031129 | 0.00781 | -0.031118 | -0.0078033 | 1.0742e-05 | 6.7069e-06 | 0.04682 | 0.04682 | 0.04682 | 0.98939 | -0.20399 | 0.98902 | -0.21123 | 12.8626
105 | 0.028363 | 0.0071129 | -0.028357 | -0.0071092 | 6.0696e-06 | 3.7705e-06 | 0.042675 | 0.042675 | 0.042675 | 0.98902 | -0.21123 | 0.98879 | -0.21572 | 11.724
106 | 0.025888 | 0.0064903 | -0.025883 | -0.0064873 | 4.8984e-06 | 3.0246e-06 | 0.03896 | 0.03896 | 0.03896 | 0.98879 | -0.21572 | 0.98858 | -0.21969 | 10.7032
107 | -0.023412 | -0.0058678 | 0.023412 | 0.005868 | 3.6256e-07 | 2.2206e-07 | 0.03524 | 0.03524 | 0.03524 | 0.98857 | -0.22001 | 0.98858 | -0.21969 | 9.6814
108 | 0.027408 | 0.0068754 | -0.027404 | -0.0068732 | 3.5252e-06 | 2.1831e-06 | 0.040933 | 0.040933 | 0.040933 | 0.99639 | -0.068945 | 0.99625 | -0.071643 | 11.2455
109 | 0.12493 | 0.031608 | -0.12479 | -0.031522 | 0.00013478 | 8.6128e-05 | 0.18731 | 0.18731 | 0.18731 | 0.99301 | -0.13366 | 0.99184 | -0.15616 | 51.4596
110 | -0.011232 | -0.0028146 | 0.011232 | 0.0028148 | 5.283e-07 | 2.7539e-07 | 0.016938 | 0.016938 | 0.016938 | 0.98671 | -0.25551 | 0.98676 | -0.25452 | 4.6534
111 | 0.0099696 | 0.0024982 | -0.0099692 | -0.002498 | 4.1948e-07 | 2.0526e-07 | 0.015035 | 0.015035 | 0.015035 | 0.98671 | -0.25551 | 0.98666 | -0.25639 | 4.1304
112 | -0.012375 | -0.0031012 | 0.012375 | 0.0031012 | 1.9822e-08 | 1.0747e-08 | 0.018661 | 0.018661 | 0.018661 | 0.98676 | -0.25452 | 0.98676 | -0.25449 | 5.1266
113 | 0.0087587 | 0.0021946 | -0.0087586 | -0.0021946 | 5.8049e-08 | 2.582e-08 | 0.013209 | 0.013209 | 0.013209 | 0.98666 | -0.25639 | 0.98665 | -0.25653 | 3.6289
114 | -0.013456 | -0.0033722 | 0.013457 | 0.0033726 | 7.5561e-07 | 4.2108e-07 | 0.020292 | 0.020292 | 0.020292 | 0.98676 | -0.25449 | 0.98682 | -0.25331 | 5.5747
115 | 0.007559 | 0.0018939 | -0.0075587 | -0.0018938 | 2.6152e-07 | 9.8839e-08 | 0.0114 | 0.0114 | 0.0114 | 0.98665 | -0.25653 | 0.98662 | -0.25726 | 3.1318
116 | -0.014547 | -0.0036459 | 0.014548 | 0.0036459 | 2.2568e-08 | 1.2846e-08 | 0.021936 | 0.021936 | 0.021936 | 0.98682 | -0.25331 | 0.98682 | -0.25328 | 6.0264
117 | 0.0065523 | 0.0016416 | -0.0065522 | -0.0016416 | 4.5022e-08 | 1.3114e-08 | 0.0098819 | 0.0098819 | 0.0098819 | 0.98662 | -0.25726 | 0.98661 | -0.2574 | 2.7148
118 | -0.015578 | -0.0039043 | 0.015579 | 0.0039049 | 1.009e-06 | 5.8347e-07 | 0.02349 | 0.02349 | 0.02349 | 0.98682 | -0.25328 | 0.98689 | -0.25192 | 6.4534
119 | 0.0053546 | 0.0013414 | -0.0053544 | -0.0013414 | 1.4192e-07 | 1.6724e-08 | 0.0080756 | 0.0080757 | 0.0080757 | 0.98661 | -0.2574 | 0.98658 | -0.25796 | 2.2186
120 | 0.022584 | 0.0056617 | -0.022582 | -0.0056607 | 1.6074e-06 | 9.8148e-07 | 0.034046 | 0.034046 | 0.034046 | 0.98708 | -0.24824 | 0.987 | -0.24974 | 9.3533
121 | 0.0080002 | 0.0020047 | -0.0079996 | -0.0020044 | 6.3815e-07 | 2.5371e-07 | 0.011958 | 0.011958 | 0.011958 | 0.9955 | -0.086201 | 0.99541 | -0.087876 | 3.2852
122 | -0.013391 | -0.0033557 | 0.013391 | 0.0033558 | 1.6065e-07 | 8.8913e-08 | 0.020016 | 0.020016 | 0.020016 | 0.9955 | -0.086201 | 0.99551 | -0.085949 | 5.4988
123 | 0.0052943 | 0.0013264 | -0.0052941 | -0.0013264 | 1.6509e-07 | 1.4292e-08 | 0.0079141 | 0.0079142 | 0.0079142 | 0.99541 | -0.087876 | 0.99538 | -0.08853 | 2.1742
124 | -0.015257 | -0.0038234 | 0.015258 | 0.0038241 | 1.2905e-06 | 7.3989e-07 | 0.022804 | 0.022804 | 0.022804 | 0.99551 | -0.085949 | 0.9956 | -0.084174 | 6.265
125 | 0.0033879 | 0.00084868 | -0.0033879 | -0.00084868 | 1.3798e-09 | -9.8129e-10 | 0.0050645 | 0.0050645 | 0.0050645 | 0.99538 | -0.08853 | 0.99538 | -0.088539 | 1.3914
126 | -0.017114 | -0.0042893 | 0.017115 | 0.0042902 | 1.5598e-06 | 9.1559e-07 | 0.025578 | 0.025578 | 0.025578 | 0.9956 | -0.084174 | 0.9957 | -0.082261 | 7.027
127 | 0.0016211 | 0.00040589 | -0.0016211 | -0.00040616 | 5.0576e-08 | -2.6613e-07 | 0.0024233 | 0.0024234 | 0.0024234 | 0.99538 | -0.088539 | 0.99534 | -0.089194 | 0.66578
128 | -0.0215 | -0.0053891 | 0.021506 | 0.0053924 | 5.4413e-06 | 3.2996e-06 | 0.032131 | 0.032131 | 0.032131 | 0.9957 | -0.082261 | 0.99598 | -0.07695 | 8.8273
129 | 0.0016211 | 0.00040616 | -0.001621 | -0.00040627 | 2.2326e-08 | -1.1746e-07 | 0.0024234 | 0.0024235 | 0.0024235 | 0.99534 | -0.089194 | 0.99533 | -0.089483 | 0.66579
130 | -0.024869 | -0.0062353 | 0.024871 | 0.0062369 | 2.6462e-06 | 1.627e-06 | 0.037155 | 0.037155 | 0.037155 | 0.99598 | -0.07695 | 0.99609 | -0.074717 | 10.2075
131 | -0.026244 | -0.0065809 | 0.026248 | 0.0065832 | 3.8455e-06 | 2.3743e-06 | 0.039206 | 0.039206 | 0.039206 | 0.99609 | -0.074717 | 0.99625 | -0.071643 | 10.7708
132 | -0.017417 | -0.0043656 | 0.017418 | 0.0043656 | 1.1771e-07 | 6.9521e-08 | 0.026262 | 0.026262 | 0.026262 | 0.98689 | -0.25192 | 0.9869 | -0.25178 | 7.2148
133 | -0.019081 | -0.0047824 | 0.019082 | 0.0047832 | 1.411e-06 | 8.4492e-07 | 0.028769 | 0.028769 | 0.028769 | 0.9869 | -0.25178 | 0.98698 | -0.25022 | 7.9036
134 | -0.02092 | -0.005244 | 0.020921 | 0.0052442 | 4.8589e-07 | 2.9432e-07 | 0.031541 | 0.031541 | 0.031541 | 0.98698 | -0.25022 | 0.987 | -0.24974 | 8.665
135 | 0.012463 | 0.0031245 | -0.012459 | -0.0031226 | 3.5283e-06 | 1.9126e-06 | 0.018721 | 0.018721 | 0.018721 | 0.99059 | -0.18087 | 0.99028 | -0.18682 | 5.1432
136 | -0.0033553 | -0.00084046 | 0.0033553 | 0.00084043 | 4.8954e-08 | -3.3757e-08 | 0.0050606 | 0.0050606 | 0.0050606 | 0.98654 | -0.25866 | 0.98656 | -0.25835 | 1.3903
137 | 0.0023164 | 0.00058009 | -0.0023164 | -0.00058012 | 1.3323e-08 | -2.864e-08 | 0.0034937 | 0.0034937 | 0.0034937 | 0.98654 | -0.25866 | 0.98654 | -0.25878 | 0.9598
138 | -0.0043549 | -0.001091 | 0.004355 | 0.0010909 | 8.0909e-08 | -1.2078e-08 | 0.0065683 | 0.0065683 | 0.0065683 | 0.98656 | -0.25835 | 0.98658 | -0.25796 | 1.8045
139 | 0.0011913 | 0.00029816 | -0.0011913 | -0.00029837 | 2.0779e-08 | -2.0584e-07 | 0.0017968 | 0.0017969 | 0.0017969 | 0.98654 | -0.25878 | 0.98652 | -0.25914 | 0.49364
140 | 0.0011913 | 0.00029837 | -0.0011913 | -0.00029857 | 2.038e-08 | -2.0186e-07 | 0.0017969 | 0.0017969 | 0.0017969 | 0.98652 | -0.25914 | 0.9865 | -0.2595 | 0.49366

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46105 | 0.11666

## res_load
| p_mw | q_mvar
0 | 0.010158 | 0.0025459
1 | 0.0079375 | 0.0019893
2 | 0.0082057 | 0.0020565
3 | 0.0040249 | 0.0010087
4 | 0.0091645 | 0.0022968
5 | 0.0035952 | 0.00090104
6 | 0.0035019 | 0.00087766
7 | 0.0027339 | 0.00068517
8 | 0.0089042 | 0.0022316
9 | 0.0036025 | 0.00090287
10 | 0.0026518 | 0.00066461
11 | 0.0027928 | 0.00069995
12 | 0.0089102 | 0.0022331
13 | 0.0036058 | 0.00090371
14 | 0.0091909 | 0.0023035
15 | 0.0071766 | 0.0017986
16 | 0.0045972 | 0.0011522
17 | 0.0014686 | 0.00036807
18 | 0.0033027 | 0.00082774
19 | 0.0046169 | 0.0011571
20 | 0.0044052 | 0.0011041
21 | 0.013609 | 0.0034107
22 | 0.0050246 | 0.0012593
23 | 0.0014712 | 0.00036872
24 | 0.0025075 | 0.00062843
25 | 0.0018881 | 0.00047321
26 | 0.00892 | 0.0022356
27 | 0.0064242 | 0.0016101
28 | 0.0056864 | 0.0014251
29 | 0.0047466 | 0.0011896
30 | 0.0063295 | 0.0015863
31 | 0.0021855 | 0.00054773
32 | 0.0041088 | 0.0010298
33 | 0.0024369 | 0.00061075
34 | 0.0014908 | 0.00037364
35 | 0.0036711 | 0.00092006
36 | 0.0053934 | 0.0013517
37 | 0.0050959 | 0.0012771
38 | 0.0025407 | 0.00063676
39 | 0.0063119 | 0.0015819
40 | 0.00098801 | 0.00024762
41 | 0.0044847 | 0.001124
42 | 0.0051432 | 0.001289
43 | 0.007226 | 0.001811
44 | 0.0018914 | 0.00047402
45 | 0.0017514 | 0.00043894
46 | 0.0018894 | 0.00047354
47 | 0.012138 | 0.0030422
48 | 0.0026912 | 0.00067447
49 | 0.0029028 | 0.00072751
50 | 0.0029321 | 0.00073486
51 | 0.0040008 | 0.0010027
52 | 0.0031995 | 0.00080187
53 | 0.0059276 | 0.0014856
54 | 0.0035464 | 0.0008888
55 | 0.0016282 | 0.00040807
56 | 0.0023232 | 0.00058225
57 | 0.0038651 | 0.00096868
58 | 0.0045108 | 0.0011305
59 | 0.0092387 | 0.0023154
60 | 0.0070666 | 0.0017711
61 | 0.0059355 | 0.0014876
62 | 0.001836 | 0.00046014
63 | 0.0018367 | 0.00046032
64 | 0.0017009 | 0.00042628
65 | 0.0022541 | 0.00056492
66 | 0.0016634 | 0.0004169
67 | 0.0063651 | 0.0015952
68 | 0.0032391 | 0.0008118
69 | 0.0050982 | 0.0012777
70 | 0.0023009 | 0.00057667
71 | 0.0018086 | 0.00045328
72 | 0.0051008 | 0.0012784
73 | 0.0024401 | 0.00061156
74 | 0.0082794 | 0.002075
75 | 0.0016743 | 0.00041963
76 | 0.0024428 | 0.00061222
77 | 0.0020836 | 0.00052221
78 | 0.0027532 | 0.00069002
79 | 0.0024426 | 0.00061217
80 | 0.0013226 | 0.00033148
81 | 0.0024412 | 0.00061181
82 | 0.0027547 | 0.00069039
83 | 0.0024692 | 0.00061884
84 | 0.0017923 | 0.0004492
85 | 0.002471 | 0.00061928
86 | 0.00097602 | 0.00024461
87 | 0.0018457 | 0.00046257
88 | 0.0012622 | 0.00031635
89 | 0.0011425 | 0.00028633
90 | 0.0012105 | 0.00030339
91 | 0.0010815 | 0.00027105
92 | 0.0011996 | 0.00030066
93 | 0.0010904 | 0.00027328
94 | 0.0010064 | 0.00025224
95 | 0.0010309 | 0.00025836
96 | 0.0011976 | 0.00030016
97 | 0.0043918 | 0.0011007
98 | 0.0018389 | 0.00046088
99 | 0.0053905 | 0.001351
100 | 0.0027053 | 0.00067801
101 | 0.0018658 | 0.00046762
102 | 0.0019062 | 0.00047774
103 | 0.0018559 | 0.00046514
104 | 0.0017668 | 0.00044279
105 | 0.0043849 | 0.001099
106 | 0.0033628 | 0.00084281
107 | 0.0013725 | 0.00034398
108 | 0.0011568 | 0.00028993
109 | 0.0018927 | 0.00047435
110 | 0.0016589 | 0.00041576
111 | 0.001621 | 0.00040627
112 | 0.0018381 | 0.00046067
113 | 0.0016629 | 0.00041677
114 | 0.0018383 | 0.00046072
115 | 0.0016618 | 0.00041648
116 | 0.012152 | 0.0030456
117 | 0.012459 | 0.0031226
118 | 0.0010389 | 0.00026037
119 | 0.00099961 | 0.00025053
120 | 0.001125 | 0.00028196
121 | 0.00099941 | 0.00025048
122 | 0.0011913 | 0.00029857

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1