## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-201_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-201_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-201_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-201_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-201_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-201_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_2701-201_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_2701-201_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2701-201_0_4_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_2701-201_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2701-201_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2701-201_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_2701-201_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2701-201_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2701-201_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_2701-201_0_4_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_2701-201_0_4_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_2701-201_0_4_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_2701-201_0_4_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_2701-201_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2701-201_0_4_node_36 | 0.4 | n |  | TRUE
21 | bus_LV_2701-201_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2701-201_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2701-201_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_2701-201_0_4_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_2701-201_0_4_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_2701-201_0_4_node_48 | 0.4 | n |  | TRUE
27 | bus_LV_2701-201_0_4_node_47 | 0.4 | n |  | TRUE
28 | bus_LV_2701-201_0_4_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_2701-201_0_4_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_2701-201_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_2701-201_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_2701-201_0_4_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_2701-201_0_4_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_2701-201_0_4_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_2701-201_0_4_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_2701-201_0_4_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_2701-201_0_4_node_38 | 0.4 | n |  | TRUE
38 | bus_LV_2701-201_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_2701-201_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_2701-201_0_4_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_2701-201_0_4_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_2701-201_0_4_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_2701-201_0_4_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_2701-201_0_4_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_2701-201_0_4_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_2701-201_0_4_node_46 | 0.4 | n |  | TRUE
47 | bus_MV_556_0_node_43 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-201_0_4_load_0 | 0 | 0.0053347 | 0.001337 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-201_0_4_load_1 | 1 | 0.0040543 | 0.0010161 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-201_0_4_load_2 | 2 | 0.0047157 | 0.0011819 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-201_0_4_load_3 | 3 | 0.01028 | 0.0025765 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-201_0_4_load_4 | 4 | 0.0078269 | 0.0019616 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-201_0_4_load_7 | 5 | 0.0046589 | 0.0011676 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-201_0_4_load_13 | 6 | 0.0076868 | 0.0019265 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-201_0_4_load_5 | 7 | 0.0067941 | 0.0017028 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-201_0_4_load_14 | 8 | 0.0063945 | 0.0016026 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-201_0_4_load_6 | 9 | 0.004761 | 0.0011932 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-201_0_4_load_8 | 10 | 0.0040488 | 0.0010147 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-201_0_4_load_11 | 11 | 0.003654 | 0.00091579 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-201_0_4_load_9 | 12 | 0.0036478 | 0.00091423 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-201_0_4_load_10 | 13 | 0.079135 | 0.019833 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-201_0_4_load_37 | 15 | 0.021525 | 0.0053946 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-201_0_4_load_35 | 17 | 0.027911 | 0.0069952 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-201_0_4_load_16 | 19 | 0.0062821 | 0.0015744 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-201_0_4_load_36 | 20 | 0.0083612 | 0.0020955 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-201_0_4_load_15 | 21 | 0.010049 | 0.0025185 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-201_0_4_load_17 | 22 | 0.0044901 | 0.0011253 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-201_0_4_load_32 | 24 | 0.0098844 | 0.0024773 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-201_0_4_load_33 | 25 | 0.010087 | 0.002528 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-201_0_4_load_48 | 26 | 0.0094706 | 0.0023735 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-201_0_4_load_47 | 27 | 0.008213 | 0.0020584 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-201_0_4_load_31 | 28 | 0.0063786 | 0.0015986 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-201_0_4_load_30 | 29 | 0.0063731 | 0.0015972 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-201_0_4_load_23 | 30 | 0.0033058 | 0.00082851 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-201_0_4_load_24 | 31 | 0.0050805 | 0.0012733 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-201_0_4_load_25 | 32 | 0.0060344 | 0.0015124 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-201_0_4_load_26 | 33 | 0.0094321 | 0.0023639 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-201_0_4_load_27 | 34 | 0.0025933 | 0.00064994 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-201_0_4_load_39 | 35 | 0.0050738 | 0.0012716 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-201_0_4_load_28 | 36 | 0.0030262 | 0.00075844 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-201_0_4_load_38 | 37 | 0.0085367 | 0.0021395 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-201_0_4_load_29 | 38 | 0.0025942 | 0.00065016 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-201_0_4_load_34 | 39 | 0.0085402 | 0.0021404 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-201_0_4_load_40 | 40 | 0.012392 | 0.0031057 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-201_0_4_load_41 | 41 | 0.027937 | 0.0070016 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-201_0_4_load_42 | 42 | 0.027943 | 0.0070033 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-201_0_4_load_43 | 43 | 0.0087312 | 0.0021882 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-201_0_4_load_44 | 44 | 0.011687 | 0.0029291 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2701-201_0_4_load_45 | 45 | 0.0090777 | 0.0022751 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2701-201_0_4_load_46 | 46 | 0.010161 | 0.0025467 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 41 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-201_0_4_line_0 |  | 0 | 1 | 0.00013302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2701-201_0_4_line_1 |  | 0 | 2 | 0.0056584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2701-201_0_4_line_2 |  | 1 | 3 | 0.0056063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2701-201_0_4_line_3 |  | 2 | 4 | 0.0052644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2701-201_0_4_line_4 |  | 3 | 5 | 0.0030897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_2701-201_0_4_line_5 |  | 4 | 6 | 0.00028794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2701-201_0_4_line_6 |  | 5 | 7 | 0.0034388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2701-201_0_4_line_7 |  | 6 | 8 | 0.0027684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2701-201_0_4_line_8 |  | 7 | 9 | 0.0048803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_2701-201_0_4_line_9 |  | 8 | 21 | 0.0016417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2701-201_0_4_line_10 |  | 9 | 10 | 0.0072043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2701-201_0_4_line_11 |  | 10 | 11 | 0.006424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2701-201_0_4_line_12 |  | 11 | 12 | 0.0066297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2701-201_0_4_line_13 |  | 12 | 13 | 0.00088484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2701-201_0_4_line_14 |  | 13 | 14 | 0.047701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-201_0_4_line_15 |  | 14 | 15 | 0.033827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-201_0_4_line_16 |  | 15 | 20 | 0.030981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-201_0_4_line_17 |  | 16 | 17 | 0.01017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2701-201_0_4_line_18 |  | 16 | 18 | 0.023905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2701-201_0_4_line_19 |  | 17 | 23 | 0.021286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2701-201_0_4_line_20 |  | 18 | 19 | 0.035992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2701-201_0_4_line_21 |  | 19 | 22 | 0.0011846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2701-201_0_4_line_22 |  | 20 | 37 | 0.011844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-201_0_4_line_23 |  | 21 | 22 | 0.0069317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2701-201_0_4_line_24 |  | 23 | 24 | 0.007669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_2701-201_0_4_line_25 |  | 24 | 25 | 0.0058617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2701-201_0_4_line_26 |  | 25 | 39 | 0.0059825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2701-201_0_4_line_27 |  | 26 | 27 | 0.0089924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-201_0_4_line_28 |  | 27 | 46 | 0.0091447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-201_0_4_line_29 |  | 28 | 29 | 0.013796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-201_0_4_line_30 |  | 29 | 38 | 0.0060717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-201_0_4_line_31 |  | 30 | 31 | 0.0061286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-201_0_4_line_32 |  | 30 | 32 | 0.0029519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-201_0_4_line_33 |  | 31 | 33 | 0.0069072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-201_0_4_line_34 |  | 32 | 34 | 0.0057147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-201_0_4_line_35 |  | 33 | 35 | 0.0018217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-201_0_4_line_36 |  | 34 | 36 | 0.0025158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-201_0_4_line_37 |  | 35 | 37 | 0.010854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-201_0_4_line_38 |  | 36 | 38 | 0.0053574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2701-201_0_4_line_39 |  | 39 | 40 | 0.0020984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2701-201_0_4_line_40 |  | 40 | 41 | 0.015853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2701-201_0_4_line_41 |  | 41 | 42 | 0.024076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-201_0_4_line_42 |  | 42 | 43 | 0.010814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-201_0_4_line_43 |  | 43 | 44 | 0.0047887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-201_0_4_line_44 |  | 44 | 45 | 0.0048666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2701-201_0_4_line_45 |  | 45 | 46 | 0.0088362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-201_0_4_trafo_41 | 0.63 MVA 20/0.4 kV | 47 | 41 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2610247.5151 | 1267964.0968 | 2610247.4187 | 1267964.0051
1 | 2610247.4187 | 1267964.0051 | 2610243.3192 | 1267960.1049
2 | 2610247.5151 | 1267964.0968 | 2610251.5768 | 1267967.9611
3 | 2610243.3192 | 1267960.1049 | 2610239.5051 | 1267956.4763
4 | 2610251.5768 | 1267967.9611 | 2610253.8153 | 1267970.0907
5 | 2610239.5051 | 1267956.4763 | 2610239.2965 | 1267956.2779
6 | 2610256.3067 | 1267972.4611 | 2610253.8153 | 1267970.0907
7 | 2610237.2908 | 1267954.3697 | 2610239.2965 | 1267956.2779
8 | 2610256.3067 | 1267972.4611 | 2610259.8425 | 1267975.8249
9 | 2610237.2908 | 1267954.3697 | 2610236.1014 | 1267953.2381
10 | 2610259.8425 | 1267975.8249 | 2610265.062 | 1267980.7907
11 | 2610265.062 | 1267980.7907 | 2610269.7162 | 1267985.2186
12 | 2610274.5194 | 1267989.7884 | 2610269.7162 | 1267985.2186
13 | 2610275.1605 | 1267990.3983 | 2610274.5194 | 1267989.7884
14 | 2610309.7195 | 1268023.2772 | 2610275.1605 | 1267990.3983
15 | 2610309.7195 | 1268023.2772 | 2610289.5803 | 1268050.4555
16 | 2610271.1356 | 1268075.3471 | 2610289.5803 | 1268050.4555
17 | 2610186.6976 | 1267937.9497 | 2610184.5782 | 1267947.8968
18 | 2610204.0934 | 1267922.8912 | 2610200.0977 | 1267926.8983 | 2610194.925 | 1267928.3126 | 2610192.8432 | 1267930.9776 | 2610189.9373 | 1267935.8761 | 2610186.6976 | 1267937.9497
19 | 2610180.1425 | 1267968.7157 | 2610184.5782 | 1267947.8968
20 | 2610204.0934 | 1267922.8912 | 2610205.972 | 1267924.5734 | 2610230.2211 | 1267947.6437
21 | 2610231.0794 | 1267948.4602 | 2610230.2211 | 1267947.6437
22 | 2610271.1356 | 1268075.3471 | 2610264.0842 | 1268084.8632
23 | 2610236.1014 | 1267953.2381 | 2610231.0794 | 1267948.4602
24 | 2610180.1425 | 1267968.7157 | 2610181.7335 | 1267976.2178
25 | 2610181.7335 | 1267976.2178 | 2610182.9495 | 1267981.952 | 2610182.9495 | 1267981.952
26 | 2610182.9495 | 1267981.952 | 2610181.8225 | 1267987.8274
27 | 2610166.6615 | 1268066.8643 | 2610164.9675 | 1268075.6957
28 | 2610168.3843 | 1268057.8833 | 2610166.6615 | 1268066.8643
29 | 2610235.3146 | 1268123.6885 | 2610227.1008 | 1268134.7733
30 | 2610238.9294 | 1268118.8102 | 2610235.3146 | 1268123.6885
31 | 2610248.7766 | 1268105.5211 | 2610252.4254 | 1268100.5971
32 | 2610248.7766 | 1268105.5211 | 2610247.0192 | 1268107.8929
33 | 2610252.4254 | 1268100.5971 | 2610256.5377 | 1268095.0474
34 | 2610243.6168 | 1268112.4844 | 2610247.0192 | 1268107.8929
35 | 2610257.6222 | 1268093.5838 | 2610256.5377 | 1268095.0474
36 | 2610243.6168 | 1268112.4844 | 2610242.119 | 1268114.5057
37 | 2610264.0842 | 1268084.8632 | 2610257.6222 | 1268093.5838
38 | 2610238.9294 | 1268118.8102 | 2610242.119 | 1268114.5057
39 | 2610181.4272 | 1267989.8882 | 2610181.8225 | 1267987.8274
40 | 2610181.4272 | 1267989.8882 | 2610178.4406 | 1268005.4578
41 | 2610178.4406 | 1268005.4578 | 2610173.905 | 1268029.1029
42 | 2610173.905 | 1268029.1029 | 2610171.8678 | 1268039.7229
43 | 2610171.8678 | 1268039.7229 | 2610170.9657 | 1268044.4259
44 | 2610170.9657 | 1268044.4259 | 2610170.0489 | 1268049.2053
45 | 2610170.0489 | 1268049.2053 | 2610168.3843 | 1268057.8833

## bus_geodata
| x | y | coords
0 | 2610247.4187 | 1267964.0051
1 | 2610247.5151 | 1267964.0968
2 | 2610243.3192 | 1267960.1049
3 | 2610251.5768 | 1267967.9611
4 | 2610239.5051 | 1267956.4763
5 | 2610253.8153 | 1267970.0907
6 | 2610239.2965 | 1267956.2779
7 | 2610256.3067 | 1267972.4611
8 | 2610237.2908 | 1267954.3697
9 | 2610259.8425 | 1267975.8249
10 | 2610265.062 | 1267980.7907
11 | 2610269.7162 | 1267985.2186
12 | 2610274.5194 | 1267989.7883
13 | 2610275.1605 | 1267990.3983
14 | 2610309.7195 | 1268023.2772
15 | 2610289.5803 | 1268050.4555
16 | 2610186.6976 | 1267937.9497
17 | 2610184.5782 | 1267947.8968
18 | 2610204.0934 | 1267922.8912
19 | 2610230.2211 | 1267947.6437
20 | 2610271.1356 | 1268075.3471
21 | 2610236.1014 | 1267953.2381
22 | 2610231.0794 | 1267948.4602
23 | 2610180.1425 | 1267968.7157
24 | 2610181.7335 | 1267976.2178
25 | 2610182.9495 | 1267981.952
26 | 2610164.9675 | 1268075.6957
27 | 2610166.6615 | 1268066.8643
28 | 2610227.1008 | 1268134.7733
29 | 2610235.3146 | 1268123.6885
30 | 2610248.7766 | 1268105.5211
31 | 2610252.4254 | 1268100.5971
32 | 2610247.0192 | 1268107.8929
33 | 2610256.5377 | 1268095.0474
34 | 2610243.6168 | 1268112.4844
35 | 2610257.6222 | 1268093.5838
36 | 2610242.119 | 1268114.5057
37 | 2610264.0842 | 1268084.8632
38 | 2610238.9294 | 1268118.8102
39 | 2610181.8225 | 1267987.8274
40 | 2610181.4272 | 1267989.8882
41 | 2610178.4406 | 1268005.4578
42 | 2610173.905 | 1268029.1029
43 | 2610171.8678 | 1268039.7229
44 | 2610170.9657 | 1268044.4259
45 | 2610170.0489 | 1268049.2053
46 | 2610168.3843 | 1268057.8833
47 | 2610180.1425 | 1267968.7157

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98713 | -0.24614 | 0.0053347 | 0.001337
1 | 0.98713 | -0.24631 | 0.0040543 | 0.0010161
2 | 0.98751 | -0.2389 | 0.0047157 | 0.0011819
3 | 0.98677 | -0.25318 | 0.01028 | 0.0025765
4 | 0.98786 | -0.23203 | 0.0078269 | 0.0019616
5 | 0.98659 | -0.25677 | 0.0046589 | 0.0011676
6 | 0.98788 | -0.23164 | 0.0076868 | 0.0019265
7 | 0.98638 | -0.26068 | 0.0067941 | 0.0017028
8 | 0.98808 | -0.22777 | 0.0063945 | 0.0016026
9 | 0.98611 | -0.26603 | 0.004761 | 0.0011932
10 | 0.98571 | -0.27373 | 0.0040488 | 0.0010147
11 | 0.98536 | -0.28045 | 0.003654 | 0.00091579
12 | 0.98501 | -0.28724 | 0.0036478 | 0.00091423
13 | 0.98495 | -0.28857 | 0.079135 | 0.019833
14 | 0.98103 | -0.36456 | 0 | 0
15 | 0.97825 | -0.41882 | 0.021525 | 0.0053946
16 | 0.99367 | -0.12041 | 0 | 0
17 | 0.99449 | -0.10473 | 0.027911 | 0.0069952
18 | 0.99174 | -0.15735 | 0 | 0
19 | 0.98884 | -0.21325 | 0.0062821 | 0.0015744
20 | 0.97633 | -0.45658 | 0.0083612 | 0.0020955
21 | 0.98821 | -0.22541 | 0.010049 | 0.0025185
22 | 0.98874 | -0.21505 | 0.0044901 | 0.0011253
23 | 0.99639 | -0.06853 | 0 | 0
24 | 0.99707 | -0.055521 | 0.0098844 | 0.0024773
25 | 0.99761 | -0.045252 | 0.010087 | 0.002528
26 | 0.99675 | -0.062581 | 0.0094706 | 0.0023735
27 | 0.99682 | -0.061087 | 0.008213 | 0.0020584
28 | 0.97424 | -0.4976 | 0.0063786 | 0.0015986
29 | 0.97433 | -0.49599 | 0.0063731 | 0.0015972
30 | 0.9747 | -0.48855 | 0.0033058 | 0.00082851
31 | 0.97488 | -0.48514 | 0.0050805 | 0.0012733
32 | 0.97463 | -0.49001 | 0.0060344 | 0.0015124
33 | 0.9751 | -0.48066 | 0.0094321 | 0.0023639
34 | 0.97452 | -0.49221 | 0.0025933 | 0.00064994
35 | 0.97518 | -0.47916 | 0.0050738 | 0.0012716
36 | 0.97448 | -0.49306 | 0.0030262 | 0.00075844
37 | 0.97568 | -0.46924 | 0.0085367 | 0.0021395
38 | 0.9744 | -0.49457 | 0.0025942 | 0.00065016
39 | 0.99818 | -0.03443 | 0.0085402 | 0.0021404
40 | 0.99839 | -0.030533 | 0.012392 | 0.0031057
41 | 1 | 0 | -0.42253 | -0.10728
42 | 0.99813 | -0.035856 | 0.027943 | 0.0070033
43 | 0.99757 | -0.04671 | 0.0087312 | 0.0021882
44 | 0.99736 | -0.050788 | 0.011687 | 0.0029291
45 | 0.99719 | -0.053937 | 0.0090777 | 0.0022751
46 | 0.99697 | -0.058251 | 0.010161 | 0.0025467
47 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.21048 | 0.053189 | -0.21048 | -0.053188 | 1.6756e-06 | 1.0673e-06 | 0.31744 | 0.31744 | 0.31744 | 0.98713 | -0.24614 | 0.98713 | -0.24631 | 29.0696
1 | -0.21582 | -0.054526 | 0.21589 | 0.054574 | 7.493e-05 | 4.7738e-05 | 0.32548 | 0.32548 | 0.32548 | 0.98713 | -0.24614 | 0.98751 | -0.2389 | 29.806
2 | 0.20643 | 0.052172 | -0.20636 | -0.052129 | 6.7924e-05 | 4.3256e-05 | 0.31133 | 0.31133 | 0.31133 | 0.98713 | -0.24631 | 0.98677 | -0.25318 | 28.5099
3 | -0.22061 | -0.055756 | 0.22068 | 0.055802 | 7.2789e-05 | 4.6383e-05 | 0.33259 | 0.33259 | 0.33259 | 0.98751 | -0.2389 | 0.98786 | -0.23203 | 30.4567
4 | 0.19608 | 0.049552 | -0.19604 | -0.049531 | 3.3799e-05 | 2.1513e-05 | 0.29583 | 0.29583 | 0.29583 | 0.98677 | -0.25318 | 0.98659 | -0.25677 | 27.0903
5 | -0.22851 | -0.057764 | 0.22851 | 0.057767 | 4.2686e-06 | 2.7208e-06 | 0.34438 | 0.34438 | 0.34438 | 0.98786 | -0.23203 | 0.98788 | -0.23164 | 31.5363
6 | 0.19139 | 0.048363 | -0.19135 | -0.04834 | 3.5852e-05 | 2.2814e-05 | 0.2888 | 0.2888 | 0.2888 | 0.98659 | -0.25677 | 0.98638 | -0.26068 | 26.4468
7 | -0.2362 | -0.059693 | 0.23624 | 0.059721 | 4.3846e-05 | 2.7955e-05 | 0.35596 | 0.35596 | 0.35596 | 0.98788 | -0.23164 | 0.98808 | -0.22777 | 32.5966
8 | 0.18456 | 0.046638 | -0.18451 | -0.046608 | 4.7333e-05 | 3.0106e-05 | 0.27855 | 0.27855 | 0.27855 | 0.98638 | -0.26068 | 0.98611 | -0.26603 | 25.5082
9 | -0.24264 | -0.061324 | 0.24266 | 0.061341 | 2.7428e-05 | 1.7491e-05 | 0.36558 | 0.36558 | 0.36558 | 0.98808 | -0.22777 | 0.98821 | -0.22541 | 33.4785
10 | 0.17975 | 0.045414 | -0.17968 | -0.045372 | 6.6315e-05 | 4.2166e-05 | 0.27137 | 0.27137 | 0.27137 | 0.98611 | -0.26603 | 0.98571 | -0.27373 | 24.8503
11 | 0.17563 | 0.044357 | -0.17558 | -0.044322 | 5.6499e-05 | 3.5914e-05 | 0.26525 | 0.26525 | 0.26525 | 0.98571 | -0.27373 | 0.98536 | -0.28045 | 24.2907
12 | 0.17192 | 0.043406 | -0.17187 | -0.04337 | 5.5907e-05 | 3.5528e-05 | 0.25974 | 0.25974 | 0.25974 | 0.98536 | -0.28045 | 0.98501 | -0.28724 | 23.7853
13 | 0.16822 | 0.042456 | -0.16821 | -0.042449 | 1.0723e-05 | 6.84e-06 | 0.25423 | 0.25423 | 0.25423 | 0.98501 | -0.28724 | 0.98495 | -0.28857 | 34.9211
14 | 0.089072 | 0.022616 | -0.088747 | -0.022409 | 0.00032442 | 0.00020702 | 0.13467 | 0.13467 | 0.13467 | 0.98495 | -0.28857 | 0.98103 | -0.36456 | 36.9976
15 | 0.088747 | 0.022409 | -0.088517 | -0.022262 | 0.00023006 | 0.00014681 | 0.13467 | 0.13467 | 0.13467 | 0.98103 | -0.36456 | 0.97825 | -0.41882 | 36.9976
16 | 0.066992 | 0.016867 | -0.066872 | -0.016791 | 0.00012071 | 7.6863e-05 | 0.10193 | 0.10193 | 0.10193 | 0.97825 | -0.41882 | 0.97633 | -0.45658 | 28.0028
17 | -0.26481 | -0.067406 | 0.26501 | 0.067534 | 0.00020029 | 0.00012779 | 0.39693 | 0.39693 | 0.39693 | 0.99367 | -0.12041 | 0.99449 | -0.10473 | 36.3485
18 | 0.26481 | 0.067406 | -0.26434 | -0.067106 | 0.00047078 | 0.00030037 | 0.39693 | 0.39693 | 0.39693 | 0.99367 | -0.12041 | 0.99174 | -0.15735 | 36.3486
19 | -0.29292 | -0.074529 | 0.29344 | 0.074856 | 0.00051206 | 0.00032689 | 0.43869 | 0.43869 | 0.43869 | 0.99449 | -0.10473 | 0.99639 | -0.06853 | 40.1729
20 | 0.26434 | 0.067106 | -0.26363 | -0.066654 | 0.00070882 | 0.00045226 | 0.39693 | 0.39693 | 0.39693 | 0.99174 | -0.15735 | 0.98884 | -0.21325 | 36.3486
21 | 0.25735 | 0.065079 | -0.25733 | -0.065065 | 2.2231e-05 | 1.4182e-05 | 0.38747 | 0.38747 | 0.38747 | 0.98884 | -0.21325 | 0.98874 | -0.21505 | 35.4829
22 | 0.058511 | 0.014695 | -0.058475 | -0.014673 | 3.5329e-05 | 2.2462e-05 | 0.089187 | 0.089187 | 0.089187 | 0.97633 | -0.45658 | 0.97568 | -0.46924 | 24.5019
23 | -0.25271 | -0.06386 | 0.25284 | 0.06394 | 0.00012559 | 8.011e-05 | 0.38072 | 0.38072 | 0.38072 | 0.98821 | -0.22541 | 0.98874 | -0.21505 | 34.8641
24 | -0.29344 | -0.074856 | 0.29362 | 0.074974 | 0.00018449 | 0.00011777 | 0.43869 | 0.43869 | 0.43869 | 0.99639 | -0.06853 | 0.99707 | -0.055521 | 40.1728
25 | -0.30351 | -0.077451 | 0.30366 | 0.077547 | 0.00015065 | 9.6186e-05 | 0.45344 | 0.45344 | 0.45344 | 0.99707 | -0.055521 | 0.99761 | -0.045252 | 41.5237
26 | -0.31374 | -0.080075 | 0.31391 | 0.08018 | 0.00016413 | 0.00010481 | 0.46848 | 0.46848 | 0.46848 | 0.99761 | -0.045252 | 0.99818 | -0.03443 | 42.9014
27 | -0.0094706 | -0.0023735 | 0.0094712 | 0.0023739 | 6.7406e-07 | 3.1418e-07 | 0.014138 | 0.014138 | 0.014138 | 0.99675 | -0.062581 | 0.99682 | -0.061087 | 3.8842
28 | -0.017684 | -0.0044322 | 0.017687 | 0.0044336 | 2.3898e-06 | 1.4102e-06 | 0.026398 | 0.026398 | 0.026398 | 0.99682 | -0.061087 | 0.99697 | -0.058251 | 7.2523
29 | -0.0063786 | -0.0015986 | 0.0063791 | 0.0015988 | 4.9105e-07 | 1.4246e-07 | 0.0097424 | 0.0097423 | 0.0097424 | 0.97424 | -0.4976 | 0.97433 | -0.49599 | 2.6765
30 | -0.012752 | -0.003196 | 0.012753 | 0.0031965 | 8.636e-07 | 4.7708e-07 | 0.019475 | 0.019475 | 0.019475 | 0.97433 | -0.49599 | 0.9744 | -0.49457 | 5.3504
31 | -0.030313 | -0.0075995 | 0.030318 | 0.0076026 | 4.9219e-06 | 3.0736e-06 | 0.046278 | 0.046278 | 0.046278 | 0.9747 | -0.48855 | 0.97488 | -0.48514 | 12.7136
32 | 0.027007 | 0.006771 | -0.027005 | -0.0067698 | 1.8818e-06 | 1.1676e-06 | 0.041231 | 0.041231 | 0.041231 | 0.9747 | -0.48855 | 0.97463 | -0.49001 | 11.3272
33 | -0.035398 | -0.0088759 | 0.035406 | 0.0088806 | 7.5621e-06 | 4.7536e-06 | 0.054032 | 0.054032 | 0.054032 | 0.97488 | -0.48514 | 0.9751 | -0.48066 | 14.844
34 | 0.020971 | 0.0052575 | -0.020969 | -0.0052561 | 2.1969e-06 | 1.3348e-06 | 0.032018 | 0.032018 | 0.032018 | 0.97463 | -0.49001 | 0.97452 | -0.49221 | 8.7961
35 | -0.044838 | -0.011245 | 0.044841 | 0.011247 | 3.1984e-06 | 2.0243e-06 | 0.068426 | 0.068426 | 0.068426 | 0.9751 | -0.48066 | 0.97518 | -0.47916 | 18.7982
36 | 0.018375 | 0.0046062 | -0.018375 | -0.0046057 | 7.4271e-07 | 4.4399e-07 | 0.028058 | 0.028058 | 0.028058 | 0.97452 | -0.49221 | 0.97448 | -0.49306 | 7.7083
37 | -0.049915 | -0.012518 | 0.049939 | 0.012533 | 2.3613e-05 | 1.4977e-05 | 0.076168 | 0.076168 | 0.076168 | 0.97518 | -0.47916 | 0.97568 | -0.46924 | 20.9252
38 | 0.015348 | 0.0038473 | -0.015347 | -0.0038467 | 1.1035e-06 | 6.3953e-07 | 0.023437 | 0.023437 | 0.023437 | 0.97448 | -0.49306 | 0.9744 | -0.49457 | 6.4388
39 | -0.32245 | -0.082321 | 0.32251 | 0.082359 | 6.0739e-05 | 3.8791e-05 | 0.48121 | 0.48121 | 0.48121 | 0.99818 | -0.03443 | 0.99839 | -0.030533 | 44.0672
40 | -0.3349 | -0.085465 | 0.33539 | 0.085781 | 0.00049479 | 0.00031604 | 0.49968 | 0.49968 | 0.49968 | 0.99839 | -0.030533 | 1 | 0 | 45.7585
41 | 0.085484 | 0.021501 | -0.085338 | -0.021408 | 0.00014615 | 9.3219e-05 | 0.12723 | 0.12723 | 0.12723 | 1 | 0 | 0.99813 | -0.035856 | 34.953
42 | 0.057395 | 0.014405 | -0.057365 | -0.014386 | 2.9693e-05 | 1.8862e-05 | 0.085571 | 0.085571 | 0.085571 | 0.99813 | -0.035856 | 0.99757 | -0.04671 | 23.5085
43 | 0.048634 | 0.012198 | -0.048624 | -0.012192 | 9.4513e-06 | 5.9864e-06 | 0.072547 | 0.072547 | 0.072547 | 0.99757 | -0.04671 | 0.99736 | -0.050788 | 19.9306
44 | 0.036937 | 0.0092624 | -0.036931 | -0.009259 | 5.5427e-06 | 3.4838e-06 | 0.05511 | 0.05511 | 0.05511 | 0.99736 | -0.050788 | 0.99719 | -0.053937 | 15.1402
45 | 0.027854 | 0.0069839 | -0.027848 | -0.0069803 | 5.7246e-06 | 3.5485e-06 | 0.041565 | 0.041565 | 0.041565 | 0.99719 | -0.053937 | 0.99697 | -0.058251 | 11.4188

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45047 | 0.11428

## res_load
| p_mw | q_mvar
0 | 0.0053347 | 0.001337
1 | 0.0040543 | 0.0010161
2 | 0.0047157 | 0.0011819
3 | 0.01028 | 0.0025765
4 | 0.0078269 | 0.0019616
5 | 0.0046589 | 0.0011676
6 | 0.0076868 | 0.0019265
7 | 0.0067941 | 0.0017028
8 | 0.0063945 | 0.0016026
9 | 0.004761 | 0.0011932
10 | 0.0040488 | 0.0010147
11 | 0.003654 | 0.00091579
12 | 0.0036478 | 0.00091423
13 | 0.079135 | 0.019833
14 | 0.021525 | 0.0053946
15 | 0.027911 | 0.0069952
16 | 0.0062821 | 0.0015744
17 | 0.0083612 | 0.0020955
18 | 0.010049 | 0.0025185
19 | 0.0044901 | 0.0011253
20 | 0.0098844 | 0.0024773
21 | 0.010087 | 0.002528
22 | 0.0094706 | 0.0023735
23 | 0.008213 | 0.0020584
24 | 0.0063786 | 0.0015986
25 | 0.0063731 | 0.0015972
26 | 0.0033058 | 0.00082851
27 | 0.0050805 | 0.0012733
28 | 0.0060344 | 0.0015124
29 | 0.0094321 | 0.0023639
30 | 0.0025933 | 0.00064994
31 | 0.0050738 | 0.0012716
32 | 0.0030262 | 0.00075844
33 | 0.0085367 | 0.0021395
34 | 0.0025942 | 0.00065016
35 | 0.0085402 | 0.0021404
36 | 0.012392 | 0.0031057
37 | 0.027937 | 0.0070016
38 | 0.027943 | 0.0070033
39 | 0.0087312 | 0.0021882
40 | 0.011687 | 0.0029291
41 | 0.0090777 | 0.0022751
42 | 0.010161 | 0.0025467

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1