## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-226_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-226_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-226_0_6_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_2701-226_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-226_0_6_node_113 | 0.4 | n |  | TRUE
5 | bus_LV_2701-226_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2701-226_0_6_node_50 | 0.4 | n |  | TRUE
7 | bus_LV_2701-226_0_6_node_92 | 0.4 | n |  | TRUE
8 | bus_LV_2701-226_0_6_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_2701-226_0_6_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2701-226_0_6_node_84 | 0.4 | n |  | TRUE
11 | bus_LV_2701-226_0_6_node_124 | 0.4 | n |  | TRUE
12 | bus_LV_2701-226_0_6_node_65 | 0.4 | n |  | TRUE
13 | bus_LV_2701-226_0_6_node_52 | 0.4 | n |  | TRUE
14 | bus_LV_2701-226_0_6_node_48 | 0.4 | n |  | TRUE
15 | bus_LV_2701-226_0_6_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_2701-226_0_6_node_83 | 0.4 | n |  | TRUE
17 | bus_LV_2701-226_0_6_node_125 | 0.4 | n |  | TRUE
18 | bus_LV_2701-226_0_6_node_123 | 0.4 | n |  | TRUE
19 | bus_LV_2701-226_0_6_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_2701-226_0_6_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_2701-226_0_6_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2701-226_0_6_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_2701-226_0_6_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_2701-226_0_6_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_2701-226_0_6_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_2701-226_0_6_node_112 | 0.4 | n |  | TRUE
27 | bus_LV_2701-226_0_6_node_118 | 0.4 | n |  | TRUE
28 | bus_LV_2701-226_0_6_node_39 | 0.4 | n |  | TRUE
29 | bus_LV_2701-226_0_6_node_110 | 0.4 | n |  | TRUE
30 | bus_LV_2701-226_0_6_node_116 | 0.4 | n |  | TRUE
31 | bus_LV_2701-226_0_6_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_2701-226_0_6_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_2701-226_0_6_node_42 | 0.4 | n |  | TRUE
34 | bus_LV_2701-226_0_6_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_2701-226_0_6_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_2701-226_0_6_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_2701-226_0_6_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_2701-226_0_6_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_2701-226_0_6_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_2701-226_0_6_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_2701-226_0_6_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_2701-226_0_6_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2701-226_0_6_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_2701-226_0_6_node_60 | 0.4 | n |  | TRUE
45 | bus_LV_2701-226_0_6_node_61 | 0.4 | n |  | TRUE
46 | bus_LV_2701-226_0_6_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_2701-226_0_6_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_2701-226_0_6_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_2701-226_0_6_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_2701-226_0_6_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_2701-226_0_6_node_152 | 0.4 | n |  | TRUE
52 | bus_LV_2701-226_0_6_node_127 | 0.4 | n |  | TRUE
53 | bus_LV_2701-226_0_6_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_2701-226_0_6_node_33 | 0.4 | n |  | TRUE
55 | bus_LV_2701-226_0_6_node_34 | 0.4 | n |  | TRUE
56 | bus_LV_2701-226_0_6_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_2701-226_0_6_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_2701-226_0_6_node_103 | 0.4 | n |  | TRUE
59 | bus_LV_2701-226_0_6_node_154 | 0.4 | n |  | TRUE
60 | bus_LV_2701-226_0_6_node_104 | 0.4 | n |  | TRUE
61 | bus_LV_2701-226_0_6_node_91 | 0.4 | n |  | TRUE
62 | bus_LV_2701-226_0_6_node_38 | 0.4 | n |  | TRUE
63 | bus_LV_2701-226_0_6_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_2701-226_0_6_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_2701-226_0_6_node_150 | 0.4 | n |  | TRUE
66 | bus_LV_2701-226_0_6_node_43 | 0.4 | n |  | TRUE
67 | bus_LV_2701-226_0_6_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_2701-226_0_6_node_82 | 0.4 | n |  | TRUE
69 | bus_LV_2701-226_0_6_node_145 | 0.4 | n |  | TRUE
70 | bus_LV_2701-226_0_6_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_2701-226_0_6_node_51 | 0.4 | n |  | TRUE
72 | bus_LV_2701-226_0_6_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_2701-226_0_6_node_85 | 0.4 | n |  | TRUE
74 | bus_LV_2701-226_0_6_node_86 | 0.4 | n |  | TRUE
75 | bus_LV_2701-226_0_6_node_53 | 0.4 | n |  | TRUE
76 | bus_LV_2701-226_0_6_node_54 | 0.4 | n |  | TRUE
77 | bus_LV_2701-226_0_6_node_55 | 0.4 | n |  | TRUE
78 | bus_LV_2701-226_0_6_node_56 | 0.4 | n |  | TRUE
79 | bus_LV_2701-226_0_6_node_57 | 0.4 | n |  | TRUE
80 | bus_LV_2701-226_0_6_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_2701-226_0_6_node_59 | 0.4 | n |  | TRUE
82 | bus_LV_2701-226_0_6_node_105 | 0.4 | n |  | TRUE
83 | bus_LV_2701-226_0_6_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_2701-226_0_6_node_126 | 0.4 | n |  | TRUE
85 | bus_LV_2701-226_0_6_node_153 | 0.4 | n |  | TRUE
86 | bus_LV_2701-226_0_6_node_106 | 0.4 | n |  | TRUE
87 | bus_LV_2701-226_0_6_node_75 | 0.4 | n |  | TRUE
88 | bus_LV_2701-226_0_6_node_111 | 0.4 | n |  | TRUE
89 | bus_LV_2701-226_0_6_node_90 | 0.4 | n |  | TRUE
90 | bus_LV_2701-226_0_6_node_88 | 0.4 | n |  | TRUE
91 | bus_LV_2701-226_0_6_node_62 | 0.4 | n |  | TRUE
92 | bus_LV_2701-226_0_6_node_63 | 0.4 | n |  | TRUE
93 | bus_LV_2701-226_0_6_node_64 | 0.4 | n |  | TRUE
94 | bus_LV_2701-226_0_6_node_66 | 0.4 | n |  | TRUE
95 | bus_LV_2701-226_0_6_node_93 | 0.4 | n |  | TRUE
96 | bus_LV_2701-226_0_6_node_69 | 0.4 | n |  | TRUE
97 | bus_LV_2701-226_0_6_node_70 | 0.4 | n |  | TRUE
98 | bus_LV_2701-226_0_6_node_71 | 0.4 | n |  | TRUE
99 | bus_LV_2701-226_0_6_node_73 | 0.4 | n |  | TRUE
100 | bus_LV_2701-226_0_6_node_120 | 0.4 | n |  | TRUE
101 | bus_LV_2701-226_0_6_node_119 | 0.4 | n |  | TRUE
102 | bus_LV_2701-226_0_6_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_2701-226_0_6_node_97 | 0.4 | n |  | TRUE
104 | bus_LV_2701-226_0_6_node_76 | 0.4 | n |  | TRUE
105 | bus_LV_2701-226_0_6_node_77 | 0.4 | n |  | TRUE
106 | bus_LV_2701-226_0_6_node_79 | 0.4 | n |  | TRUE
107 | bus_LV_2701-226_0_6_node_148 | 0.4 | n |  | TRUE
108 | bus_LV_2701-226_0_6_node_149 | 0.4 | n |  | TRUE
109 | bus_LV_2701-226_0_6_node_101 | 0.4 | n |  | TRUE
110 | bus_LV_2701-226_0_6_node_99 | 0.4 | n |  | TRUE
111 | bus_LV_2701-226_0_6_node_155 | 0.4 | n |  | TRUE
112 | bus_LV_2701-226_0_6_node_121 | 0.4 | n |  | TRUE
113 | bus_LV_2701-226_0_6_node_87 | 0.4 | n |  | TRUE
114 | bus_LV_2701-226_0_6_node_89 | 0.4 | n |  | TRUE
115 | bus_LV_2701-226_0_6_node_95 | 0.4 | n |  | TRUE
116 | bus_LV_2701-226_0_6_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_2701-226_0_6_node_98 | 0.4 | n |  | TRUE
118 | bus_LV_2701-226_0_6_node_122 | 0.4 | n |  | TRUE
119 | bus_LV_2701-226_0_6_node_100 | 0.4 | n |  | TRUE
120 | bus_LV_2701-226_0_6_node_102 | 0.4 | n |  | TRUE
121 | bus_LV_2701-226_0_6_node_133 | 0.4 | n |  | TRUE
122 | bus_LV_2701-226_0_6_node_132 | 0.4 | n |  | TRUE
123 | bus_LV_2701-226_0_6_node_128 | 0.4 | n |  | TRUE
124 | bus_LV_2701-226_0_6_node_129 | 0.4 | n |  | TRUE
125 | bus_LV_2701-226_0_6_node_130 | 0.4 | n |  | TRUE
126 | bus_LV_2701-226_0_6_node_107 | 0.4 | n |  | TRUE
127 | bus_LV_2701-226_0_6_node_108 | 0.4 | n |  | TRUE
128 | bus_LV_2701-226_0_6_node_109 | 0.4 | n |  | TRUE
129 | bus_LV_2701-226_0_6_node_114 | 0.4 | n |  | TRUE
130 | bus_LV_2701-226_0_6_node_115 | 0.4 | n |  | TRUE
131 | bus_LV_2701-226_0_6_node_117 | 0.4 | n |  | TRUE
132 | bus_LV_2701-226_0_6_node_131 | 0.4 | n |  | TRUE
133 | bus_LV_2701-226_0_6_node_135 | 0.4 | n |  | TRUE
134 | bus_LV_2701-226_0_6_node_134 | 0.4 | n |  | TRUE
135 | bus_LV_2701-226_0_6_node_136 | 0.4 | n |  | TRUE
136 | bus_LV_2701-226_0_6_node_137 | 0.4 | n |  | TRUE
137 | bus_LV_2701-226_0_6_node_138 | 0.4 | n |  | TRUE
138 | bus_LV_2701-226_0_6_node_139 | 0.4 | n |  | TRUE
139 | bus_LV_2701-226_0_6_node_140 | 0.4 | n |  | TRUE
140 | bus_LV_2701-226_0_6_node_151 | 0.4 | n |  | TRUE
141 | bus_LV_2701-226_0_6_node_147 | 0.4 | n |  | TRUE
142 | bus_LV_2701-226_0_6_node_141 | 0.4 | n |  | TRUE
143 | bus_LV_2701-226_0_6_node_142 | 0.4 | n |  | TRUE
144 | bus_LV_2701-226_0_6_node_143 | 0.4 | n |  | TRUE
145 | bus_LV_2701-226_0_6_node_144 | 0.4 | n |  | TRUE
146 | bus_LV_2701-226_0_6_node_146 | 0.4 | n |  | TRUE
147 | bus_MV_556_0_node_67 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-226_0_6_load_0 | 0 | 0.0024885 | 0.00062368 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-226_0_6_load_113 | 4 | 0.0053791 | 0.0013481 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-226_0_6_load_92 | 7 | 0.0082028 | 0.0020558 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-226_0_6_load_15 | 8 | 0.0062843 | 0.001575 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-226_0_6_load_84 | 10 | 0.0022347 | 0.00056006 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-226_0_6_load_65 | 12 | 0.0038498 | 0.00096485 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-226_0_6_load_52 | 13 | 0.007329 | 0.0018368 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-226_0_6_load_48 | 14 | 0.0091938 | 0.0023042 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-226_0_6_load_16 | 15 | 0.0020827 | 0.00052198 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-226_0_6_load_83 | 16 | 0.0020698 | 0.00051875 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-226_0_6_load_125 | 17 | 0.0095471 | 0.0023927 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-226_0_6_load_123 | 18 | 0.0039047 | 0.00097861 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-226_0_6_load_8 | 19 | 0.0014937 | 0.00037435 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-226_0_6_load_9 | 20 | 0.0014902 | 0.00037348 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-226_0_6_load_11 | 22 | 0.0037467 | 0.00093902 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-226_0_6_load_12 | 23 | 0.0024637 | 0.00061746 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-226_0_6_load_13 | 24 | 0.016242 | 0.0040706 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-226_0_6_load_14 | 25 | 0.0027368 | 0.0006859 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-226_0_6_load_112 | 26 | 0.0024639 | 0.00061751 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-226_0_6_load_118 | 27 | 0.0024607 | 0.0006167 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-226_0_6_load_39 | 28 | 0.0028814 | 0.00072214 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-226_0_6_load_110 | 29 | 0.0037285 | 0.00093445 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-226_0_6_load_116 | 30 | 0.0025347 | 0.00063525 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-226_0_6_load_37 | 31 | 0.0029057 | 0.00072823 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-226_0_6_load_17 | 32 | 0.0065588 | 0.0016438 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-226_0_6_load_42 | 33 | 0.0071593 | 0.0017943 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-226_0_6_load_41 | 34 | 0.0099439 | 0.0024922 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-226_0_6_load_18 | 35 | 0.001813 | 0.00045439 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-226_0_6_load_19 | 36 | 0.0016215 | 0.00040639 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-226_0_6_load_20 | 37 | 0.0028756 | 0.00072069 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-226_0_6_load_21 | 38 | 0.0017395 | 0.00043597 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-226_0_6_load_22 | 39 | 0.0016394 | 0.00041088 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-226_0_6_load_25 | 40 | 0.004323 | 0.0010834 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-226_0_6_load_23 | 41 | 0.0023721 | 0.0005945 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-226_0_6_load_24 | 42 | 0.0012385 | 0.00031041 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-226_0_6_load_26 | 43 | 0.0036651 | 0.00091856 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-226_0_6_load_60 | 44 | 0.0012505 | 0.00031339 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-226_0_6_load_61 | 45 | 0.0013275 | 0.00033269 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-226_0_6_load_27 | 46 | 0.0010614 | 0.00026602 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-226_0_6_load_28 | 47 | 0.00087814 | 0.00022008 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-226_0_6_load_29 | 48 | 0.00114 | 0.00028571 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2701-226_0_6_load_30 | 49 | 0.001578 | 0.00039548 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2701-226_0_6_load_31 | 50 | 0.0052377 | 0.0013127 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2701-226_0_6_load_152 | 51 | 0.0057015 | 0.0014289 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2701-226_0_6_load_127 | 52 | 0.0082717 | 0.0020731 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2701-226_0_6_load_32 | 53 | 0.00152 | 0.00038094 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2701-226_0_6_load_33 | 54 | 0.0012523 | 0.00031386 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2701-226_0_6_load_34 | 55 | 0.001342 | 0.00033634 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2701-226_0_6_load_35 | 56 | 0.0015503 | 0.00038854 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2701-226_0_6_load_36 | 57 | 0.0012593 | 0.00031561 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2701-226_0_6_load_103 | 58 | 0.0012507 | 0.00031345 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2701-226_0_6_load_154 | 59 | 0.0014215 | 0.00035626 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2701-226_0_6_load_104 | 60 | 0.0016636 | 0.00041693 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2701-226_0_6_load_91 | 61 | 0.0015054 | 0.00037728 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2701-226_0_6_load_38 | 62 | 0.0034523 | 0.00086523 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2701-226_0_6_load_40 | 63 | 0.0015202 | 0.00038101 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2701-226_0_6_load_47 | 64 | 0.0015171 | 0.00038022 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2701-226_0_6_load_150 | 65 | 0.0028563 | 0.00071585 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2701-226_0_6_load_43 | 66 | 0.0046949 | 0.0011766 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2701-226_0_6_load_44 | 67 | 0.0021565 | 0.00054046 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2701-226_0_6_load_82 | 68 | 0.0020672 | 0.00051808 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2701-226_0_6_load_145 | 69 | 0.0015131 | 0.00037921 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2701-226_0_6_load_49 | 70 | 0.0042384 | 0.0010623 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2701-226_0_6_load_51 | 71 | 0.0074695 | 0.001872 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2701-226_0_6_load_67 | 72 | 0.012146 | 0.0030442 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2701-226_0_6_load_85 | 73 | 0.0062463 | 0.0015655 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2701-226_0_6_load_86 | 74 | 0.0023188 | 0.00058114 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2701-226_0_6_load_53 | 75 | 0.0061202 | 0.0015339 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2701-226_0_6_load_54 | 76 | 0.0050395 | 0.001263 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2701-226_0_6_load_56 | 78 | 0.0089671 | 0.0022474 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2701-226_0_6_load_57 | 79 | 0.0073403 | 0.0018397 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2701-226_0_6_load_58 | 80 | 0.0089955 | 0.0022545 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2701-226_0_6_load_59 | 81 | 0.0082485 | 0.0020673 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2701-226_0_6_load_105 | 82 | 0.0018571 | 0.00046544 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2701-226_0_6_load_74 | 83 | 0.0093224 | 0.0023364 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2701-226_0_6_load_126 | 84 | 0.0072909 | 0.0018273 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2701-226_0_6_load_153 | 85 | 0.0037442 | 0.00093838 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2701-226_0_6_load_106 | 86 | 0.0024878 | 0.00062351 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2701-226_0_6_load_75 | 87 | 0.0050344 | 0.0012618 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2701-226_0_6_load_111 | 88 | 0.0027292 | 0.00068399 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2701-226_0_6_load_90 | 89 | 0.001603 | 0.00040174 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2701-226_0_6_load_88 | 90 | 0.0012585 | 0.0003154 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2701-226_0_6_load_62 | 91 | 0.0031295 | 0.00078432 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2701-226_0_6_load_63 | 92 | 0.0090913 | 0.0022785 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2701-226_0_6_load_64 | 93 | 0.0028106 | 0.00070439 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2701-226_0_6_load_66 | 94 | 0.0024646 | 0.00061768 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2701-226_0_6_load_93 | 95 | 0.0079757 | 0.0019989 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2701-226_0_6_load_69 | 96 | 0.0081326 | 0.0020382 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2701-226_0_6_load_70 | 97 | 0.0061268 | 0.0015355 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2701-226_0_6_load_71 | 98 | 0.012508 | 0.0031348 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2701-226_0_6_load_73 | 99 | 0.0026293 | 0.00065898 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2701-226_0_6_load_120 | 100 | 0.0012984 | 0.00032542 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2701-226_0_6_load_94 | 102 | 0.0090635 | 0.0022715 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2701-226_0_6_load_97 | 103 | 0.0058671 | 0.0014704 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2701-226_0_6_load_76 | 104 | 0.0051901 | 0.0013007 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2701-226_0_6_load_77 | 105 | 0.002447 | 0.00061328 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2701-226_0_6_load_79 | 106 | 0.0024741 | 0.00062008 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2701-226_0_6_load_148 | 107 | 0.0024543 | 0.0006151 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2701-226_0_6_load_149 | 108 | 0.0027697 | 0.00069414 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2701-226_0_6_load_101 | 109 | 0.0042265 | 0.0010593 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2701-226_0_6_load_99 | 110 | 0.0054229 | 0.0013591 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2701-226_0_6_load_155 | 111 | 0.0062628 | 0.0015696 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2701-226_0_6_load_87 | 113 | 0.0018143 | 0.00045471 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2701-226_0_6_load_89 | 114 | 0.0015146 | 0.00037958 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2701-226_0_6_load_95 | 115 | 0.0042792 | 0.0010725 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2701-226_0_6_load_96 | 116 | 0.0033539 | 0.00084057 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2701-226_0_6_load_98 | 117 | 0.0036111 | 0.00090503 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2701-226_0_6_load_122 | 118 | 0.0073028 | 0.0018303 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2701-226_0_6_load_100 | 119 | 0.0042332 | 0.0010609 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2701-226_0_6_load_102 | 120 | 0.0045822 | 0.0011484 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2701-226_0_6_load_133 | 121 | 0.004229 | 0.0010599 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2701-226_0_6_load_132 | 122 | 0.0018758 | 0.00047012 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2701-226_0_6_load_128 | 123 | 0.003142 | 0.00078746 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2701-226_0_6_load_129 | 124 | 0.0018671 | 0.00046795 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2701-226_0_6_load_130 | 125 | 0.0040131 | 0.0010058 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2701-226_0_6_load_107 | 126 | 0.015108 | 0.0037865 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2701-226_0_6_load_108 | 127 | 0.0074659 | 0.0018711 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2701-226_0_6_load_109 | 128 | 0.0047636 | 0.0011939 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2701-226_0_6_load_114 | 129 | 0.0036801 | 0.00092232 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2701-226_0_6_load_115 | 130 | 0.0012274 | 0.00030761 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2701-226_0_6_load_117 | 131 | 0.0029998 | 0.00075182 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2701-226_0_6_load_131 | 132 | 0.0018709 | 0.0004689 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2701-226_0_6_load_135 | 133 | 0.0040149 | 0.0010062 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2701-226_0_6_load_134 | 134 | 0.0042337 | 0.0010611 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2701-226_0_6_load_136 | 135 | 0.0024501 | 0.00061405 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2701-226_0_6_load_137 | 136 | 0.0024263 | 0.0006081 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2701-226_0_6_load_138 | 137 | 0.0024299 | 0.000609 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2701-226_0_6_load_139 | 138 | 0.0024573 | 0.00061586 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2701-226_0_6_load_140 | 139 | 0.0024531 | 0.00061481 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2701-226_0_6_load_151 | 140 | 0.0046063 | 0.0011545 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2701-226_0_6_load_147 | 141 | 0.0015214 | 0.00038129 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2701-226_0_6_load_141 | 142 | 0.0028535 | 0.00071515 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2701-226_0_6_load_142 | 143 | 0.0015199 | 0.00038092 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2701-226_0_6_load_143 | 144 | 0.0015197 | 0.00038088 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2701-226_0_6_load_144 | 145 | 0.0046098 | 0.0011553 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2701-226_0_6_load_146 | 146 | 0.00152 | 0.00038096 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-226_0_6_line_0 |  | 0 | 1 | 0.054845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-226_0_6_line_1 |  | 1 | 2 | 0.069329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-226_0_6_line_2 |  | 2 | 8 | 0.025825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-226_0_6_line_3 |  | 2 | 3 | 0.013307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-226_0_6_line_4 |  | 3 | 4 | 0.016757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-226_0_6_line_5 |  | 4 | 12 | 0.01104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-226_0_6_line_6 |  | 5 | 6 | 0.01874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-226_0_6_line_7 |  | 5 | 7 | 0.017423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-226_0_6_line_8 |  | 6 | 13 | 0.019864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-226_0_6_line_9 |  | 6 | 14 | 0.02468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-226_0_6_line_10 |  | 8 | 15 | 0.012464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-226_0_6_line_11 |  | 9 | 10 | 0.011797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-226_0_6_line_12 |  | 9 | 11 | 0.002177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-226_0_6_line_13 |  | 10 | 16 | 0.0076717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-226_0_6_line_14 |  | 11 | 17 | 0.024577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-226_0_6_line_15 |  | 11 | 18 | 0.012669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-226_0_6_line_16 |  | 12 | 92 | 0.0094348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-226_0_6_line_17 |  | 13 | 73 | 0.012773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-226_0_6_line_18 |  | 14 | 70 | 0.011954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-226_0_6_line_19 |  | 15 | 32 | 0.0032616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-226_0_6_line_20 |  | 16 | 68 | 0.0060071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-226_0_6_line_21 |  | 18 | 118 | 0.014071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-226_0_6_line_22 |  | 19 | 20 | 0.0071162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-226_0_6_line_23 |  | 19 | 21 | 0.020509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-226_0_6_line_24 |  | 20 | 22 | 0.0048478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-226_0_6_line_25 |  | 21 | 23 | 0.0031143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2701-226_0_6_line_26 |  | 21 | 24 | 0.001415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2701-226_0_6_line_27 |  | 22 | 25 | 0.003891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-226_0_6_line_28 |  | 23 | 26 | 0.0065106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2701-226_0_6_line_29 |  | 24 | 27 | 0.0024934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_2701-226_0_6_line_30 |  | 25 | 28 | 0.0079415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-226_0_6_line_31 |  | 26 | 29 | 0.0023985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2701-226_0_6_line_32 |  | 27 | 30 | 0.0065932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_2701-226_0_6_line_33 |  | 28 | 31 | 0.0036774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-226_0_6_line_34 |  | 29 | 127 | 0.0079237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2701-226_0_6_line_35 |  | 30 | 129 | 0.006059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_2701-226_0_6_line_36 |  | 31 | 62 | 0.0075121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-226_0_6_line_37 |  | 32 | 33 | 0.0070382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-226_0_6_line_38 |  | 33 | 34 | 0.0063472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2701-226_0_6_line_39 |  | 34 | 66 | 0.0070504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2701-226_0_6_line_40 |  | 35 | 36 | 0.0075447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2701-226_0_6_line_41 |  | 35 | 37 | 0.0064752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-226_0_6_line_42 |  | 36 | 38 | 0.017145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-226_0_6_line_43 |  | 37 | 39 | 0.01112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-226_0_6_line_44 |  | 39 | 40 | 0.0056986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2701-226_0_6_line_45 |  | 40 | 41 | 0.0090078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2701-226_0_6_line_46 |  | 41 | 42 | 0.0018118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2701-226_0_6_line_47 |  | 42 | 43 | 0.0073243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2701-226_0_6_line_48 |  | 43 | 44 | 0.0033886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2701-226_0_6_line_49 |  | 44 | 45 | 0.0044519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2701-226_0_6_line_50 |  | 45 | 89 | 0.0029199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2701-226_0_6_line_51 |  | 46 | 47 | 0.0010066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2701-226_0_6_line_52 |  | 46 | 48 | 0.0077209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2701-226_0_6_line_53 |  | 47 | 49 | 0.0034931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2701-226_0_6_line_54 |  | 48 | 50 | 0.0013936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2701-226_0_6_line_55 |  | 49 | 51 | 0.0034268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2701-226_0_6_line_56 |  | 51 | 52 | 0.0038081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2701-226_0_6_line_57 |  | 52 | 84 | 0.015055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2701-226_0_6_line_58 |  | 53 | 54 | 0.0077376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2701-226_0_6_line_59 |  | 53 | 55 | 0.0028947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2701-226_0_6_line_60 |  | 54 | 56 | 0.0017376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2701-226_0_6_line_61 |  | 55 | 57 | 0.0044385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2701-226_0_6_line_62 |  | 56 | 58 | 0.0049609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2701-226_0_6_line_63 |  | 57 | 59 | 0.0025552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2701-226_0_6_line_64 |  | 58 | 60 | 0.0032689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2701-226_0_6_line_65 |  | 59 | 61 | 0.007966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2701-226_0_6_line_66 |  | 60 | 123 | 0.01582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2701-226_0_6_line_67 |  | 61 | 114 | 0.0023239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2701-226_0_6_line_68 |  | 62 | 63 | 0.0018867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2701-226_0_6_line_69 |  | 63 | 64 | 0.0070076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2701-226_0_6_line_70 |  | 64 | 65 | 0.0028796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2701-226_0_6_line_71 |  | 65 | 69 | 0.0041156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2701-226_0_6_line_72 |  | 66 | 67 | 0.0097953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2701-226_0_6_line_73 |  | 67 | 68 | 0.0063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2701-226_0_6_line_74 |  | 69 | 144 | 0.0069916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2701-226_0_6_line_75 |  | 70 | 71 | 0.016672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2701-226_0_6_line_76 |  | 71 | 72 | 0.025657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2701-226_0_6_line_77 |  | 73 | 74 | 0.003927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2701-226_0_6_line_78 |  | 74 | 111 | 0.0074563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2701-226_0_6_line_79 |  | 75 | 76 | 0.0056375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2701-226_0_6_line_80 |  | 75 | 77 | 0.028685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2701-226_0_6_line_81 |  | 76 | 78 | 0.0068388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2701-226_0_6_line_82 |  | 77 | 79 | 0.018559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_2701-226_0_6_line_83 |  | 77 | 80 | 0.023238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2701-226_0_6_line_84 |  | 77 | 81 | 0.009034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_2701-226_0_6_line_85 |  | 78 | 82 | 0.003702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2701-226_0_6_line_86 |  | 79 | 83 | 0.0013813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_2701-226_0_6_line_87 |  | 80 | 84 | 0.0075046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2701-226_0_6_line_88 |  | 81 | 85 | 0.0057065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2701-226_0_6_line_89 |  | 82 | 86 | 0.006199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2701-226_0_6_line_90 |  | 83 | 87 | 0.012611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2701-226_0_6_line_91 |  | 85 | 88 | 0.0066122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_2701-226_0_6_line_92 |  | 86 | 124 | 0.0067533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2701-226_0_6_line_93 |  | 87 | 102 | 0.0015715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2701-226_0_6_line_94 |  | 88 | 128 | 0.00019598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_2701-226_0_6_line_95 |  | 89 | 90 | 0.0077034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2701-226_0_6_line_96 |  | 90 | 113 | 0.0013041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2701-226_0_6_line_97 |  | 91 | 92 | 0.0087884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2701-226_0_6_line_98 |  | 91 | 93 | 0.0076338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2701-226_0_6_line_99 |  | 93 | 94 | 0.0074922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2701-226_0_6_line_100 |  | 94 | 95 | 0.011037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2701-226_0_6_line_101 |  | 96 | 97 | 0.0040267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2701-226_0_6_line_102 |  | 96 | 98 | 0.0066805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2701-226_0_6_line_103 |  | 98 | 99 | 0.0019541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2701-226_0_6_line_104 |  | 99 | 100 | 0.01861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2701-226_0_6_line_105 |  | 100 | 101 | 0.011044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2701-226_0_6_line_106 |  | 101 | 112 | 0.017741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2701-226_0_6_line_107 |  | 101 | 131 | 0.0034151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2701-226_0_6_line_108 |  | 102 | 103 | 0.006719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2701-226_0_6_line_109 |  | 103 | 115 | 0.0025239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2701-226_0_6_line_110 |  | 104 | 105 | 0.0073858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2701-226_0_6_line_111 |  | 105 | 106 | 0.0032706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2701-226_0_6_line_112 |  | 106 | 107 | 0.0037395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2701-226_0_6_line_113 |  | 107 | 108 | 0.0027751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2701-226_0_6_line_114 |  | 108 | 139 | 0.0042248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2701-226_0_6_line_115 |  | 109 | 110 | 0.0077653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2701-226_0_6_line_116 |  | 110 | 119 | 0.0029833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2701-226_0_6_line_117 |  | 111 | 112 | 0.0099257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2701-226_0_6_line_118 |  | 112 | 123 | 0.011939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2701-226_0_6_line_119 |  | 113 | 114 | 0.0057032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2701-226_0_6_line_120 |  | 115 | 116 | 0.00044486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2701-226_0_6_line_121 |  | 116 | 117 | 0.0068381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2701-226_0_6_line_122 |  | 117 | 118 | 0.0033756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2701-226_0_6_line_123 |  | 119 | 120 | 0.0092231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2701-226_0_6_line_124 |  | 120 | 121 | 0.0015275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2701-226_0_6_line_125 |  | 121 | 122 | 0.010274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2701-226_0_6_line_126 |  | 122 | 134 | 0.00047565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2701-226_0_6_line_127 |  | 124 | 125 | 0.0040045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2701-226_0_6_line_128 |  | 125 | 132 | 0.0089923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2701-226_0_6_line_129 |  | 126 | 127 | 0.0052231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_2701-226_0_6_line_130 |  | 126 | 128 | 0.0067259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
131 | LV_2701-226_0_6_line_131 |  | 129 | 130 | 0.00063697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
132 | LV_2701-226_0_6_line_132 |  | 130 | 131 | 0.013396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
133 | LV_2701-226_0_6_line_133 |  | 132 | 133 | 0.0017646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2701-226_0_6_line_134 |  | 133 | 134 | 0.010755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2701-226_0_6_line_135 |  | 135 | 136 | 0.0017066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2701-226_0_6_line_136 |  | 135 | 137 | 0.0047961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2701-226_0_6_line_137 |  | 136 | 138 | 0.0053027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2701-226_0_6_line_138 |  | 137 | 139 | 0.0022035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2701-226_0_6_line_139 |  | 138 | 140 | 0.0038318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2701-226_0_6_line_140 |  | 140 | 141 | 0.0031812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2701-226_0_6_line_141 |  | 141 | 146 | 0.0070125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2701-226_0_6_line_142 |  | 142 | 143 | 0.0063326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2701-226_0_6_line_143 |  | 142 | 144 | 0.00066324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2701-226_0_6_line_144 |  | 143 | 145 | 0.0054355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2701-226_0_6_line_145 |  | 145 | 146 | 0.0015672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-226_0_6_trafo_110 | 0.63 MVA 20/0.4 kV | 147 | 29 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2610237.5291 | 1267714.4915 | 2610237.1855 | 1267708.5756 | 2610236.332 | 1267705.9723 | 2610236.3373 | 1267702.9035 | 2610244.3618 | 1267660.5458
1 | 2610203.7999 | 1267756.2961 | 2610207.2081 | 1267756.9914 | 2610210.0744 | 1267757.6634 | 2610212.4294 | 1267758.09 | 2610215.0928 | 1267758.5949 | 2610216.4094 | 1267758.8418 | 2610218.5006 | 1267759.5125 | 2610224.543 | 1267729.5575 | 2610226.8372 | 1267717.175 | 2610232.212 | 1267716.5616 | 2610237.5291 | 1267714.4915
2 | 2610203.7999 | 1267756.2961 | 2610203.2088 | 1267749.9129 | 2610206.8549 | 1267730.8437
3 | 2610195.4983 | 1267760.8073 | 2610196.3586 | 1267755.0825 | 2610203.7999 | 1267756.2961
4 | 2610195.4983 | 1267760.8073 | 2610178.8494 | 1267758.9039
5 | 2610167.8812 | 1267757.65 | 2610178.8494 | 1267758.9039
6 | 2610033.9081 | 1267758.0528 | 2610023.5031 | 1267742.4465
7 | 2610033.9081 | 1267758.0528 | 2610051.1588 | 1267755.6069
8 | 2610023.5031 | 1267742.4465 | 2610038.6646 | 1267729.6121
9 | 2610023.5031 | 1267742.4465 | 2610008.1312 | 1267723.1378
10 | 2610206.8549 | 1267730.8437 | 2610209.1957 | 1267718.6014
11 | 2610221.9399 | 1267654.5894 | 2610219.6063 | 1267666.1537
12 | 2610222.3725 | 1267652.4553 | 2610221.9399 | 1267654.5894
13 | 2610218.0887 | 1267673.6739 | 2610219.6063 | 1267666.1537
14 | 2610222.3725 | 1267652.4553 | 2610226.8544 | 1267628.2904
15 | 2610222.3725 | 1267652.4553 | 2610209.9256 | 1267650.0915
16 | 2610167.8812 | 1267757.65 | 2610158.5075 | 1267756.5784
17 | 2610048.4137 | 1267721.3594 | 2610038.6646 | 1267729.6121
18 | 2610008.1312 | 1267723.1378 | 2610000.686 | 1267713.786
19 | 2610209.8083 | 1267715.3978 | 2610209.1957 | 1267718.6014
20 | 2610216.9005 | 1267679.5623 | 2610218.0887 | 1267673.6739
21 | 2610209.9256 | 1267650.0915 | 2610196.1017 | 1267647.4662
22 | 2610090.03 | 1267656.5667 | 2610085.592 | 1267651.0039
23 | 2610102.8202 | 1267672.5984 | 2610090.03 | 1267656.5667
24 | 2610085.592 | 1267651.0039 | 2610082.5687 | 1267647.2143
25 | 2610102.8202 | 1267672.5984 | 2610105.163 | 1267670.5466
26 | 2610102.8202 | 1267672.5984 | 2610101.7955 | 1267673.5742
27 | 2610080.1421 | 1267644.1727 | 2610082.5687 | 1267647.2143
28 | 2610105.163 | 1267670.5466 | 2610110.0608 | 1267666.2571
29 | 2610101.7955 | 1267673.5742 | 2610099.9898 | 1267675.2937
30 | 2610075.1895 | 1267637.9648 | 2610080.1421 | 1267644.1727
31 | 2610110.0608 | 1267666.2571 | 2610111.8652 | 1267664.6769
32 | 2610099.9898 | 1267675.2937 | 2610095.2151 | 1267679.8404
33 | 2610075.1895 | 1267637.9648 | 2610072.8961 | 1267635.0901
34 | 2610117.826 | 1267659.4564 | 2610111.8652 | 1267664.6769
35 | 2610090.8273 | 1267684.0188 | 2610095.2151 | 1267679.8404
36 | 2610068.2112 | 1267629.2179 | 2610072.8961 | 1267635.0901
37 | 2610211.1301 | 1267708.4849 | 2610209.8083 | 1267715.3978
38 | 2610211.1301 | 1267708.4849 | 2610212.3221 | 1267702.2507 | 2610212.3221 | 1267702.2507
39 | 2610213.7167 | 1267695.3396 | 2610212.3221 | 1267702.2507
40 | 2609983.1277 | 1267603.0975 | 2609978.4858 | 1267597.1497
41 | 2609987.1115 | 1267608.2021 | 2609983.1277 | 1267603.0975
42 | 2609967.9373 | 1267583.6334 | 2609978.4858 | 1267597.1497
43 | 2609987.1115 | 1267608.2021 | 2609993.9527 | 1267616.9681
44 | 2609993.9527 | 1267616.9681 | 2609997.4587 | 1267621.4605
45 | 2609997.4587 | 1267621.4605 | 2610003.0007 | 1267628.5617
46 | 2610003.0007 | 1267628.5617 | 2610004.1154 | 1267629.99
47 | 2610008.6215 | 1267635.764 | 2610004.1154 | 1267629.99
48 | 2610008.6215 | 1267635.764 | 2610010.7063 | 1267638.4354
49 | 2610013.4453 | 1267641.945 | 2610010.7063 | 1267638.4354
50 | 2610013.4453 | 1267641.945 | 2610015.2418 | 1267644.2469
51 | 2610170.4037 | 1267586.786 | 2610169.9247 | 1267587.6713
52 | 2610174.0779 | 1267579.9954 | 2610170.4037 | 1267586.786
53 | 2610168.2625 | 1267590.7435 | 2610169.9247 | 1267587.6713
54 | 2610174.7411 | 1267578.7697 | 2610174.0779 | 1267579.9954
55 | 2610168.2625 | 1267590.7435 | 2610166.6317 | 1267593.7574
56 | 2610166.6317 | 1267593.7574 | 2610164.8196 | 1267597.1067
57 | 2610164.8196 | 1267597.1067 | 2610157.6553 | 1267610.3479
58 | 2610036.707 | 1267671.7512 | 2610041.4675 | 1267677.8511
59 | 2610036.707 | 1267671.7512 | 2610034.926 | 1267669.4692
60 | 2610042.5365 | 1267679.2209 | 2610041.4675 | 1267677.8511
61 | 2610032.1953 | 1267665.9702 | 2610034.926 | 1267669.4692
62 | 2610042.5365 | 1267679.2209 | 2610045.5886 | 1267683.1317
63 | 2610032.1953 | 1267665.9702 | 2610030.6232 | 1267663.9558
64 | 2610047.5998 | 1267685.7087 | 2610045.5886 | 1267683.1317
65 | 2610030.6232 | 1267663.9558 | 2610025.7222 | 1267657.6759
66 | 2610057.3326 | 1267698.1798 | 2610047.5998 | 1267685.7087
67 | 2610025.7222 | 1267657.6759 | 2610024.2924 | 1267655.8439
68 | 2610068.2112 | 1267629.2179 | 2610067.0346 | 1267627.7431
69 | 2610062.6644 | 1267622.2652 | 2610065.3885 | 1267625.6799 | 2610067.0346 | 1267627.7431
70 | 2610060.8686 | 1267620.0142 | 2610062.6644 | 1267622.2652
71 | 2610060.8686 | 1267620.0142 | 2610058.302 | 1267616.7969
72 | 2610213.7167 | 1267695.3396 | 2610215.6543 | 1267685.7378
73 | 2610215.6543 | 1267685.7378 | 2610216.9005 | 1267679.5623
74 | 2610058.302 | 1267616.7969 | 2610053.9418 | 1267611.3315
75 | 2610000.686 | 1267713.786 | 2609990.302 | 1267700.7425
76 | 2609990.302 | 1267700.7425 | 2609974.3216 | 1267680.6696
77 | 2610048.4137 | 1267721.3594 | 2610051.411 | 1267718.8221
78 | 2610051.411 | 1267718.8221 | 2610057.102 | 1267714.0046
79 | 2610122.9955 | 1267609.5144 | 2610126.2854 | 1267614.0924
80 | 2610143.0256 | 1267637.3866 | 2610126.2854 | 1267614.0924
81 | 2610122.9955 | 1267609.5144 | 2610119.0045 | 1267603.9609
82 | 2610143.0256 | 1267637.3866 | 2610161.2587 | 1267640.8493
83 | 2610143.0256 | 1267637.3866 | 2610154.084 | 1267616.9483
84 | 2610143.0256 | 1267637.3866 | 2610136.2295 | 1267643.3387
85 | 2610119.0045 | 1267603.9609 | 2610116.8441 | 1267600.9547
86 | 2610161.2587 | 1267640.8493 | 2610162.6157 | 1267641.107
87 | 2610157.6553 | 1267610.3479 | 2610154.084 | 1267616.9483
88 | 2610136.2295 | 1267643.3387 | 2610131.9366 | 1267647.0983
89 | 2610116.8441 | 1267600.9547 | 2610113.2265 | 1267595.9207
90 | 2610162.6157 | 1267641.107 | 2610175.0057 | 1267643.4599
91 | 2610126.9624 | 1267651.4548 | 2610131.9366 | 1267647.0983
92 | 2610109.2854 | 1267590.4367 | 2610113.2265 | 1267595.9207
93 | 2610176.5496 | 1267643.7531 | 2610175.0057 | 1267643.4599
94 | 2610126.8149 | 1267651.5839 | 2610126.9624 | 1267651.4548
95 | 2610015.2418 | 1267644.2469 | 2610019.9813 | 1267650.3198
96 | 2610020.7836 | 1267651.3478 | 2610019.9813 | 1267650.3198
97 | 2610149.7759 | 1267755.5802 | 2610158.5075 | 1267756.5784
98 | 2610142.1915 | 1267754.7131 | 2610149.7759 | 1267755.5802
99 | 2610142.1915 | 1267754.7131 | 2610134.7478 | 1267753.8621
100 | 2610123.7825 | 1267752.6086 | 2610134.7478 | 1267753.8621
101 | 2610092.4183 | 1267730.3629 | 2610093.0192 | 1267734.3446
102 | 2610092.4183 | 1267730.3629 | 2610091.4214 | 1267723.7573
103 | 2610091.1297 | 1267721.825 | 2610091.4214 | 1267723.7573
104 | 2610091.1297 | 1267721.825 | 2610090.945 | 1267720.6008 | 2610089.6788 | 1267712.7487 | 2610087.5504 | 1267707.4303 | 2610085.2069 | 1267704.5807
105 | 2610078.192 | 1267696.0509 | 2610085.2069 | 1267704.5807
106 | 2610064.6778 | 1267707.5916 | 2610078.192 | 1267696.0509
107 | 2610078.192 | 1267696.0509 | 2610080.6651 | 1267693.6958
108 | 2610176.5496 | 1267643.7531 | 2610183.1506 | 1267645.0067
109 | 2610183.1506 | 1267645.0067 | 2610185.6302 | 1267645.4776
110 | 2610014.3854 | 1267561.7481 | 2610018.9915 | 1267567.5217
111 | 2610021.0311 | 1267570.0784 | 2610018.9915 | 1267567.5217
112 | 2610023.3632 | 1267573.0016 | 2610021.0311 | 1267570.0784
113 | 2610023.3632 | 1267573.0016 | 2610025.0938 | 1267575.171
114 | 2610025.0938 | 1267575.171 | 2610027.7286 | 1267578.4736
115 | 2610080.1071 | 1267549.8346 | 2610075.5755 | 1267543.5287
116 | 2610080.1071 | 1267549.8346 | 2610081.8481 | 1267552.2572
117 | 2610064.6778 | 1267707.5916 | 2610057.102 | 1267714.0046
118 | 2610064.6778 | 1267707.5916 | 2610057.3326 | 1267698.1798
119 | 2610020.7836 | 1267651.3478 | 2610024.2924 | 1267655.8439
120 | 2610186.0673 | 1267645.5606 | 2610185.6302 | 1267645.4776
121 | 2610192.7853 | 1267646.8364 | 2610186.0673 | 1267645.5606
122 | 2610192.7853 | 1267646.8364 | 2610196.1017 | 1267647.4662
123 | 2610087.2305 | 1267559.7468 | 2610081.8481 | 1267552.2572
124 | 2610087.2305 | 1267559.7468 | 2610088.1219 | 1267560.9872
125 | 2610094.1173 | 1267569.33 | 2610088.1219 | 1267560.9872
126 | 2610094.1173 | 1267569.33 | 2610094.3949 | 1267569.7162
127 | 2610109.2854 | 1267590.4367 | 2610106.9485 | 1267587.1848
128 | 2610101.7008 | 1267579.8825 | 2610106.9485 | 1267587.1848
129 | 2610121.7552 | 1267656.0152 | 2610117.826 | 1267659.4564
130 | 2610121.7552 | 1267656.0152 | 2610126.8149 | 1267651.5839
131 | 2610090.366 | 1267684.4581 | 2610090.8273 | 1267684.0188
132 | 2610080.6651 | 1267693.6958 | 2610090.366 | 1267684.4581
133 | 2610101.7008 | 1267579.8825 | 2610100.671 | 1267578.4496
134 | 2610100.671 | 1267578.4496 | 2610094.3949 | 1267569.7162
135 | 2610032.0938 | 1267583.9453 | 2610033.158 | 1267585.2793
136 | 2610032.0938 | 1267583.9453 | 2610029.1028 | 1267580.1961
137 | 2610033.158 | 1267585.2793 | 2610036.465 | 1267589.4246
138 | 2610029.1028 | 1267580.1961 | 2610027.7286 | 1267578.4736
139 | 2610036.465 | 1267589.4246 | 2610038.8547 | 1267592.42
140 | 2610040.8386 | 1267594.9068 | 2610038.8547 | 1267592.42
141 | 2610040.8386 | 1267594.9068 | 2610045.2118 | 1267600.3886
142 | 2610053.5282 | 1267610.813 | 2610049.5789 | 1267605.8627
143 | 2610053.5282 | 1267610.813 | 2610053.9418 | 1267611.3315
144 | 2610049.5789 | 1267605.8627 | 2610046.1891 | 1267601.6137
145 | 2610046.1891 | 1267601.6137 | 2610045.2118 | 1267600.3886

## bus_geodata
| x | y | coords
0 | 2610244.3618 | 1267660.5458
1 | 2610237.5291 | 1267714.4915
2 | 2610203.7999 | 1267756.2961
3 | 2610195.4983 | 1267760.8073
4 | 2610178.8494 | 1267758.9039
5 | 2610033.9081 | 1267758.0528
6 | 2610023.5031 | 1267742.4465
7 | 2610051.1588 | 1267755.6069
8 | 2610206.8549 | 1267730.8437
9 | 2610221.9399 | 1267654.5894
10 | 2610219.6063 | 1267666.1537
11 | 2610222.3725 | 1267652.4553
12 | 2610167.8812 | 1267757.65
13 | 2610038.6646 | 1267729.6121
14 | 2610008.1312 | 1267723.1378
15 | 2610209.1957 | 1267718.6014
16 | 2610218.0887 | 1267673.6739
17 | 2610226.8544 | 1267628.2904
18 | 2610209.9256 | 1267650.0915
19 | 2610090.03 | 1267656.5667
20 | 2610085.592 | 1267651.0039
21 | 2610102.8202 | 1267672.5984
22 | 2610082.5687 | 1267647.2143
23 | 2610105.163 | 1267670.5466
24 | 2610101.7955 | 1267673.5742
25 | 2610080.1421 | 1267644.1727
26 | 2610110.0608 | 1267666.2571
27 | 2610099.9898 | 1267675.2937
28 | 2610075.1895 | 1267637.9648
29 | 2610111.8652 | 1267664.6769
30 | 2610095.2151 | 1267679.8404
31 | 2610072.8961 | 1267635.0901
32 | 2610209.8083 | 1267715.3978
33 | 2610211.1301 | 1267708.4849
34 | 2610212.3221 | 1267702.2507
35 | 2609983.1277 | 1267603.0975
36 | 2609978.4858 | 1267597.1497
37 | 2609987.1115 | 1267608.2021
38 | 2609967.9373 | 1267583.6334
39 | 2609993.9527 | 1267616.9681
40 | 2609997.4587 | 1267621.4605
41 | 2610003.0007 | 1267628.5617
42 | 2610004.1154 | 1267629.99
43 | 2610008.6215 | 1267635.764
44 | 2610010.7063 | 1267638.4354
45 | 2610013.4453 | 1267641.945
46 | 2610170.4037 | 1267586.786
47 | 2610169.9247 | 1267587.6713
48 | 2610174.0779 | 1267579.9954
49 | 2610168.2625 | 1267590.7435
50 | 2610174.7411 | 1267578.7697
51 | 2610166.6317 | 1267593.7574
52 | 2610164.8196 | 1267597.1067
53 | 2610036.707 | 1267671.7512
54 | 2610041.4675 | 1267677.8511
55 | 2610034.926 | 1267669.4692
56 | 2610042.5365 | 1267679.2209
57 | 2610032.1953 | 1267665.9702
58 | 2610045.5886 | 1267683.1317
59 | 2610030.6232 | 1267663.9558
60 | 2610047.5998 | 1267685.7087
61 | 2610025.7222 | 1267657.6759
62 | 2610068.2112 | 1267629.2179
63 | 2610067.0346 | 1267627.7431
64 | 2610062.6644 | 1267622.2652
65 | 2610060.8686 | 1267620.0142
66 | 2610213.7167 | 1267695.3396
67 | 2610215.6543 | 1267685.7378
68 | 2610216.9005 | 1267679.5623
69 | 2610058.302 | 1267616.7969
70 | 2610000.686 | 1267713.786
71 | 2609990.302 | 1267700.7425
72 | 2609974.3216 | 1267680.6696
73 | 2610048.4137 | 1267721.3594
74 | 2610051.411 | 1267718.8221
75 | 2610126.2854 | 1267614.0924
76 | 2610122.9955 | 1267609.5144
77 | 2610143.0256 | 1267637.3866
78 | 2610119.0045 | 1267603.9609
79 | 2610161.2587 | 1267640.8493
80 | 2610154.084 | 1267616.9483
81 | 2610136.2295 | 1267643.3387
82 | 2610116.8441 | 1267600.9547
83 | 2610162.6157 | 1267641.107
84 | 2610157.6553 | 1267610.3479
85 | 2610131.9366 | 1267647.0983
86 | 2610113.2265 | 1267595.9207
87 | 2610175.0057 | 1267643.4599
88 | 2610126.9624 | 1267651.4548
89 | 2610015.2418 | 1267644.2469
90 | 2610019.9813 | 1267650.3198
91 | 2610149.7759 | 1267755.5802
92 | 2610158.5075 | 1267756.5784
93 | 2610142.1915 | 1267754.7131
94 | 2610134.7478 | 1267753.8621
95 | 2610123.7825 | 1267752.6086
96 | 2610092.4183 | 1267730.3629
97 | 2610093.0192 | 1267734.3446
98 | 2610091.4214 | 1267723.7573
99 | 2610091.1297 | 1267721.825
100 | 2610085.2069 | 1267704.5807
101 | 2610078.192 | 1267696.0509
102 | 2610176.5496 | 1267643.7531
103 | 2610183.1506 | 1267645.0067
104 | 2610014.3854 | 1267561.7481
105 | 2610018.9915 | 1267567.5217
106 | 2610021.0311 | 1267570.0784
107 | 2610023.3632 | 1267573.0016
108 | 2610025.0938 | 1267575.171
109 | 2610075.5755 | 1267543.5287
110 | 2610080.1071 | 1267549.8346
111 | 2610057.102 | 1267714.0046
112 | 2610064.6778 | 1267707.5916
113 | 2610020.7836 | 1267651.3478
114 | 2610024.2924 | 1267655.8439
115 | 2610185.6302 | 1267645.4776
116 | 2610186.0673 | 1267645.5606
117 | 2610192.7853 | 1267646.8364
118 | 2610196.1017 | 1267647.4662
119 | 2610081.8481 | 1267552.2572
120 | 2610087.2305 | 1267559.7468
121 | 2610088.1219 | 1267560.9872
122 | 2610094.1173 | 1267569.33
123 | 2610057.3326 | 1267698.1798
124 | 2610109.2854 | 1267590.4367
125 | 2610106.9485 | 1267587.1848
126 | 2610121.7552 | 1267656.0152
127 | 2610117.826 | 1267659.4564
128 | 2610126.8149 | 1267651.5839
129 | 2610090.8273 | 1267684.0188
130 | 2610090.366 | 1267684.4581
131 | 2610080.6651 | 1267693.6958
132 | 2610101.7008 | 1267579.8825
133 | 2610100.671 | 1267578.4496
134 | 2610094.3949 | 1267569.7162
135 | 2610032.0938 | 1267583.9453
136 | 2610033.158 | 1267585.2793
137 | 2610029.1028 | 1267580.1961
138 | 2610036.465 | 1267589.4246
139 | 2610027.7286 | 1267578.4736
140 | 2610038.8547 | 1267592.42
141 | 2610040.8386 | 1267594.9068
142 | 2610053.5282 | 1267610.813
143 | 2610049.5789 | 1267605.8627
144 | 2610053.9418 | 1267611.3315
145 | 2610046.1891 | 1267601.6137
146 | 2610045.2118 | 1267600.3886
147 | 2610102.8202 | 1267672.5984

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98335 | -0.32083 | 0.0024885 | 0.00062368
1 | 0.98348 | -0.31837 | 0 | 0
2 | 0.98364 | -0.31526 | 0 | 0
3 | 0.98321 | -0.32358 | 0 | 0
4 | 0.98267 | -0.33407 | 0.0053791 | 0.0013481
5 | 0.99262 | -0.14196 | 0 | 0
6 | 0.99276 | -0.13924 | 0 | 0
7 | 0.99249 | -0.14449 | 0.0082028 | 0.0020558
8 | 0.98452 | -0.29797 | 0.0062843 | 0.001575
9 | 0.9893 | -0.20522 | 0 | 0
10 | 0.98841 | -0.22256 | 0.0022347 | 0.00056006
11 | 0.98947 | -0.20203 | 0 | 0
12 | 0.98238 | -0.33991 | 0.0038498 | 0.00096485
13 | 0.99351 | -0.12476 | 0.007329 | 0.0018368
14 | 0.99201 | -0.15367 | 0.0091938 | 0.0023042
15 | 0.98502 | -0.28823 | 0.0020827 | 0.00052198
16 | 0.98784 | -0.23355 | 0.0020698 | 0.00051875
17 | 0.98925 | -0.20621 | 0.0095471 | 0.0023927
18 | 0.99054 | -0.1813 | 0.0039047 | 0.00097861
19 | 0.99777 | -0.042768 | 0.0014937 | 0.00037435
20 | 0.99731 | -0.051534 | 0.0014902 | 0.00037348
21 | 0.99911 | -0.017015 | 0 | 0
22 | 0.99701 | -0.057383 | 0.0037467 | 0.00093902
23 | 0.99934 | -0.012647 | 0.0024637 | 0.00061746
24 | 0.99904 | -0.018409 | 0.016242 | 0.0040706
25 | 0.99678 | -0.061825 | 0.0027368 | 0.0006859
26 | 0.99982 | -0.0034283 | 0.0024639 | 0.00061751
27 | 0.99892 | -0.02063 | 0.0024607 | 0.0006167
28 | 0.99632 | -0.070515 | 0.0028814 | 0.00072214
29 | 1 | 0 | -0.54946 | -0.13865
30 | 0.99862 | -0.02641 | 0.0025347 | 0.00063525
31 | 0.99613 | -0.074356 | 0.0029057 | 0.00072823
32 | 0.98516 | -0.28556 | 0.0065588 | 0.0016438
33 | 0.9855 | -0.27897 | 0.0071593 | 0.0017943
34 | 0.98585 | -0.27222 | 0.0099439 | 0.0024922
35 | 0.99188 | -0.15626 | 0.001813 | 0.00045439
36 | 0.99186 | -0.15671 | 0.0016215 | 0.00040639
37 | 0.99191 | -0.15566 | 0.0028756 | 0.00072069
38 | 0.99183 | -0.15724 | 0.0017395 | 0.00043597
39 | 0.99199 | -0.15408 | 0.0016394 | 0.00041088
40 | 0.99204 | -0.1531 | 0.004323 | 0.0010834
41 | 0.99216 | -0.15087 | 0.0023721 | 0.0005945
42 | 0.99219 | -0.15034 | 0.0012385 | 0.00031041
43 | 0.9923 | -0.14805 | 0.0036651 | 0.00091856
44 | 0.99237 | -0.14678 | 0.0012505 | 0.00031339
45 | 0.99246 | -0.145 | 0.0013275 | 0.00033269
46 | 0.99502 | -0.095517 | 0.0010614 | 0.00026602
47 | 0.99502 | -0.095385 | 0.00087814 | 0.00022008
48 | 0.99497 | -0.096384 | 0.00114 | 0.00028571
49 | 0.99505 | -0.094874 | 0.001578 | 0.00039548
50 | 0.99496 | -0.096513 | 0.0052377 | 0.0013127
51 | 0.99508 | -0.094277 | 0.0057015 | 0.0014289
52 | 0.99513 | -0.093231 | 0.0082717 | 0.0020731
53 | 0.99349 | -0.12513 | 0.00152 | 0.00038094
54 | 0.99375 | -0.12006 | 0.0012523 | 0.00031386
55 | 0.99339 | -0.12695 | 0.001342 | 0.00033634
56 | 0.99381 | -0.11888 | 0.0015503 | 0.00038854
57 | 0.99325 | -0.12963 | 0.0012593 | 0.00031561
58 | 0.99399 | -0.11539 | 0.0012507 | 0.00031345
59 | 0.99318 | -0.13112 | 0.0014215 | 0.00035626
60 | 0.99411 | -0.11302 | 0.0016636 | 0.00041693
61 | 0.99295 | -0.13557 | 0.0015054 | 0.00037728
62 | 0.99574 | -0.081823 | 0.0034523 | 0.00086523
63 | 0.99565 | -0.083584 | 0.0015202 | 0.00038101
64 | 0.99532 | -0.089943 | 0.0015171 | 0.00038022
65 | 0.99518 | -0.09248 | 0.0028563 | 0.00071585
66 | 0.9863 | -0.26347 | 0.0046949 | 0.0011766
67 | 0.98696 | -0.25051 | 0.0021565 | 0.00054046
68 | 0.98741 | -0.24194 | 0.0020672 | 0.00051808
69 | 0.99501 | -0.095901 | 0.0015131 | 0.00037921
70 | 0.99175 | -0.15873 | 0.0042384 | 0.0010623
71 | 0.99145 | -0.16452 | 0.0074695 | 0.001872
72 | 0.99117 | -0.17005 | 0.012146 | 0.0030442
73 | 0.99407 | -0.1138 | 0.0062463 | 0.0015655
74 | 0.99427 | -0.11001 | 0.0023188 | 0.00058114
75 | 0.99482 | -0.099208 | 0.0061202 | 0.0015339
76 | 0.99452 | -0.10506 | 0.0050395 | 0.001263
77 | 0.99652 | -0.066404 | 0 | 0
78 | 0.99418 | -0.11156 | 0.0089671 | 0.0022474
79 | 0.99567 | -0.082823 | 0.0073403 | 0.0018397
80 | 0.99567 | -0.082797 | 0.0089955 | 0.0022545
81 | 0.99723 | -0.052869 | 0.0082485 | 0.0020673
82 | 0.99403 | -0.11449 | 0.0018571 | 0.00046544
83 | 0.99558 | -0.084568 | 0.0093224 | 0.0023364
84 | 0.99546 | -0.086909 | 0.0072909 | 0.0018273
85 | 0.99769 | -0.044054 | 0.0037442 | 0.00093838
86 | 0.99379 | -0.1192 | 0.0024878 | 0.00062351
87 | 0.99402 | -0.11442 | 0.0050344 | 0.0012618
88 | 0.99823 | -0.033705 | 0.0027292 | 0.00068399
89 | 0.99252 | -0.14377 | 0.001603 | 0.00040174
90 | 0.9927 | -0.1403 | 0.0012585 | 0.0003154
91 | 0.98202 | -0.34686 | 0.0031295 | 0.00078432
92 | 0.98215 | -0.34425 | 0.0090913 | 0.0022785
93 | 0.98193 | -0.34868 | 0.0028106 | 0.00070439
94 | 0.98186 | -0.3501 | 0.0024646 | 0.00061768
95 | 0.98177 | -0.35169 | 0.0079757 | 0.0019989
96 | 0.99607 | -0.07547 | 0.0081326 | 0.0020382
97 | 0.99604 | -0.075903 | 0.0061268 | 0.0015355
98 | 0.99615 | -0.073797 | 0.012508 | 0.0031348
99 | 0.9962 | -0.072878 | 0.0026293 | 0.00065898
100 | 0.9967 | -0.063275 | 0.0012984 | 0.00032542
101 | 0.99701 | -0.057329 | 0 | 0
102 | 0.99383 | -0.11801 | 0.0090635 | 0.0022715
103 | 0.99309 | -0.13229 | 0.0058671 | 0.0014704
104 | 0.99333 | -0.12826 | 0.0051901 | 0.0013007
105 | 0.99337 | -0.12758 | 0.002447 | 0.00061328
106 | 0.99339 | -0.12714 | 0.0024741 | 0.00062008
107 | 0.99343 | -0.12647 | 0.0024543 | 0.0006151
108 | 0.99346 | -0.12586 | 0.0027697 | 0.00069414
109 | 0.99235 | -0.14697 | 0.0042265 | 0.0010593
110 | 0.99238 | -0.14639 | 0.0054229 | 0.0013591
111 | 0.99466 | -0.1025 | 0.0062628 | 0.0015696
112 | 0.99523 | -0.091415 | 0 | 0
113 | 0.99274 | -0.13968 | 0.0018143 | 0.00045471
114 | 0.99288 | -0.1368 | 0.0015146 | 0.00037958
115 | 0.99282 | -0.13739 | 0.0042792 | 0.0010725
116 | 0.99278 | -0.13826 | 0.0033539 | 0.00084057
117 | 0.9921 | -0.15119 | 0.0036111 | 0.00090503
118 | 0.99178 | -0.15736 | 0.0073028 | 0.0018303
119 | 0.99241 | -0.14588 | 0.0042332 | 0.0010609
120 | 0.99252 | -0.14361 | 0.0045822 | 0.0011484
121 | 0.99255 | -0.14311 | 0.004229 | 0.0010599
122 | 0.99276 | -0.13899 | 0.0018758 | 0.00047012
123 | 0.99473 | -0.10108 | 0.003142 | 0.00078746
124 | 0.99354 | -0.12403 | 0.0018671 | 0.00046795
125 | 0.99339 | -0.12677 | 0.0040131 | 0.0010058
126 | 0.99882 | -0.022588 | 0.015108 | 0.0037865
127 | 0.99928 | -0.013744 | 0.0074659 | 0.0018711
128 | 0.99825 | -0.033396 | 0.0047636 | 0.0011939
129 | 0.99835 | -0.031635 | 0.0036801 | 0.00092232
130 | 0.99832 | -0.032171 | 0.0012274 | 0.00030761
131 | 0.99744 | -0.048944 | 0.0029998 | 0.00075182
132 | 0.99311 | -0.13228 | 0.0018709 | 0.0004689
133 | 0.99306 | -0.13331 | 0.0040149 | 0.0010062
134 | 0.99277 | -0.13878 | 0.0042337 | 0.0010611
135 | 0.99364 | -0.12231 | 0.0024501 | 0.00061405
136 | 0.99368 | -0.12163 | 0.0024263 | 0.0006081
137 | 0.99355 | -0.12402 | 0.0024299 | 0.000609
138 | 0.9938 | -0.11928 | 0.0024573 | 0.00061586
139 | 0.99352 | -0.12471 | 0.0024531 | 0.00061481
140 | 0.99389 | -0.11741 | 0.0046063 | 0.0011545
141 | 0.99399 | -0.11561 | 0.0015214 | 0.00038129
142 | 0.99469 | -0.10204 | 0.0028535 | 0.00071515
143 | 0.99445 | -0.10666 | 0.0015199 | 0.00038092
144 | 0.99472 | -0.10153 | 0.0015197 | 0.00038088
145 | 0.99425 | -0.11047 | 0.0046098 | 0.0011553
146 | 0.9942 | -0.11144 | 0.00152 | 0.00038096
147 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0024885 | -0.00062368 | 0.0024888 | 0.00062317 | 2.9162e-07 | -5.0923e-07 | 0.0037657 | 0.0037654 | 0.0037657 | 0.98335 | -0.32083 | 0.98348 | -0.31837 | 1.0345
1 | -0.0024888 | -0.00062317 | 0.0024892 | 0.00062253 | 3.6858e-07 | -6.44e-07 | 0.0037654 | 0.0037651 | 0.0037654 | 0.98348 | -0.31837 | 0.98364 | -0.31526 | 1.0345
2 | -0.037239 | -0.0093496 | 0.037269 | 0.009369 | 3.074e-05 | 1.9345e-05 | 0.05634 | 0.056339 | 0.05634 | 0.98364 | -0.31526 | 0.98452 | -0.29797 | 15.4779
3 | 0.03475 | 0.0087271 | -0.034736 | -0.0087184 | 1.3793e-05 | 8.6587e-06 | 0.052574 | 0.052574 | 0.052574 | 0.98364 | -0.31526 | 0.98321 | -0.32358 | 14.4435
4 | 0.034736 | 0.0087184 | -0.034718 | -0.0087075 | 1.737e-05 | 1.0904e-05 | 0.052574 | 0.052575 | 0.052575 | 0.98321 | -0.32358 | 0.98267 | -0.33407 | 14.4436
5 | 0.029339 | 0.0073594 | -0.029331 | -0.0073543 | 8.1719e-06 | 5.0902e-06 | 0.044429 | 0.044429 | 0.044429 | 0.98267 | -0.33407 | 0.98238 | -0.33991 | 12.2059
6 | -0.0082038 | -0.0020562 | 0.0082048 | 0.0020567 | 1.0629e-06 | 4.3796e-07 | 0.012298 | 0.012298 | 0.012298 | 0.99262 | -0.14196 | 0.99276 | -0.13924 | 3.3786
7 | 0.0082038 | 0.0020562 | -0.0082028 | -0.0020558 | 9.882e-07 | 4.0726e-07 | 0.012298 | 0.012298 | 0.012298 | 0.99262 | -0.14196 | 0.99249 | -0.14449 | 3.3786
8 | -0.04129 | -0.010362 | 0.041319 | 0.01038 | 2.8536e-05 | 1.8006e-05 | 0.061894 | 0.061893 | 0.061894 | 0.99276 | -0.13924 | 0.99351 | -0.12476 | 17.0037
9 | 0.033085 | 0.0083054 | -0.033063 | -0.0082912 | 2.2765e-05 | 1.4251e-05 | 0.049595 | 0.049596 | 0.049596 | 0.99276 | -0.13924 | 0.99201 | -0.15367 | 13.6252
10 | -0.043554 | -0.010944 | 0.043574 | 0.010957 | 2.026e-05 | 1.2808e-05 | 0.065838 | 0.065837 | 0.065838 | 0.98452 | -0.29797 | 0.98502 | -0.28823 | 18.0872
11 | 0.082832 | 0.020908 | -0.082763 | -0.020864 | 6.8729e-05 | 4.3835e-05 | 0.12464 | 0.12464 | 0.12464 | 0.9893 | -0.20522 | 0.98841 | -0.22256 | 34.242
12 | -0.082832 | -0.020908 | 0.082845 | 0.020916 | 1.2683e-05 | 8.0889e-06 | 0.12464 | 0.12464 | 0.12464 | 0.9893 | -0.20522 | 0.98947 | -0.20203 | 34.242
13 | 0.080528 | 0.020304 | -0.080486 | -0.020277 | 4.2314e-05 | 2.6982e-05 | 0.12128 | 0.12128 | 0.12128 | 0.98841 | -0.22256 | 0.98784 | -0.23355 | 33.3177
14 | 0.009549 | 0.0023936 | -0.0095471 | -0.0023927 | 1.9006e-06 | 9.008e-07 | 0.01436 | 0.014361 | 0.014361 | 0.98947 | -0.20203 | 0.98925 | -0.20621 | 3.9452
15 | -0.092394 | -0.02331 | 0.092485 | 0.023368 | 9.1796e-05 | 5.8586e-05 | 0.139 | 0.139 | 0.139 | 0.98947 | -0.20203 | 0.99054 | -0.1813 | 38.1871
16 | 0.025481 | 0.0063895 | -0.025476 | -0.0063862 | 5.271e-06 | 3.254e-06 | 0.038598 | 0.038598 | 0.038598 | 0.98238 | -0.33991 | 0.98215 | -0.34425 | 10.6039
17 | -0.048648 | -0.012217 | 0.048673 | 0.012233 | 2.5435e-05 | 1.6113e-05 | 0.07287 | 0.07287 | 0.07287 | 0.99351 | -0.12476 | 0.99407 | -0.1138 | 20.0193
18 | 0.023869 | 0.005987 | -0.023863 | -0.0059834 | 5.7466e-06 | 3.5235e-06 | 0.035805 | 0.035805 | 0.035805 | 0.99201 | -0.15367 | 0.99175 | -0.15873 | 9.8365
19 | -0.045657 | -0.011479 | 0.045663 | 0.011482 | 5.8205e-06 | 3.6836e-06 | 0.068984 | 0.068984 | 0.068984 | 0.98502 | -0.28823 | 0.98516 | -0.28556 | 18.9516
20 | 0.078416 | 0.019758 | -0.078385 | -0.019738 | 3.145e-05 | 2.0051e-05 | 0.11816 | 0.11816 | 0.11816 | 0.98784 | -0.23355 | 0.98741 | -0.24194 | 32.4612
21 | -0.09639 | -0.024347 | 0.096501 | 0.024417 | 0.00011074 | 7.0691e-05 | 0.14487 | 0.14487 | 0.14487 | 0.99054 | -0.1813 | 0.99178 | -0.15736 | 39.7986
22 | 0.070527 | 0.017754 | -0.070497 | -0.017735 | 2.9537e-05 | 1.8811e-05 | 0.10521 | 0.10521 | 0.10521 | 0.99777 | -0.042768 | 0.99731 | -0.051534 | 28.9032
23 | -0.072021 | -0.018128 | 0.072109 | 0.018185 | 8.8769e-05 | 5.6544e-05 | 0.10744 | 0.10743 | 0.10744 | 0.99777 | -0.042768 | 0.99911 | -0.017015 | 29.5151
24 | 0.069007 | 0.017361 | -0.068988 | -0.017349 | 1.928e-05 | 1.2276e-05 | 0.10298 | 0.10298 | 0.10298 | 0.99731 | -0.051534 | 0.99701 | -0.057383 | 28.2923
25 | -0.24207 | -0.061065 | 0.24212 | 0.061098 | 5.0638e-05 | 3.2286e-05 | 0.36066 | 0.36066 | 0.36066 | 0.99911 | -0.017015 | 0.99934 | -0.012647 | 33.0276
26 | 0.16996 | 0.042881 | -0.16995 | -0.042874 | 1.1342e-05 | 7.2032e-06 | 0.25323 | 0.25323 | 0.25323 | 0.99911 | -0.017015 | 0.99904 | -0.018409 | 23.1892
27 | 0.065241 | 0.01641 | -0.065227 | -0.016401 | 1.384e-05 | 8.8069e-06 | 0.097392 | 0.097392 | 0.097392 | 0.99701 | -0.057383 | 0.99678 | -0.061825 | 26.7561
28 | -0.24458 | -0.061715 | 0.24469 | 0.061784 | 0.00010802 | 6.8879e-05 | 0.36433 | 0.36433 | 0.36433 | 0.99934 | -0.012647 | 0.99982 | -0.0034283 | 33.3635
29 | 0.15371 | 0.038803 | -0.15369 | -0.038793 | 1.635e-05 | 1.0366e-05 | 0.22904 | 0.22904 | 0.22904 | 0.99904 | -0.018409 | 0.99892 | -0.02063 | 20.9739
30 | 0.062491 | 0.015715 | -0.062465 | -0.015699 | 2.5927e-05 | 1.649e-05 | 0.093307 | 0.093307 | 0.093307 | 0.99678 | -0.061825 | 0.99632 | -0.070515 | 25.6337
31 | -0.24715 | -0.062402 | 0.24719 | 0.062427 | 4.0602e-05 | 2.5891e-05 | 0.368 | 0.368 | 0.368 | 0.99982 | -0.0034283 | 1 | 0 | 33.6993
32 | 0.15123 | 0.038176 | -0.15119 | -0.038149 | 4.186e-05 | 2.6531e-05 | 0.22537 | 0.22537 | 0.22537 | 0.99892 | -0.02063 | 0.99862 | -0.02641 | 20.6383
33 | 0.059583 | 0.014977 | -0.059572 | -0.01497 | 1.0924e-05 | 6.9436e-06 | 0.089003 | 0.089003 | 0.089003 | 0.99632 | -0.070515 | 0.99613 | -0.074356 | 24.4515
34 | 0.30062 | 0.076224 | -0.30042 | -0.076097 | 0.00019846 | 0.0001267 | 0.44763 | 0.44763 | 0.44763 | 1 | 0 | 0.99928 | -0.013744 | 40.992
35 | 0.14865 | 0.037514 | -0.14861 | -0.037491 | 3.719e-05 | 2.3564e-05 | 0.22159 | 0.22159 | 0.22159 | 0.99862 | -0.02641 | 0.99835 | -0.031635 | 20.2924
36 | 0.056667 | 0.014242 | -0.056646 | -0.014229 | 2.0192e-05 | 1.2825e-05 | 0.084663 | 0.084663 | 0.084663 | 0.99613 | -0.074356 | 0.99574 | -0.081823 | 23.259
37 | -0.052221 | -0.013126 | 0.052238 | 0.013137 | 1.6426e-05 | 1.0423e-05 | 0.07889 | 0.07889 | 0.07889 | 0.98516 | -0.28556 | 0.9855 | -0.27897 | 21.6732
38 | -0.059397 | -0.014931 | 0.059416 | 0.014943 | 1.9151e-05 | 1.2176e-05 | 0.0897 | 0.0897 | 0.0897 | 0.9855 | -0.27897 | 0.98585 | -0.27222 | 24.6429
39 | -0.06936 | -0.017435 | 0.069389 | 0.017454 | 2.8988e-05 | 1.8462e-05 | 0.10471 | 0.10471 | 0.10471 | 0.98585 | -0.27222 | 0.9863 | -0.26347 | 28.7663
40 | 0.0033612 | 0.00084211 | -0.0033611 | -0.00084216 | 7.1934e-08 | -5.134e-08 | 0.0050423 | 0.0050423 | 0.0050423 | 0.99188 | -0.15626 | 0.99186 | -0.15671 | 1.3853
41 | -0.0051742 | -0.0012965 | 0.0051743 | 0.0012965 | 1.463e-07 | 1.0056e-08 | 0.0077622 | 0.0077622 | 0.0077622 | 0.99188 | -0.15626 | 0.99191 | -0.15566 | 2.1325
42 | 0.0017396 | 0.00043578 | -0.0017395 | -0.00043597 | 4.379e-08 | -1.9325e-07 | 0.0026097 | 0.0026098 | 0.0026098 | 0.99186 | -0.15671 | 0.99183 | -0.15724 | 0.71697
43 | -0.0080499 | -0.0020172 | 0.0080506 | 0.0020175 | 6.0809e-07 | 2.4563e-07 | 0.012076 | 0.012076 | 0.012076 | 0.99191 | -0.15566 | 0.99199 | -0.15408 | 3.3176
44 | -0.00969 | -0.0024283 | 0.0096904 | 0.0024285 | 4.5148e-07 | 2.1538e-07 | 0.014535 | 0.014535 | 0.014535 | 0.99199 | -0.15408 | 0.99204 | -0.1531 | 3.9932
45 | -0.014013 | -0.003512 | 0.014015 | 0.0035128 | 1.4924e-06 | 8.3884e-07 | 0.021019 | 0.021019 | 0.021019 | 0.99204 | -0.1531 | 0.99216 | -0.15087 | 5.7746
46 | -0.016387 | -0.0041073 | 0.016387 | 0.0041076 | 4.1039e-07 | 2.3925e-07 | 0.024577 | 0.024577 | 0.024577 | 0.99216 | -0.15087 | 0.99219 | -0.15034 | 6.7519
47 | -0.017626 | -0.004418 | 0.017628 | 0.0044191 | 1.9193e-06 | 1.1337e-06 | 0.026434 | 0.026434 | 0.026434 | 0.99219 | -0.15034 | 0.9923 | -0.14805 | 7.2622
48 | -0.021293 | -0.0053377 | 0.021294 | 0.0053385 | 1.2956e-06 | 7.8538e-07 | 0.03193 | 0.03193 | 0.03193 | 0.9923 | -0.14805 | 0.99237 | -0.14678 | 8.7721
49 | -0.022545 | -0.0056518 | 0.022547 | 0.005653 | 1.9079e-06 | 1.1635e-06 | 0.033805 | 0.033805 | 0.033805 | 0.99237 | -0.14678 | 0.99246 | -0.145 | 9.2872
50 | -0.023874 | -0.0059857 | 0.023875 | 0.0059866 | 1.403e-06 | 8.602e-07 | 0.035796 | 0.035796 | 0.035796 | 0.99246 | -0.145 | 0.99252 | -0.14377 | 9.834
51 | -0.0074394 | -0.0018645 | 0.0074394 | 0.0018645 | 4.6721e-08 | 1.6827e-08 | 0.011125 | 0.011125 | 0.011125 | 0.99502 | -0.095517 | 0.99502 | -0.095385 | 3.0564
52 | 0.0063779 | 0.0015985 | -0.0063777 | -0.0015984 | 2.634e-07 | 6.8295e-08 | 0.009538 | 0.009538 | 0.009538 | 0.99502 | -0.095517 | 0.99497 | -0.096384 | 2.6203
53 | -0.0083176 | -0.0020846 | 0.0083178 | 0.0020847 | 2.0266e-07 | 8.4333e-08 | 0.012439 | 0.012439 | 0.012439 | 0.99502 | -0.095385 | 0.99505 | -0.094874 | 3.4172
54 | 0.0052377 | 0.0013127 | -0.0052377 | -0.0013127 | 3.2066e-08 | 2.4228e-09 | 0.0078332 | 0.0078332 | 0.0078332 | 0.99497 | -0.096384 | 0.99496 | -0.096513 | 2.152
55 | -0.0098958 | -0.0024801 | 0.0098961 | 0.0024803 | 2.8141e-07 | 1.3559e-07 | 0.014798 | 0.014798 | 0.014798 | 0.99505 | -0.094874 | 0.99508 | -0.094277 | 4.0655
56 | -0.015598 | -0.0039092 | 0.015598 | 0.0039097 | 7.7687e-07 | 4.4773e-07 | 0.023324 | 0.023324 | 0.023324 | 0.99508 | -0.094277 | 0.99513 | -0.093231 | 6.4078
57 | -0.02387 | -0.0059828 | 0.023877 | 0.0059872 | 7.1925e-06 | 4.4075e-06 | 0.035693 | 0.035693 | 0.035693 | 0.99513 | -0.093231 | 0.99546 | -0.086909 | 9.8057
58 | -0.037141 | -0.0093214 | 0.03715 | 0.009327 | 8.9807e-06 | 5.6474e-06 | 0.055633 | 0.055633 | 0.055633 | 0.99349 | -0.12513 | 0.99375 | -0.12006 | 15.2839
59 | 0.035621 | 0.0089404 | -0.035618 | -0.0089385 | 3.0904e-06 | 1.9404e-06 | 0.053357 | 0.053357 | 0.053357 | 0.99349 | -0.12513 | 0.99339 | -0.12695 | 14.6585
60 | -0.038402 | -0.0096409 | 0.038405 | 0.0096423 | 2.155e-06 | 1.3567e-06 | 0.057509 | 0.057509 | 0.057509 | 0.99375 | -0.12006 | 0.99381 | -0.11888 | 15.7991
61 | 0.034276 | 0.0086022 | -0.034272 | -0.0085994 | 4.3883e-06 | 2.7511e-06 | 0.051347 | 0.051347 | 0.051347 | 0.99339 | -0.12695 | 0.99325 | -0.12963 | 14.1062
62 | -0.039955 | -0.010031 | 0.039962 | 0.010035 | 6.6592e-06 | 4.1976e-06 | 0.05983 | 0.05983 | 0.05983 | 0.99381 | -0.11888 | 0.99399 | -0.11539 | 16.4368
63 | 0.033012 | 0.0082838 | -0.03301 | -0.0082823 | 2.344e-06 | 1.4671e-06 | 0.04946 | 0.04946 | 0.04946 | 0.99325 | -0.12963 | 0.99318 | -0.13112 | 13.588
64 | -0.041212 | -0.010348 | 0.041217 | 0.010351 | 4.6669e-06 | 2.9444e-06 | 0.061702 | 0.061702 | 0.061702 | 0.99399 | -0.11539 | 0.99411 | -0.11302 | 16.9511
65 | 0.031589 | 0.0079261 | -0.031582 | -0.0079219 | 6.6919e-06 | 4.1798e-06 | 0.04733 | 0.04733 | 0.04733 | 0.99318 | -0.13112 | 0.99295 | -0.13557 | 13.0029
66 | -0.04288 | -0.010768 | 0.042905 | 0.010784 | 2.4445e-05 | 1.5439e-05 | 0.064192 | 0.064192 | 0.064192 | 0.99411 | -0.11302 | 0.99473 | -0.10108 | 17.6352
67 | 0.030076 | 0.0075446 | -0.030075 | -0.0075435 | 1.7705e-06 | 1.1031e-06 | 0.045075 | 0.045075 | 0.045075 | 0.99295 | -0.13557 | 0.99288 | -0.1368 | 12.3831
68 | 0.053194 | 0.013364 | -0.05319 | -0.013361 | 4.4721e-06 | 2.8376e-06 | 0.079504 | 0.079504 | 0.079504 | 0.99574 | -0.081823 | 0.99565 | -0.083584 | 21.8417
69 | 0.051669 | 0.01298 | -0.051654 | -0.01297 | 1.5674e-05 | 9.9405e-06 | 0.077232 | 0.077232 | 0.077232 | 0.99565 | -0.083584 | 0.99532 | -0.089943 | 21.2175
70 | 0.050137 | 0.01259 | -0.050131 | -0.012586 | 6.0682e-06 | 3.8463e-06 | 0.074964 | 0.074964 | 0.074964 | 0.99532 | -0.089943 | 0.99518 | -0.09248 | 20.5944
71 | 0.047274 | 0.01187 | -0.047267 | -0.011865 | 7.7128e-06 | 4.8828e-06 | 0.070693 | 0.070693 | 0.070693 | 0.99518 | -0.09248 | 0.99501 | -0.095901 | 19.4212
72 | -0.074084 | -0.01863 | 0.07413 | 0.01866 | 4.5907e-05 | 2.9255e-05 | 0.11179 | 0.11179 | 0.11179 | 0.9863 | -0.26347 | 0.98696 | -0.25051 | 30.7122
73 | -0.076286 | -0.0192 | 0.076318 | 0.01922 | 3.1268e-05 | 1.9931e-05 | 0.11504 | 0.11504 | 0.11504 | 0.98696 | -0.25051 | 0.98741 | -0.24194 | 31.6054
74 | 0.045754 | 0.011486 | -0.045741 | -0.011478 | 1.2277e-05 | 7.7667e-06 | 0.06843 | 0.06843 | 0.06843 | 0.99501 | -0.095901 | 0.99472 | -0.10153 | 18.7995
75 | 0.019625 | 0.0049212 | -0.019619 | -0.0049179 | 5.4208e-06 | 3.2543e-06 | 0.029446 | 0.029446 | 0.029446 | 0.99175 | -0.15873 | 0.99145 | -0.16452 | 8.0895
76 | 0.01215 | 0.0030459 | -0.012146 | -0.0030442 | 3.1993e-06 | 1.7168e-06 | 0.018235 | 0.018235 | 0.018235 | 0.99145 | -0.16452 | 0.99117 | -0.17005 | 5.0097
77 | -0.054919 | -0.013798 | 0.054929 | 0.013805 | 9.9553e-06 | 6.3205e-06 | 0.08222 | 0.08222 | 0.08222 | 0.99407 | -0.1138 | 0.99427 | -0.11001 | 22.588
78 | -0.057248 | -0.014386 | 0.057269 | 0.014399 | 2.0532e-05 | 1.3043e-05 | 0.085691 | 0.085691 | 0.085691 | 0.99427 | -0.11001 | 0.99466 | -0.1025 | 23.5414
79 | 0.05901 | 0.014823 | -0.058993 | -0.014812 | 1.6474e-05 | 1.047e-05 | 0.088276 | 0.088276 | 0.088276 | 0.99482 | -0.099208 | 0.99452 | -0.10506 | 24.2518
80 | -0.06513 | -0.016357 | 0.065232 | 0.016422 | 0.00010211 | 6.498e-05 | 0.097431 | 0.097431 | 0.097431 | 0.99482 | -0.099208 | 0.99652 | -0.066404 | 26.7667
81 | 0.053954 | 0.013549 | -0.053937 | -0.013539 | 1.6716e-05 | 1.061e-05 | 0.080736 | 0.080736 | 0.080736 | 0.99452 | -0.10506 | 0.99418 | -0.11156 | 22.1803
82 | 0.15224 | 0.038604 | -0.15212 | -0.038528 | 0.00012005 | 7.6106e-05 | 0.22748 | 0.22748 | 0.22748 | 0.99652 | -0.066404 | 0.99567 | -0.082823 | 20.8316
83 | 0.040201 | 0.010093 | -0.04017 | -0.010073 | 3.1408e-05 | 1.9799e-05 | 0.060035 | 0.060035 | 0.060035 | 0.99652 | -0.066404 | 0.99567 | -0.082797 | 16.4931
84 | -0.25767 | -0.065118 | 0.25784 | 0.065225 | 0.00016734 | 0.00010674 | 0.38495 | 0.38495 | 0.38495 | 0.99652 | -0.066404 | 0.99723 | -0.052869 | 35.2515
85 | 0.04497 | 0.011291 | -0.044964 | -0.011287 | 6.2907e-06 | 3.978e-06 | 0.067315 | 0.067315 | 0.067315 | 0.99418 | -0.11156 | 0.99403 | -0.11449 | 18.4931
86 | 0.14478 | 0.036688 | -0.14476 | -0.03668 | 1.2141e-05 | 7.7342e-06 | 0.21651 | 0.21651 | 0.21651 | 0.99567 | -0.082823 | 0.99558 | -0.084568 | 29.7406
87 | 0.031174 | 0.0078182 | -0.031168 | -0.0078144 | 6.109e-06 | 3.8122e-06 | 0.046591 | 0.046591 | 0.046591 | 0.99567 | -0.082797 | 0.99546 | -0.086909 | 12.7998
88 | -0.26609 | -0.067292 | 0.2662 | 0.067364 | 0.00011257 | 7.182e-05 | 0.39725 | 0.39725 | 0.39725 | 0.99723 | -0.052869 | 0.99769 | -0.044054 | 36.3786
89 | 0.043107 | 0.010822 | -0.043097 | -0.010816 | 9.6815e-06 | 6.1158e-06 | 0.064535 | 0.064535 | 0.064535 | 0.99403 | -0.11449 | 0.99379 | -0.1192 | 17.7294
90 | 0.13544 | 0.034344 | -0.13525 | -0.03422 | 0.00019408 | 0.00012405 | 0.20258 | 0.20258 | 0.20258 | 0.99558 | -0.084568 | 0.99402 | -0.11442 | 55.6533
91 | -0.26994 | -0.068302 | 0.27008 | 0.068388 | 0.00013413 | 8.5583e-05 | 0.40284 | 0.40284 | 0.40284 | 0.99769 | -0.044054 | 0.99823 | -0.033705 | 36.8899
92 | 0.040609 | 0.010192 | -0.0406 | -0.010186 | 9.3647e-06 | 5.9059e-06 | 0.06081 | 0.06081 | 0.06081 | 0.99379 | -0.1192 | 0.99354 | -0.12403 | 16.706
93 | 0.13021 | 0.032958 | -0.13019 | -0.032944 | 2.2418e-05 | 1.4327e-05 | 0.19504 | 0.19504 | 0.19504 | 0.99402 | -0.11442 | 0.99383 | -0.11801 | 53.5828
94 | -0.27281 | -0.069072 | 0.27281 | 0.069074 | 4.0561e-06 | 2.5882e-06 | 0.40691 | 0.40691 | 0.40691 | 0.99823 | -0.033705 | 0.99825 | -0.033396 | 37.2625
95 | -0.025478 | -0.0063883 | 0.025483 | 0.0063909 | 4.2152e-06 | 2.5981e-06 | 0.038199 | 0.038199 | 0.038199 | 0.99252 | -0.14377 | 0.9927 | -0.1403 | 10.4942
96 | -0.026741 | -0.0067063 | 0.026742 | 0.0067068 | 7.8578e-07 | 4.8604e-07 | 0.040085 | 0.040085 | 0.040085 | 0.9927 | -0.1403 | 0.99274 | -0.13968 | 11.0124
97 | -0.016383 | -0.0041065 | 0.016385 | 0.0041077 | 2.0309e-06 | 1.1886e-06 | 0.024824 | 0.024824 | 0.024824 | 0.98202 | -0.34686 | 0.98215 | -0.34425 | 6.8199
98 | 0.013253 | 0.0033222 | -0.013252 | -0.0033216 | 1.1545e-06 | 6.4233e-07 | 0.020082 | 0.020082 | 0.020082 | 0.98202 | -0.34686 | 0.98193 | -0.34868 | 5.5172
99 | 0.010442 | 0.0026172 | -0.010441 | -0.0026168 | 7.0346e-07 | 3.5545e-07 | 0.015823 | 0.015823 | 0.015823 | 0.98193 | -0.34868 | 0.98186 | -0.3501 | 4.3471
100 | 0.0079763 | 0.0019992 | -0.0079757 | -0.0019989 | 6.0479e-07 | 2.4749e-07 | 0.012088 | 0.012088 | 0.012088 | 0.98186 | -0.3501 | 0.98177 | -0.35169 | 3.321
101 | 0.0061269 | 0.0015356 | -0.0061268 | -0.0015355 | 1.2651e-07 | 2.8552e-08 | 0.009153 | 0.009153 | 0.009153 | 0.99607 | -0.07547 | 0.99604 | -0.075903 | 2.5146
102 | -0.01426 | -0.0035738 | 0.014261 | 0.0035744 | 1.1368e-06 | 6.406e-07 | 0.021302 | 0.021302 | 0.021302 | 0.99607 | -0.07547 | 0.99615 | -0.073797 | 5.8523
103 | -0.026769 | -0.0067092 | 0.02677 | 0.0067099 | 1.1717e-06 | 7.2442e-07 | 0.039986 | 0.039986 | 0.039986 | 0.99615 | -0.073797 | 0.9962 | -0.072878 | 10.9852
104 | -0.029399 | -0.0073689 | 0.029413 | 0.0073773 | 1.3457e-05 | 8.3703e-06 | 0.043913 | 0.043913 | 0.043913 | 0.9962 | -0.072878 | 0.9967 | -0.063275 | 12.0641
105 | -0.030711 | -0.0077027 | 0.03072 | 0.0077081 | 8.7069e-06 | 5.4285e-06 | 0.045852 | 0.045852 | 0.045852 | 0.9967 | -0.063275 | 0.99701 | -0.057329 | 12.5966
106 | 0.10981 | 0.027689 | -0.10963 | -0.027575 | 0.00017883 | 0.00011422 | 0.16395 | 0.16395 | 0.16395 | 0.99701 | -0.057329 | 0.99523 | -0.091415 | 45.0417
107 | -0.14053 | -0.035397 | 0.14059 | 0.035433 | 5.6371e-05 | 3.6033e-05 | 0.2098 | 0.2098 | 0.2098 | 0.99701 | -0.057329 | 0.99744 | -0.048944 | 57.6383
108 | 0.12113 | 0.030672 | -0.12105 | -0.030619 | 8.2976e-05 | 5.3017e-05 | 0.18147 | 0.18147 | 0.18147 | 0.99383 | -0.11801 | 0.99309 | -0.13229 | 49.8548
109 | 0.11518 | 0.029149 | -0.11515 | -0.029131 | 2.8222e-05 | 1.803e-05 | 0.17268 | 0.17268 | 0.17268 | 0.99309 | -0.13229 | 0.99282 | -0.13739 | 47.4396
110 | -0.0051901 | -0.0013007 | 0.0051902 | 0.0013008 | 1.6742e-07 | 1.1534e-08 | 0.0077747 | 0.0077747 | 0.0077747 | 0.99333 | -0.12826 | 0.99337 | -0.12758 | 2.1359
111 | -0.0076372 | -0.001914 | 0.0076374 | 0.0019141 | 1.6052e-07 | 6.039e-08 | 0.01144 | 0.01144 | 0.01144 | 0.99337 | -0.12758 | 0.99339 | -0.12714 | 3.1429
112 | -0.010112 | -0.0025342 | 0.010112 | 0.0025343 | 3.217e-07 | 1.5748e-07 | 0.015146 | 0.015146 | 0.015146 | 0.99339 | -0.12714 | 0.99343 | -0.12647 | 4.1611
113 | -0.012566 | -0.0031494 | 0.012567 | 0.0031496 | 3.6869e-07 | 2.0003e-07 | 0.018822 | 0.018822 | 0.018822 | 0.99343 | -0.12647 | 0.99346 | -0.12586 | 5.171
114 | -0.015336 | -0.0038438 | 0.015337 | 0.0038443 | 8.3598e-07 | 4.8032e-07 | 0.022971 | 0.022971 | 0.022971 | 0.99346 | -0.12586 | 0.99352 | -0.12471 | 6.3107
115 | -0.0042265 | -0.0010593 | 0.0042266 | 0.0010592 | 1.1696e-07 | -2.5473e-08 | 0.0063375 | 0.0063375 | 0.0063375 | 0.99235 | -0.14697 | 0.99238 | -0.14639 | 1.7411
116 | -0.0096495 | -0.0024183 | 0.0096497 | 0.0024185 | 2.342e-07 | 1.1134e-07 | 0.014469 | 0.014469 | 0.014469 | 0.99238 | -0.14639 | 0.99241 | -0.14588 | 3.975
117 | -0.063532 | -0.015969 | 0.063565 | 0.01599 | 3.3634e-05 | 2.1397e-05 | 0.09506 | 0.09506 | 0.09506 | 0.99466 | -0.1025 | 0.99523 | -0.091415 | 26.1153
118 | 0.046068 | 0.011585 | -0.046047 | -0.011571 | 2.1249e-05 | 1.3444e-05 | 0.068892 | 0.068892 | 0.068892 | 0.99523 | -0.091415 | 0.99473 | -0.10108 | 18.9264
119 | -0.028556 | -0.0071615 | 0.02856 | 0.0071639 | 3.9186e-06 | 2.4342e-06 | 0.042805 | 0.042805 | 0.042805 | 0.99274 | -0.13968 | 0.99288 | -0.1368 | 11.7595
120 | 0.11087 | 0.028058 | -0.11087 | -0.028055 | 4.6117e-06 | 2.9457e-06 | 0.16627 | 0.16627 | 0.16627 | 0.99282 | -0.13739 | 0.99278 | -0.13826 | 45.6776
121 | 0.10751 | 0.027215 | -0.10745 | -0.027172 | 6.6667e-05 | 4.2579e-05 | 0.16124 | 0.16124 | 0.16124 | 0.99278 | -0.13826 | 0.9921 | -0.15119 | 44.2966
122 | 0.10383 | 0.026267 | -0.1038 | -0.026248 | 3.0736e-05 | 1.9628e-05 | 0.15582 | 0.15582 | 0.15582 | 0.9921 | -0.15119 | 0.99178 | -0.15736 | 42.8087
123 | -0.013883 | -0.0034794 | 0.013884 | 0.0034802 | 1.4987e-06 | 8.3997e-07 | 0.020816 | 0.020816 | 0.020816 | 0.99241 | -0.14588 | 0.99252 | -0.14361 | 5.7187
124 | -0.018467 | -0.0046286 | 0.018467 | 0.0046289 | 4.3906e-07 | 2.6126e-07 | 0.027686 | 0.027686 | 0.027686 | 0.99252 | -0.14361 | 0.99255 | -0.14311 | 7.606
125 | -0.022696 | -0.0056888 | 0.022701 | 0.0056915 | 4.4604e-06 | 2.7218e-06 | 0.034026 | 0.034026 | 0.034026 | 0.99255 | -0.14311 | 0.99276 | -0.13899 | 9.3478
126 | -0.024576 | -0.0061616 | 0.024577 | 0.0061618 | 2.4205e-07 | 1.4876e-07 | 0.036837 | 0.036837 | 0.036837 | 0.99276 | -0.13899 | 0.99277 | -0.13878 | 10.1202
127 | 0.038733 | 0.0097183 | -0.038727 | -0.0097151 | 5.054e-06 | 3.1827e-06 | 0.058013 | 0.058013 | 0.058013 | 0.99354 | -0.12403 | 0.99339 | -0.12677 | 15.9378
128 | 0.034714 | 0.0087094 | -0.034705 | -0.0087037 | 9.119e-06 | 5.7198e-06 | 0.052002 | 0.052002 | 0.052002 | 0.99339 | -0.12677 | 0.99311 | -0.13228 | 14.2863
129 | -0.29283 | -0.074147 | 0.29295 | 0.074226 | 0.0001244 | 7.9413e-05 | 0.43651 | 0.43651 | 0.43651 | 0.99882 | -0.022588 | 0.99928 | -0.013744 | 39.9739
130 | 0.27772 | 0.07036 | -0.27757 | -0.070268 | 0.0001441 | 9.1962e-05 | 0.41401 | 0.41401 | 0.41401 | 0.99882 | -0.022588 | 0.99825 | -0.033396 | 37.9127
131 | 0.14493 | 0.036568 | -0.14493 | -0.036566 | 3.7185e-06 | 2.3549e-06 | 0.21611 | 0.21611 | 0.21611 | 0.99835 | -0.031635 | 0.99832 | -0.032171 | 19.7901
132 | 0.1437 | 0.036258 | -0.14359 | -0.036185 | 0.00011532 | 7.3458e-05 | 0.21428 | 0.21428 | 0.21428 | 0.99832 | -0.032171 | 0.99744 | -0.048944 | 29.4339
133 | 0.032834 | 0.0082348 | -0.032833 | -0.0082337 | 1.6017e-06 | 1.0023e-06 | 0.049199 | 0.049199 | 0.049199 | 0.99311 | -0.13228 | 0.99306 | -0.13331 | 13.5162
134 | 0.028818 | 0.0072275 | -0.02881 | -0.0072229 | 7.5206e-06 | 4.6741e-06 | 0.043183 | 0.043183 | 0.043183 | 0.99306 | -0.13331 | 0.99277 | -0.13878 | 11.8635
135 | -0.022672 | -0.0056835 | 0.022673 | 0.0056839 | 7.3776e-07 | 4.5006e-07 | 0.033953 | 0.033953 | 0.033953 | 0.99364 | -0.12231 | 0.99368 | -0.12163 | 9.3278
136 | 0.020222 | 0.0050694 | -0.020221 | -0.0050684 | 1.6495e-06 | 9.9355e-07 | 0.030284 | 0.030284 | 0.030284 | 0.99364 | -0.12231 | 0.99355 | -0.12402 | 8.3198
137 | -0.025099 | -0.006292 | 0.025102 | 0.0062937 | 2.8093e-06 | 1.7292e-06 | 0.037587 | 0.037587 | 0.037587 | 0.99368 | -0.12163 | 0.9938 | -0.11928 | 10.326
138 | 0.017791 | 0.0044594 | -0.01779 | -0.0044591 | 5.8664e-07 | 3.4691e-07 | 0.026645 | 0.026645 | 0.026645 | 0.99355 | -0.12402 | 0.99352 | -0.12471 | 7.32
139 | -0.02756 | -0.0069096 | 0.027562 | 0.0069111 | 2.4469e-06 | 1.5164e-06 | 0.041266 | 0.041266 | 0.041266 | 0.9938 | -0.11928 | 0.99389 | -0.11741 | 11.3368
140 | -0.032168 | -0.0080656 | 0.032171 | 0.0080673 | 2.7672e-06 | 1.7298e-06 | 0.048162 | 0.048162 | 0.048162 | 0.99389 | -0.11741 | 0.99399 | -0.11561 | 13.2314
141 | -0.033693 | -0.0084486 | 0.033699 | 0.0084528 | 6.6904e-06 | 4.1909e-06 | 0.05044 | 0.05044 | 0.05044 | 0.99399 | -0.11561 | 0.9942 | -0.11144 | 13.8571
142 | 0.041367 | 0.010381 | -0.041358 | -0.010376 | 9.0956e-06 | 5.739e-06 | 0.061888 | 0.061888 | 0.061888 | 0.99469 | -0.10204 | 0.99445 | -0.10666 | 17.0022
143 | -0.04422 | -0.011096 | 0.044221 | 0.011097 | 1.0886e-06 | 6.8806e-07 | 0.066157 | 0.066157 | 0.066157 | 0.99469 | -0.10204 | 0.99472 | -0.10153 | 18.175
144 | 0.039838 | 0.0099947 | -0.039831 | -0.0099901 | 7.2438e-06 | 4.5655e-06 | 0.059614 | 0.059614 | 0.059614 | 0.99445 | -0.10666 | 0.99425 | -0.11047 | 16.3775
145 | 0.035221 | 0.0088348 | -0.035219 | -0.0088337 | 1.6331e-06 | 1.0249e-06 | 0.052715 | 0.052715 | 0.052715 | 0.99425 | -0.11047 | 0.9942 | -0.11144 | 14.4821

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.55319 | 0.13959

## res_load
| p_mw | q_mvar
0 | 0.0024885 | 0.00062368
1 | 0.0053791 | 0.0013481
2 | 0.0082028 | 0.0020558
3 | 0.0062843 | 0.001575
4 | 0.0022347 | 0.00056006
5 | 0.0038498 | 0.00096485
6 | 0.007329 | 0.0018368
7 | 0.0091938 | 0.0023042
8 | 0.0020827 | 0.00052198
9 | 0.0020698 | 0.00051875
10 | 0.0095471 | 0.0023927
11 | 0.0039047 | 0.00097861
12 | 0.0014937 | 0.00037435
13 | 0.0014902 | 0.00037348
14 | 0.0037467 | 0.00093902
15 | 0.0024637 | 0.00061746
16 | 0.016242 | 0.0040706
17 | 0.0027368 | 0.0006859
18 | 0.0024639 | 0.00061751
19 | 0.0024607 | 0.0006167
20 | 0.0028814 | 0.00072214
21 | 0.0037285 | 0.00093445
22 | 0.0025347 | 0.00063525
23 | 0.0029057 | 0.00072823
24 | 0.0065588 | 0.0016438
25 | 0.0071593 | 0.0017943
26 | 0.0099439 | 0.0024922
27 | 0.001813 | 0.00045439
28 | 0.0016215 | 0.00040639
29 | 0.0028756 | 0.00072069
30 | 0.0017395 | 0.00043597
31 | 0.0016394 | 0.00041088
32 | 0.004323 | 0.0010834
33 | 0.0023721 | 0.0005945
34 | 0.0012385 | 0.00031041
35 | 0.0036651 | 0.00091856
36 | 0.0012505 | 0.00031339
37 | 0.0013275 | 0.00033269
38 | 0.0010614 | 0.00026602
39 | 0.00087814 | 0.00022008
40 | 0.00114 | 0.00028571
41 | 0.001578 | 0.00039548
42 | 0.0052377 | 0.0013127
43 | 0.0057015 | 0.0014289
44 | 0.0082717 | 0.0020731
45 | 0.00152 | 0.00038094
46 | 0.0012523 | 0.00031386
47 | 0.001342 | 0.00033634
48 | 0.0015503 | 0.00038854
49 | 0.0012593 | 0.00031561
50 | 0.0012507 | 0.00031345
51 | 0.0014215 | 0.00035626
52 | 0.0016636 | 0.00041693
53 | 0.0015054 | 0.00037728
54 | 0.0034523 | 0.00086523
55 | 0.0015202 | 0.00038101
56 | 0.0015171 | 0.00038022
57 | 0.0028563 | 0.00071585
58 | 0.0046949 | 0.0011766
59 | 0.0021565 | 0.00054046
60 | 0.0020672 | 0.00051808
61 | 0.0015131 | 0.00037921
62 | 0.0042384 | 0.0010623
63 | 0.0074695 | 0.001872
64 | 0.012146 | 0.0030442
65 | 0.0062463 | 0.0015655
66 | 0.0023188 | 0.00058114
67 | 0.0061202 | 0.0015339
68 | 0.0050395 | 0.001263
69 | 0.0089671 | 0.0022474
70 | 0.0073403 | 0.0018397
71 | 0.0089955 | 0.0022545
72 | 0.0082485 | 0.0020673
73 | 0.0018571 | 0.00046544
74 | 0.0093224 | 0.0023364
75 | 0.0072909 | 0.0018273
76 | 0.0037442 | 0.00093838
77 | 0.0024878 | 0.00062351
78 | 0.0050344 | 0.0012618
79 | 0.0027292 | 0.00068399
80 | 0.001603 | 0.00040174
81 | 0.0012585 | 0.0003154
82 | 0.0031295 | 0.00078432
83 | 0.0090913 | 0.0022785
84 | 0.0028106 | 0.00070439
85 | 0.0024646 | 0.00061768
86 | 0.0079757 | 0.0019989
87 | 0.0081326 | 0.0020382
88 | 0.0061268 | 0.0015355
89 | 0.012508 | 0.0031348
90 | 0.0026293 | 0.00065898
91 | 0.0012984 | 0.00032542
92 | 0.0090635 | 0.0022715
93 | 0.0058671 | 0.0014704
94 | 0.0051901 | 0.0013007
95 | 0.002447 | 0.00061328
96 | 0.0024741 | 0.00062008
97 | 0.0024543 | 0.0006151
98 | 0.0027697 | 0.00069414
99 | 0.0042265 | 0.0010593
100 | 0.0054229 | 0.0013591
101 | 0.0062628 | 0.0015696
102 | 0.0018143 | 0.00045471
103 | 0.0015146 | 0.00037958
104 | 0.0042792 | 0.0010725
105 | 0.0033539 | 0.00084057
106 | 0.0036111 | 0.00090503
107 | 0.0073028 | 0.0018303
108 | 0.0042332 | 0.0010609
109 | 0.0045822 | 0.0011484
110 | 0.004229 | 0.0010599
111 | 0.0018758 | 0.00047012
112 | 0.003142 | 0.00078746
113 | 0.0018671 | 0.00046795
114 | 0.0040131 | 0.0010058
115 | 0.015108 | 0.0037865
116 | 0.0074659 | 0.0018711
117 | 0.0047636 | 0.0011939
118 | 0.0036801 | 0.00092232
119 | 0.0012274 | 0.00030761
120 | 0.0029998 | 0.00075182
121 | 0.0018709 | 0.0004689
122 | 0.0040149 | 0.0010062
123 | 0.0042337 | 0.0010611
124 | 0.0024501 | 0.00061405
125 | 0.0024263 | 0.0006081
126 | 0.0024299 | 0.000609
127 | 0.0024573 | 0.00061586
128 | 0.0024531 | 0.00061481
129 | 0.0046063 | 0.0011545
130 | 0.0015214 | 0.00038129
131 | 0.0028535 | 0.00071515
132 | 0.0015199 | 0.00038092
133 | 0.0015197 | 0.00038088
134 | 0.0046098 | 0.0011553
135 | 0.00152 | 0.00038096

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1