## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-241_1_3_node_2 | 0.4 | n |  | TRUE
1 | bus_LV_2701-241_1_3_node_74 | 0.4 | n |  | TRUE
2 | bus_LV_2701-241_1_3_node_65 | 0.4 | n |  | TRUE
3 | bus_LV_2701-241_1_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2701-241_1_3_node_73 | 0.4 | n |  | TRUE
5 | bus_LV_2701-241_1_3_node_55 | 0.4 | n |  | TRUE
6 | bus_LV_2701-241_1_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2701-241_1_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2701-241_1_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_2701-241_1_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2701-241_1_3_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_2701-241_1_3_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_2701-241_1_3_node_42 | 0.4 | n |  | TRUE
13 | bus_LV_2701-241_1_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2701-241_1_3_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_2701-241_1_3_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_2701-241_1_3_node_56 | 0.4 | n |  | TRUE
17 | bus_LV_2701-241_1_3_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_2701-241_1_3_node_43 | 0.4 | n |  | TRUE
19 | bus_LV_2701-241_1_3_node_64 | 0.4 | n |  | TRUE
20 | bus_LV_2701-241_1_3_node_67 | 0.4 | n |  | TRUE
21 | bus_LV_2701-241_1_3_node_57 | 0.4 | n |  | TRUE
22 | bus_LV_2701-241_1_3_node_61 | 0.4 | n |  | TRUE
23 | bus_LV_2701-241_1_3_node_62 | 0.4 | n |  | TRUE
24 | bus_LV_2701-241_1_3_node_66 | 0.4 | n |  | TRUE
25 | bus_LV_2701-241_1_3_node_78 | 0.4 | n |  | TRUE
26 | bus_LV_2701-241_1_3_node_75 | 0.4 | n |  | TRUE
27 | bus_MV_570_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-241_1_3_load_2 | 0 | 0.01381 | 0.0034611 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-241_1_3_load_74 | 1 | 0.00040589 | 0.00010172 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-241_1_3_load_73 | 4 | 0.0040849 | 0.0010238 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-241_1_3_load_55 | 5 | 0.0013237 | 0.00033176 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-241_1_3_load_5 | 6 | 0.0017134 | 0.00042942 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-241_1_3_load_6 | 7 | 0.0005163 | 0.0001294 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-241_1_3_load_7 | 8 | 0.0014144 | 0.00035447 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-241_1_3_load_27 | 10 | 0.0053354 | 0.0013372 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-241_1_3_load_28 | 11 | 0.016881 | 0.0042308 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-241_1_3_load_42 | 12 | 0.0014128 | 0.00035409 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-241_1_3_load_9 | 13 | 0.0082228 | 0.0020608 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-241_1_3_load_30 | 14 | 0.0024326 | 0.00060968 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-241_1_3_load_29 | 15 | 0.00099651 | 0.00024975 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-241_1_3_load_56 | 16 | 0.00030605 | 7.6704e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-241_1_3_load_64 | 19 | 0.04093 | 0.010258 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-241_1_3_load_67 | 20 | 0.0036276 | 0.00090917 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-241_1_3_load_57 | 21 | 0.0085411 | 0.0021406 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-241_1_3_load_61 | 22 | 0.043511 | 0.010905 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-241_1_3_load_66 | 24 | 0.01257 | 0.0031503 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-241_1_3_load_78 | 25 | 0.0011818 | 0.00029618 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-241_1_3_load_75 | 26 | 0.034611 | 0.0086744 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-241_1_3_line_0 |  | 0 | 1 | 0.025701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-241_1_3_line_1 |  | 0 | 2 | 0.067988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-241_1_3_line_2 |  | 1 | 26 | 0.019297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-241_1_3_line_3 |  | 1 | 21 | 0.055001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2701-241_1_3_line_4 |  | 2 | 24 | 0.032577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-241_1_3_line_5 |  | 2 | 20 | 0.04644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-241_1_3_line_6 |  | 3 | 4 | 0.10678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-241_1_3_line_7 |  | 3 | 5 | 0.10156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-241_1_3_line_8 |  | 4 | 23 | 0.12303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-241_1_3_line_9 |  | 5 | 20 | 0.02956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-241_1_3_line_10 |  | 6 | 7 | 0.023265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-241_1_3_line_11 |  | 6 | 8 | 0.040964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-241_1_3_line_12 |  | 7 | 9 | 0.054051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-241_1_3_line_13 |  | 7 | 10 | 0.017727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-241_1_3_line_14 |  | 8 | 11 | 0.018722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-241_1_3_line_15 |  | 9 | 12 | 0.0593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-241_1_3_line_16 |  | 10 | 15 | 0.022638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-241_1_3_line_17 |  | 11 | 14 | 0.074858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-241_1_3_line_18 |  | 12 | 17 | 0.063106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-241_1_3_line_19 |  | 13 | 14 | 0.070512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-241_1_3_line_20 |  | 14 | 16 | 0.013494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-241_1_3_line_21 |  | 16 | 21 | 0.038936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-241_1_3_line_22 |  | 17 | 18 | 0.032838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-241_1_3_line_23 |  | 18 | 19 | 0.057381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-241_1_3_line_24 |  | 22 | 23 | 0.070505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-241_1_3_line_25 |  | 24 | 25 | 0.013499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-241_1_3_trafo_57 | 0.63 MVA 20/0.4 kV | 27 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2612091.8463 | 1270424.7989 | 2612077.1979 | 1270403.6804
1 | 2612091.5008 | 1270337.2135 | 2612077.1979 | 1270403.6804
2 | 2612091.8463 | 1270424.7989 | 2612108.501 | 1270415.052
3 | 2612091.8463 | 1270424.7989 | 2612044.3766 | 1270452.5798
4 | 2612091.5008 | 1270337.2135 | 2612079.8338 | 1270306.7978
5 | 2612091.5008 | 1270337.2135 | 2612100.1334 | 1270339.0323 | 2612104.7767 | 1270338.2412 | 2612109.2172 | 1270337.2385 | 2612135.6503 | 1270326.9766
6 | 2612264.4955 | 1270323.7587 | 2612276.9926 | 1270429.8008
7 | 2612163.2064 | 1270316.2787 | 2612264.4955 | 1270323.7587
8 | 2612276.9926 | 1270429.8008 | 2612272.1466 | 1270552.7372
9 | 2612135.6503 | 1270326.9766 | 2612163.2064 | 1270316.2787
10 | 2611894.7658 | 1270521.078 | 2611874.7456 | 1270532.9284
11 | 2611894.7658 | 1270521.078 | 2611915.7674 | 1270508.6466 | 2611929.2735 | 1270499.0664
12 | 2611845.9627 | 1270505.6827 | 2611847.6476 | 1270517.0496 | 2611848.352 | 1270522.188 | 2611849.5543 | 1270526.6158 | 2611852.5672 | 1270532.248 | 2611857.4009 | 1270537.6949 | 2611860.4226 | 1270538.9018 | 2611864.9518 | 1270538.6106 | 2611868.7023 | 1270536.5055 | 2611874.7456 | 1270532.9284
13 | 2611878.2251 | 1270550.3102 | 2611874.7456 | 1270532.9284
14 | 2611934.6026 | 1270517.0134 | 2611929.2735 | 1270499.0664
15 | 2611845.9627 | 1270505.6827 | 2611852.9198 | 1270506.3859 | 2611857.6691 | 1270505.1056 | 2611860.6985 | 1270502.4987 | 2611861.9197 | 1270497.4753 | 2611864.7033 | 1270459.3546
16 | 2611858.733 | 1270561.8224 | 2611878.2251 | 1270550.3102
17 | 2611999.1267 | 1270479.0615 | 2611970.0087 | 1270496.1024 | 2611934.6026 | 1270517.0134
18 | 2611868.9826 | 1270396.3954 | 2611867.914 | 1270415.3846 | 2611864.7033 | 1270459.3546
19 | 2611999.1267 | 1270479.0615 | 2611942.2539 | 1270437.3796
20 | 2611999.1267 | 1270479.0615 | 2612010.7727 | 1270472.2459
21 | 2612010.7727 | 1270472.2459 | 2612044.3766 | 1270452.5798
22 | 2611868.9826 | 1270396.3954 | 2611861.1151 | 1270395.6792 | 2611836.1118 | 1270394.3728
23 | 2611836.1118 | 1270394.3728 | 2611835.8028 | 1270398.4307 | 2611834.2117 | 1270419.1867 | 2611831.9254 | 1270449.0367 | 2611831.7294 | 1270451.5866
24 | 2612272.1466 | 1270552.7372 | 2612267.3249 | 1270563.5015 | 2612255.1027 | 1270584.3578 | 2612239.6297 | 1270602.1163 | 2612232.1162 | 1270610.1261
25 | 2612079.8338 | 1270306.7978 | 2612074.9992 | 1270294.1943

## bus_geodata
| x | y | coords
0 | 2612077.1979 | 1270403.6804
1 | 2612091.8463 | 1270424.7989
2 | 2612091.5008 | 1270337.2135
3 | 2612264.4955 | 1270323.7587
4 | 2612276.9926 | 1270429.8008
5 | 2612163.2064 | 1270316.2787
6 | 2611894.7658 | 1270521.078
7 | 2611874.7456 | 1270532.9284
8 | 2611929.2735 | 1270499.0664
9 | 2611845.9627 | 1270505.6827
10 | 2611878.2251 | 1270550.3102
11 | 2611934.6026 | 1270517.0134
12 | 2611864.7033 | 1270459.3546
13 | 2611942.2539 | 1270437.3796
14 | 2611999.1267 | 1270479.0615
15 | 2611858.733 | 1270561.8224
16 | 2612010.7727 | 1270472.2459
17 | 2611868.9826 | 1270396.3954
18 | 2611836.1118 | 1270394.3728
19 | 2611831.7294 | 1270451.5866
20 | 2612135.6503 | 1270326.9766
21 | 2612044.3766 | 1270452.5798
22 | 2612232.1162 | 1270610.1261
23 | 2612272.1466 | 1270552.7372
24 | 2612079.8338 | 1270306.7978
25 | 2612074.9992 | 1270294.1943
26 | 2612108.501 | 1270415.052
27 | 2612264.4955 | 1270323.7587

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99517 | -0.091528 | 0.01381 | 0.0034611
1 | 0.99708 | -0.055354 | 0.00040589 | 0.00010172
2 | 0.99098 | -0.17121 | 0 | 0
3 | 0.98283 | -0.32731 | 0 | 0
4 | 0.97807 | -0.41947 | 0.0040849 | 0.0010238
5 | 0.98735 | -0.24046 | 0.0013237 | 0.00033176
6 | 0.9885 | -0.21945 | 0.0017134 | 0.00042942
7 | 0.98744 | -0.23989 | 0.0005163 | 0.0001294
8 | 0.99043 | -0.18232 | 0.0014144 | 0.00035447
9 | 0.98531 | -0.2809 | 0 | 0
10 | 0.98733 | -0.2419 | 0.0053354 | 0.0013372
11 | 0.99134 | -0.16493 | 0.016881 | 0.0042308
12 | 0.98298 | -0.32609 | 0.0014128 | 0.00035409
13 | 0.9956 | -0.083673 | 0.0082228 | 0.0020608
14 | 0.99613 | -0.073482 | 0.0024326 | 0.00060968
15 | 0.98731 | -0.2423 | 0.00099651 | 0.00024975
16 | 0.99712 | -0.054569 | 0.00030605 | 7.6704e-05
17 | 0.98058 | -0.3728 | 0 | 0
18 | 0.97934 | -0.3972 | 0 | 0
19 | 0.97716 | -0.43998 | 0.04093 | 0.010258
20 | 0.9887 | -0.21464 | 0.0036276 | 0.00090917
21 | 1 | 0 | -0.19978 | -0.050744
22 | 0.9702 | -0.57415 | 0.043511 | 0.010905
23 | 0.97307 | -0.51751 | 0 | 0
24 | 0.99057 | -0.17917 | 0.01257 | 0.0031503
25 | 0.99055 | -0.17945 | 0.0011818 | 0.00029618
26 | 0.99647 | -0.067071 | 0.034611 | 0.0086744
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.081288 | -0.020824 | 0.08143 | 0.020915 | 0.00014276 | 9.1032e-05 | 0.12171 | 0.12171 | 0.12171 | 0.99517 | -0.091528 | 0.99708 | -0.055354 | 33.4355
1 | 0.067478 | 0.017363 | -0.067217 | -0.017197 | 0.00026037 | 0.00016576 | 0.10106 | 0.10106 | 0.10106 | 0.99517 | -0.091528 | 0.99098 | -0.17121 | 27.7629
2 | 0.034631 | 0.0086865 | -0.034611 | -0.0086744 | 1.933e-05 | 1.212e-05 | 0.051684 | 0.051684 | 0.051684 | 0.99708 | -0.055354 | 0.99647 | -0.067071 | 14.199
3 | -0.11647 | -0.029704 | 0.11678 | 0.029902 | 0.00031221 | 0.00019837 | 0.17399 | 0.17399 | 0.17399 | 0.99708 | -0.055354 | 1 | 0 | 23.9003
4 | 0.013757 | 0.0034492 | -0.013752 | -0.0034463 | 5.213e-06 | 2.9168e-06 | 0.020657 | 0.020657 | 0.020657 | 0.99098 | -0.17121 | 0.99057 | -0.17917 | 5.6751
5 | 0.053461 | 0.013748 | -0.053348 | -0.013677 | 0.00011257 | 7.145e-05 | 0.0804 | 0.0804 | 0.0804 | 0.99098 | -0.17121 | 0.9887 | -0.21464 | 22.0879
6 | 0.048132 | 0.012268 | -0.047919 | -0.012133 | 0.00021306 | 0.00013501 | 0.072946 | 0.072947 | 0.072947 | 0.98283 | -0.32731 | 0.97807 | -0.41947 | 20.0403
7 | -0.048132 | -0.012268 | 0.048334 | 0.012396 | 0.00020266 | 0.00012841 | 0.072946 | 0.072946 | 0.072946 | 0.98283 | -0.32731 | 0.98735 | -0.24046 | 20.0401
8 | 0.043834 | 0.011109 | -0.043628 | -0.010979 | 0.00020546 | 0.00012996 | 0.066732 | 0.066733 | 0.066733 | 0.97807 | -0.41947 | 0.97307 | -0.51751 | 18.3331
9 | -0.049658 | -0.012728 | 0.04972 | 0.012768 | 6.2254e-05 | 3.9464e-05 | 0.074941 | 0.07494 | 0.074941 | 0.98735 | -0.24046 | 0.9887 | -0.21464 | 20.5881
10 | 0.049641 | 0.012612 | -0.049592 | -0.012581 | 4.8795e-05 | 3.0931e-05 | 0.074787 | 0.074787 | 0.074787 | 0.9885 | -0.21945 | 0.98744 | -0.23989 | 20.5458
11 | -0.051354 | -0.013041 | 0.051446 | 0.0131 | 9.1946e-05 | 5.8319e-05 | 0.077366 | 0.077366 | 0.077366 | 0.9885 | -0.21945 | 0.99043 | -0.18232 | 21.2544
12 | 0.042743 | 0.010865 | -0.042659 | -0.010812 | 8.4237e-05 | 5.3222e-05 | 0.064466 | 0.064466 | 0.064466 | 0.98744 | -0.23989 | 0.98531 | -0.2809 | 17.7105
13 | 0.0063325 | 0.0015868 | -0.0063319 | -0.0015867 | 6.0535e-07 | 1.6069e-07 | 0.0095427 | 0.0095428 | 0.0095428 | 0.98744 | -0.23989 | 0.98733 | -0.2419 | 2.6216
14 | -0.05286 | -0.013454 | 0.052905 | 0.013482 | 4.4361e-05 | 2.815e-05 | 0.079491 | 0.079491 | 0.079491 | 0.99043 | -0.18232 | 0.99134 | -0.16493 | 21.8381
15 | 0.042659 | 0.010812 | -0.042566 | -0.010753 | 9.2417e-05 | 5.8394e-05 | 0.064466 | 0.064467 | 0.064467 | 0.98531 | -0.2809 | 0.98298 | -0.32609 | 17.7106
16 | 0.00099652 | 0.00024947 | -0.00099651 | -0.00024975 | 1.9147e-08 | -2.7726e-07 | 0.0015018 | 0.0015019 | 0.0015019 | 0.98733 | -0.2419 | 0.98731 | -0.2423 | 0.4126
17 | -0.069786 | -0.017713 | 0.070094 | 0.01791 | 0.00030848 | 0.00019646 | 0.10483 | 0.10483 | 0.10483 | 0.99134 | -0.16493 | 0.99613 | -0.073482 | 28.7993
18 | 0.041154 | 0.010399 | -0.041062 | -0.010341 | 9.1933e-05 | 5.8039e-05 | 0.062328 | 0.062328 | 0.062328 | 0.98298 | -0.32609 | 0.98058 | -0.3728 | 17.1231
19 | -0.0082228 | -0.0020608 | 0.0082268 | 0.0020625 | 3.9936e-06 | 1.6385e-06 | 0.01229 | 0.012289 | 0.01229 | 0.9956 | -0.083673 | 0.99613 | -0.073482 | 3.3763
20 | -0.080754 | -0.020582 | 0.080828 | 0.020629 | 7.3783e-05 | 4.7045e-05 | 0.12075 | 0.12075 | 0.12075 | 0.99613 | -0.073482 | 0.99712 | -0.054569 | 33.1737
21 | -0.081134 | -0.020705 | 0.081348 | 0.020842 | 0.00021451 | 0.00013678 | 0.12121 | 0.12121 | 0.12121 | 0.99712 | -0.054569 | 1 | 0 | 33.2991
22 | 0.041062 | 0.010341 | -0.041014 | -0.010311 | 4.7839e-05 | 3.0203e-05 | 0.062328 | 0.062328 | 0.062328 | 0.98058 | -0.3728 | 0.97934 | -0.3972 | 17.1232
23 | 0.041014 | 0.010311 | -0.04093 | -0.010258 | 8.3594e-05 | 5.278e-05 | 0.062328 | 0.062329 | 0.062329 | 0.97934 | -0.3972 | 0.97716 | -0.43998 | 17.1232
24 | -0.043511 | -0.010905 | 0.043628 | 0.010979 | 0.00011774 | 7.4481e-05 | 0.066733 | 0.066733 | 0.066733 | 0.9702 | -0.57415 | 0.97307 | -0.51751 | 18.3332
25 | 0.0011818 | 0.00029602 | -0.0011818 | -0.00029618 | 1.5953e-08 | -1.6356e-07 | 0.0017752 | 0.0017753 | 0.0017753 | 0.99057 | -0.17917 | 0.99055 | -0.17945 | 0.48771

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.20832 | 0.052885

## res_load
| p_mw | q_mvar
0 | 0.01381 | 0.0034611
1 | 0.00040589 | 0.00010172
2 | 0.0040849 | 0.0010238
3 | 0.0013237 | 0.00033176
4 | 0.0017134 | 0.00042942
5 | 0.0005163 | 0.0001294
6 | 0.0014144 | 0.00035447
7 | 0.0053354 | 0.0013372
8 | 0.016881 | 0.0042308
9 | 0.0014128 | 0.00035409
10 | 0.0082228 | 0.0020608
11 | 0.0024326 | 0.00060968
12 | 0.00099651 | 0.00024975
13 | 0.00030605 | 7.6704e-05
14 | 0.04093 | 0.010258
15 | 0.0036276 | 0.00090917
16 | 0.0085411 | 0.0021406
17 | 0.043511 | 0.010905
18 | 0.01257 | 0.0031503
19 | 0.0011818 | 0.00029618
20 | 0.034611 | 0.0086744

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1