## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-248_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-248_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-248_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-248_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-248_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-248_0_4_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_2701-248_0_4_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_2701-248_0_4_node_34 | 0.4 | n |  | TRUE
8 | bus_LV_2701-248_0_4_node_44 | 0.4 | n |  | TRUE
9 | bus_LV_2701-248_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2701-248_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2701-248_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2701-248_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2701-248_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2701-248_0_4_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_2701-248_0_4_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_2701-248_0_4_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_2701-248_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2701-248_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2701-248_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2701-248_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2701-248_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2701-248_0_4_node_42 | 0.4 | n |  | TRUE
23 | bus_LV_2701-248_0_4_node_48 | 0.4 | n |  | TRUE
24 | bus_LV_2701-248_0_4_node_41 | 0.4 | n |  | TRUE
25 | bus_LV_2701-248_0_4_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_2701-248_0_4_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_2701-248_0_4_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_2701-248_0_4_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_2701-248_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2701-248_0_4_node_46 | 0.4 | n |  | TRUE
31 | bus_LV_2701-248_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_2701-248_0_4_node_45 | 0.4 | n |  | TRUE
33 | bus_LV_2701-248_0_4_node_47 | 0.4 | n |  | TRUE
34 | bus_LV_2701-248_0_4_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_2701-248_0_4_node_37 | 0.4 | n |  | TRUE
36 | bus_LV_2701-248_0_4_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_2701-248_0_4_node_49 | 0.4 | n |  | TRUE
38 | bus_LV_2701-248_0_4_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_2701-248_0_4_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_2701-248_0_4_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_2701-248_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_2701-248_0_4_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_2701-248_0_4_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_2701-248_0_4_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_2701-248_0_4_node_31 | 0.4 | n |  | TRUE
46 | bus_MV_561_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-248_0_4_load_0 | 0 | 0.0048452 | 0.0012143 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-248_0_4_load_1 | 1 | 0.0054724 | 0.0013715 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-248_0_4_load_2 | 2 | 0.0065358 | 0.001638 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-248_0_4_load_3 | 3 | 0.0044861 | 0.0011243 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-248_0_4_load_4 | 4 | 0.0035327 | 0.00088538 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-248_0_4_load_36 | 5 | 0.0060326 | 0.0015119 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-248_0_4_load_43 | 6 | 0.0034847 | 0.00087335 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-248_0_4_load_34 | 7 | 0.0064893 | 0.0016264 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-248_0_4_load_44 | 8 | 0.021228 | 0.0053202 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-248_0_4_load_5 | 9 | 0.0067734 | 0.0016976 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-248_0_4_load_6 | 10 | 0.01011 | 0.0025339 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-248_0_4_load_7 | 11 | 0.016108 | 0.0040372 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-248_0_4_load_8 | 12 | 0.011288 | 0.0028291 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-248_0_4_load_9 | 13 | 0.0054537 | 0.0013668 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-248_0_4_load_16 | 14 | 0.010166 | 0.0025479 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-248_0_4_load_38 | 15 | 0.013081 | 0.0032784 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-248_0_4_load_15 | 16 | 0.0094913 | 0.0023787 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-248_0_4_load_14 | 17 | 0.027979 | 0.0070122 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-248_0_4_load_10 | 18 | 0.0086712 | 0.0021732 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-248_0_4_load_11 | 19 | 0.0039677 | 0.0009944 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-248_0_4_load_12 | 20 | 0.003742 | 0.00093785 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-248_0_4_load_42 | 22 | 0.0073241 | 0.0018356 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-248_0_4_load_48 | 23 | 0.0071568 | 0.0017937 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-248_0_4_load_41 | 24 | 0.0066042 | 0.0016552 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-248_0_4_load_32 | 26 | 0.0080034 | 0.0020059 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-248_0_4_load_33 | 27 | 0.064962 | 0.016281 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-248_0_4_load_29 | 28 | 0.0037103 | 0.00092989 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-248_0_4_load_46 | 30 | 0.0023895 | 0.00059885 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-248_0_4_load_45 | 32 | 0.003444 | 0.00086314 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-248_0_4_load_47 | 33 | 0.0048895 | 0.0012254 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-248_0_4_load_37 | 35 | 0.0063996 | 0.0016039 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-248_0_4_load_40 | 36 | 0.0045123 | 0.0011309 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-248_0_4_load_49 | 37 | 0.0065623 | 0.0016447 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-248_0_4_load_17 | 38 | 0.014239 | 0.0035686 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-248_0_4_load_19 | 39 | 0.009163 | 0.0022965 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-248_0_4_load_20 | 40 | 0.0017416 | 0.00043648 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-248_0_4_load_22 | 41 | 0.026441 | 0.0066267 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-248_0_4_load_39 | 42 | 0.0065913 | 0.0016519 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-248_0_4_load_30 | 43 | 0.0044372 | 0.0011121 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-248_0_4_load_35 | 44 | 0.018162 | 0.0045518 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-248_0_4_load_31 | 45 | 0.0044777 | 0.0011222 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-248_0_4_line_0 |  | 0 | 1 | 0.004882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-248_0_4_line_1 |  | 0 | 2 | 0.0024708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-248_0_4_line_2 |  | 1 | 3 | 0.006209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-248_0_4_line_3 |  | 2 | 4 | 0.0016227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-248_0_4_line_4 |  | 3 | 5 | 0.0022302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2701-248_0_4_line_5 |  | 4 | 6 | 0.0079071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-248_0_4_line_6 |  | 5 | 7 | 0.0045543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2701-248_0_4_line_7 |  | 6 | 8 | 0.0021128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-248_0_4_line_8 |  | 7 | 44 | 0.010139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_2701-248_0_4_line_9 |  | 8 | 45 | 0.0068302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-248_0_4_line_10 |  | 9 | 10 | 0.0010821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2701-248_0_4_line_11 |  | 9 | 11 | 0.0078887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2701-248_0_4_line_12 |  | 10 | 12 | 0.0096314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-248_0_4_line_13 |  | 11 | 13 | 0.0014407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2701-248_0_4_line_14 |  | 12 | 14 | 0.0027999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-248_0_4_line_15 |  | 13 | 15 | 0.0149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2701-248_0_4_line_16 |  | 14 | 16 | 0.0076999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-248_0_4_line_17 |  | 15 | 17 | 0.003007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2701-248_0_4_line_18 |  | 16 | 38 | 0.012231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-248_0_4_line_19 |  | 17 | 20 | 0.012483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2701-248_0_4_line_20 |  | 18 | 19 | 0.0068834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2701-248_0_4_line_21 |  | 18 | 20 | 0.0014585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2701-248_0_4_line_22 |  | 19 | 21 | 0.019231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2701-248_0_4_line_23 |  | 21 | 22 | 0.012074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2701-248_0_4_line_24 |  | 21 | 23 | 0.016581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-248_0_4_line_25 |  | 22 | 24 | 0.012474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2701-248_0_4_line_26 |  | 23 | 37 | 0.021544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-248_0_4_line_27 |  | 24 | 36 | 0.01688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2701-248_0_4_line_28 |  | 25 | 26 | 0.01942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-248_0_4_line_29 |  | 25 | 27 | 0.036844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-248_0_4_line_30 |  | 25 | 28 | 0.026032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-248_0_4_line_31 |  | 26 | 42 | 0.01646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-248_0_4_line_32 |  | 28 | 43 | 0.010167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-248_0_4_line_33 |  | 29 | 30 | 0.018081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-248_0_4_line_34 |  | 29 | 31 | 0.01201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-248_0_4_line_35 |  | 29 | 32 | 0.050098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-248_0_4_line_36 |  | 30 | 37 | 0.021653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-248_0_4_line_37 |  | 31 | 33 | 0.016429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-248_0_4_line_38 |  | 32 | 41 | 0.00045066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2701-248_0_4_line_39 |  | 34 | 35 | 0.031335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2701-248_0_4_line_40 |  | 34 | 36 | 0.039826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2701-248_0_4_line_41 |  | 35 | 44 | 0.0052601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2701-248_0_4_line_42 |  | 39 | 40 | 0.02384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-248_0_4_line_43 |  | 40 | 41 | 0.0064267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-248_0_4_line_44 |  | 43 | 45 | 0.010545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-248_0_4_trafo_6 | 0.63 MVA 20/0.4 kV | 46 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2611491.1327 | 1268826.2341 | 2611496.0138 | 1268826.3282
1 | 2611491.1327 | 1268826.2341 | 2611488.6624 | 1268826.1865
2 | 2611496.0138 | 1268826.3282 | 2611502.2217 | 1268826.4479
3 | 2611487.0399 | 1268826.1553 | 2611488.6624 | 1268826.1865
4 | 2611502.2217 | 1268826.4479 | 2611504.4515 | 1268826.4908
5 | 2611487.0399 | 1268826.1553 | 2611479.1343 | 1268826.0029
6 | 2611504.4515 | 1268826.4908 | 2611509.0049 | 1268826.5786
7 | 2611477.0219 | 1268825.9622 | 2611479.1343 | 1268826.0029
8 | 2611519.1423 | 1268826.7739 | 2611509.0049 | 1268826.5786
9 | 2611477.0219 | 1268825.9622 | 2611470.193 | 1268825.8306
10 | 2611489.4509 | 1268745.6733 | 2611488.3688 | 1268745.6635
11 | 2611489.4509 | 1268745.6733 | 2611497.3392 | 1268745.7443
12 | 2611488.3688 | 1268745.6635 | 2611478.7378 | 1268745.5768
13 | 2611497.3392 | 1268745.7443 | 2611498.7799 | 1268745.7573
14 | 2611475.938 | 1268745.5515 | 2611478.7378 | 1268745.5768
15 | 2611513.6793 | 1268745.8915 | 2611498.7799 | 1268745.7573
16 | 2611475.938 | 1268745.5515 | 2611468.2384 | 1268745.4822
17 | 2611513.6793 | 1268745.8915 | 2611516.6862 | 1268745.9186
18 | 2611456.0081 | 1268745.372 | 2611468.2384 | 1268745.4822
19 | 2611516.6862 | 1268745.9186 | 2611529.1682 | 1268746.031
20 | 2611530.6266 | 1268746.0442 | 2611537.5097 | 1268746.1062
21 | 2611530.6266 | 1268746.0442 | 2611529.1682 | 1268746.031
22 | 2611556.7395 | 1268746.2794 | 2611537.5097 | 1268746.1062
23 | 2611556.7395 | 1268746.2794 | 2611556.6738 | 1268752.9506 | 2611556.6378 | 1268758.3526
24 | 2611556.7395 | 1268746.2794 | 2611556.9503 | 1268738.4743 | 2611556.9893 | 1268729.7009
25 | 2611556.6378 | 1268758.3526 | 2611556.6101 | 1268762.4906 | 2611556.5403 | 1268770.8261
26 | 2611556.9893 | 1268729.7009 | 2611557.085 | 1268708.1574
27 | 2611556.5403 | 1268770.8261 | 2611556.4729 | 1268778.8685 | 2611556.541 | 1268787.7057
28 | 2611423.4551 | 1268825.8666 | 2611423.6887 | 1268829.6364 | 2611429.77 | 1268832.8726 | 2611429.7669 | 1268834.4737 | 2611429.7207 | 1268841.6271
29 | 2611423.4551 | 1268825.8666 | 2611423.4571 | 1268820.9075 | 2611422.6632 | 1268815.0797 | 2611424.3745 | 1268789.1331
30 | 2611423.4551 | 1268825.8666 | 2611449.4843 | 1268825.5085
31 | 2611429.7207 | 1268841.6271 | 2611429.6812 | 1268847.7273 | 2611428.349 | 1268858.0009
32 | 2611459.6498 | 1268825.6274 | 2611451.817 | 1268825.4765 | 2611449.4843 | 1268825.5085
33 | 2611556.876 | 1268668.4248 | 2611557.0506 | 1268686.5052
34 | 2611556.876 | 1268668.4248 | 2611563.227 | 1268668.515 | 2611568.8858 | 1268668.526
35 | 2611556.876 | 1268668.4248 | 2611533.9553 | 1268668.1023 | 2611506.7825 | 1268667.7257
36 | 2611557.0506 | 1268686.5052 | 2611557.0952 | 1268691.119 | 2611557.1378 | 1268696.2783 | 2611557.085 | 1268708.1574
37 | 2611568.8858 | 1268668.526 | 2611568.9463 | 1268684.9553
38 | 2611506.3319 | 1268667.7195 | 2611506.7825 | 1268667.7257
39 | 2611555.7311 | 1268827.4791 | 2611524.4015 | 1268826.8753
40 | 2611555.7311 | 1268827.4791 | 2611556.4943 | 1268821.9656 | 2611556.5722 | 1268805.1872 | 2611556.557 | 1268789.7763 | 2611556.541 | 1268787.7057
41 | 2611524.4015 | 1268826.8753 | 2611519.1423 | 1268826.7739
42 | 2611499.9058 | 1268667.6304 | 2611476.0681 | 1268667.3001
43 | 2611499.9058 | 1268667.6304 | 2611506.3319 | 1268667.7195
44 | 2611459.6498 | 1268825.6274 | 2611470.193 | 1268825.8306

## bus_geodata
| x | y | coords
0 | 2611491.1327 | 1268826.2341
1 | 2611496.0138 | 1268826.3282
2 | 2611488.6624 | 1268826.1865
3 | 2611502.2217 | 1268826.4479
4 | 2611487.0399 | 1268826.1553
5 | 2611504.4515 | 1268826.4908
6 | 2611479.1343 | 1268826.0029
7 | 2611509.0049 | 1268826.5786
8 | 2611477.0219 | 1268825.9622
9 | 2611489.4509 | 1268745.6733
10 | 2611488.3688 | 1268745.6635
11 | 2611497.3392 | 1268745.7443
12 | 2611478.7378 | 1268745.5768
13 | 2611498.7799 | 1268745.7573
14 | 2611475.938 | 1268745.5515
15 | 2611513.6793 | 1268745.8915
16 | 2611468.2384 | 1268745.4822
17 | 2611516.6862 | 1268745.9186
18 | 2611530.6266 | 1268746.0442
19 | 2611537.5097 | 1268746.1062
20 | 2611529.1682 | 1268746.031
21 | 2611556.7395 | 1268746.2794
22 | 2611556.6378 | 1268758.3526
23 | 2611556.9893 | 1268729.7009
24 | 2611556.5403 | 1268770.8261
25 | 2611423.4551 | 1268825.8666
26 | 2611429.7207 | 1268841.6271
27 | 2611424.3745 | 1268789.1331
28 | 2611449.4843 | 1268825.5085
29 | 2611556.876 | 1268668.4248
30 | 2611557.0506 | 1268686.5052
31 | 2611568.8858 | 1268668.526
32 | 2611506.7825 | 1268667.7257
33 | 2611568.9463 | 1268684.9553
34 | 2611555.7311 | 1268827.4791
35 | 2611524.4015 | 1268826.8753
36 | 2611556.541 | 1268787.7057
37 | 2611557.085 | 1268708.1574
38 | 2611456.0081 | 1268745.372
39 | 2611476.0681 | 1268667.3001
40 | 2611499.9058 | 1268667.6304
41 | 2611506.3319 | 1268667.7195
42 | 2611428.349 | 1268858.0009
43 | 2611459.6498 | 1268825.6274
44 | 2611519.1423 | 1268826.7739
45 | 2611470.193 | 1268825.8306
46 | 2611423.1064 | 1268745.0757

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9851 | -0.28571 | 0.0048452 | 0.0012143
1 | 0.98569 | -0.27415 | 0.0054724 | 0.0013715
2 | 0.98481 | -0.29134 | 0.0065358 | 0.001638
3 | 0.98648 | -0.25888 | 0.0044861 | 0.0011243
4 | 0.98462 | -0.29485 | 0.0035327 | 0.00088538
5 | 0.98663 | -0.25604 | 0.0060326 | 0.0015119
6 | 0.98377 | -0.31149 | 0.0034847 | 0.00087335
7 | 0.98683 | -0.25203 | 0.0064893 | 0.0016264
8 | 0.98355 | -0.3158 | 0.021228 | 0.0053202
9 | 0.99989 | -0.0021685 | 0.0067734 | 0.0016976
10 | 1 | 0 | -0.39567 | -0.10029
11 | 0.99907 | -0.017681 | 0.016108 | 0.0040372
12 | 0.99961 | -0.0075883 | 0.011288 | 0.0028291
13 | 0.99893 | -0.020382 | 0.0054537 | 0.0013668
14 | 0.99952 | -0.0092439 | 0.010166 | 0.0025479
15 | 0.99748 | -0.047883 | 0.013081 | 0.0032784
16 | 0.99935 | -0.012432 | 0.0094913 | 0.0023787
17 | 0.9972 | -0.053213 | 0.027979 | 0.0070122
18 | 0.99602 | -0.075646 | 0.0086712 | 0.0021732
19 | 0.99547 | -0.086256 | 0.0039677 | 0.0009944
20 | 0.99614 | -0.073325 | 0.003742 | 0.00093785
21 | 0.99393 | -0.11551 | 0 | 0
22 | 0.9932 | -0.12953 | 0.0073241 | 0.0018356
23 | 0.993 | -0.13361 | 0.0071568 | 0.0017937
24 | 0.99247 | -0.1435 | 0.0066042 | 0.0016552
25 | 0.9794 | -0.39672 | 0 | 0
26 | 0.97914 | -0.40187 | 0.0080034 | 0.0020059
27 | 0.97718 | -0.44031 | 0.064962 | 0.016281
28 | 0.98132 | -0.35916 | 0.0037103 | 0.00092989
29 | 0.9902 | -0.18757 | 0 | 0
30 | 0.99096 | -0.17289 | 0.0023895 | 0.00059885
31 | 0.99015 | -0.18861 | 0 | 0
32 | 0.98833 | -0.22396 | 0.003444 | 0.00086314
33 | 0.99008 | -0.19004 | 0.0048895 | 0.0012254
34 | 0.98932 | -0.20397 | 0 | 0
35 | 0.9876 | -0.23729 | 0.0063996 | 0.0016039
36 | 0.99152 | -0.16178 | 0.0045123 | 0.0011309
37 | 0.99192 | -0.15444 | 0.0065623 | 0.0016447
38 | 0.9992 | -0.015472 | 0.014239 | 0.0035686
39 | 0.98805 | -0.22941 | 0.009163 | 0.0022965
40 | 0.98825 | -0.22551 | 0.0017416 | 0.00043648
41 | 0.98831 | -0.22426 | 0.026441 | 0.0066267
42 | 0.97904 | -0.40385 | 0.0065913 | 0.0016519
43 | 0.98211 | -0.34385 | 0.0044372 | 0.0011121
44 | 0.98732 | -0.2427 | 0.018162 | 0.0045518
45 | 0.98296 | -0.32715 | 0.0044777 | 0.0011222
46 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13244 | -0.03344 | 0.13252 | 0.033487 | 7.334e-05 | 4.6875e-05 | 0.20015 | 0.20015 | 0.20015 | 0.9851 | -0.28571 | 0.98569 | -0.27415 | 54.9861
1 | 0.1276 | 0.032225 | -0.12756 | -0.032203 | 3.4452e-05 | 2.2018e-05 | 0.19283 | 0.19283 | 0.19283 | 0.9851 | -0.28571 | 0.98481 | -0.29134 | 52.9754
2 | -0.13799 | -0.034858 | 0.13809 | 0.034923 | 0.00010113 | 6.4646e-05 | 0.20841 | 0.20841 | 0.20841 | 0.98569 | -0.27415 | 0.98648 | -0.25888 | 57.2557
3 | 0.12103 | 0.030565 | -0.12101 | -0.030552 | 2.0369e-05 | 1.3015e-05 | 0.18296 | 0.18296 | 0.18296 | 0.98481 | -0.29134 | 0.98462 | -0.29485 | 50.2624
4 | -0.14258 | -0.036047 | 0.1426 | 0.03606 | 1.9362e-05 | 1.2335e-05 | 0.21518 | 0.21518 | 0.21518 | 0.98648 | -0.25888 | 0.98663 | -0.25604 | 29.5573
5 | 0.11748 | 0.029667 | -0.11738 | -0.029607 | 9.3543e-05 | 5.9767e-05 | 0.17762 | 0.17762 | 0.17762 | 0.98462 | -0.29485 | 0.98377 | -0.31149 | 48.7957
6 | -0.14863 | -0.037571 | 0.14866 | 0.03759 | 2.8635e-05 | 1.8152e-05 | 0.22428 | 0.22428 | 0.22428 | 0.98663 | -0.25604 | 0.98683 | -0.25203 | 20.5381
7 | 0.1139 | 0.028734 | -0.11387 | -0.028719 | 2.3534e-05 | 1.5035e-05 | 0.17235 | 0.17235 | 0.17235 | 0.98377 | -0.31149 | 0.98355 | -0.3158 | 47.3477
8 | -0.15515 | -0.039216 | 0.15522 | 0.03926 | 6.9434e-05 | 4.4049e-05 | 0.23406 | 0.23406 | 0.23406 | 0.98683 | -0.25203 | 0.98732 | -0.2427 | 21.4341
9 | 0.092646 | 0.023399 | -0.092596 | -0.023367 | 5.0367e-05 | 3.2148e-05 | 0.14023 | 0.14023 | 0.14023 | 0.98355 | -0.3158 | 0.98296 | -0.32715 | 38.5246
10 | -0.34877 | -0.088924 | 0.34881 | 0.088947 | 3.6516e-05 | 2.3328e-05 | 0.51957 | 0.51957 | 0.51957 | 0.99989 | -0.0021685 | 1 | 0 | 47.5801
11 | 0.342 | 0.087227 | -0.34174 | -0.087063 | 0.00025597 | 0.00016351 | 0.50949 | 0.50949 | 0.50949 | 0.99989 | -0.0021685 | 0.99907 | -0.017681 | 46.657
12 | 0.045209 | 0.01134 | -0.045193 | -0.011329 | 1.6347e-05 | 1.0336e-05 | 0.067276 | 0.067276 | 0.067276 | 1 | 0 | 0.99961 | -0.0075883 | 18.4823
13 | 0.32563 | 0.083026 | -0.32559 | -0.082999 | 4.245e-05 | 2.7111e-05 | 0.4855 | 0.4855 | 0.4855 | 0.99907 | -0.017681 | 0.99893 | -0.020382 | 44.4599
14 | 0.033905 | 0.0085003 | -0.033902 | -0.0084987 | 2.6747e-06 | 1.6751e-06 | 0.050472 | 0.050472 | 0.050472 | 0.99961 | -0.0075883 | 0.99952 | -0.0092439 | 13.866
15 | 0.32014 | 0.081632 | -0.31971 | -0.081361 | 0.00042445 | 0.00027106 | 0.47738 | 0.47738 | 0.47738 | 0.99893 | -0.020382 | 0.99748 | -0.047883 | 43.716
16 | 0.023736 | 0.0059507 | -0.023732 | -0.0059485 | 3.6056e-06 | 2.2067e-06 | 0.035337 | 0.035337 | 0.035337 | 0.99952 | -0.0092439 | 0.99935 | -0.012432 | 9.708
17 | 0.30663 | 0.078083 | -0.30655 | -0.078032 | 7.8798e-05 | 5.0313e-05 | 0.45787 | 0.45787 | 0.45787 | 0.99748 | -0.047883 | 0.9972 | -0.053213 | 41.929
18 | 0.014241 | 0.0035698 | -0.014239 | -0.0035686 | 2.0623e-06 | 1.1597e-06 | 0.021205 | 0.021205 | 0.021205 | 0.99935 | -0.012432 | 0.9992 | -0.015472 | 5.8255
19 | 0.27858 | 0.07102 | -0.27831 | -0.070848 | 0.00027017 | 0.00017242 | 0.41612 | 0.41612 | 0.41612 | 0.9972 | -0.053213 | 0.99614 | -0.073325 | 38.1058
20 | 0.26586 | 0.067717 | -0.26573 | -0.06763 | 0.000136 | 8.6772e-05 | 0.39757 | 0.39757 | 0.39757 | 0.99602 | -0.075646 | 0.99547 | -0.086256 | 36.4077
21 | -0.27453 | -0.06989 | 0.27456 | 0.06991 | 3.0725e-05 | 1.9607e-05 | 0.41053 | 0.41053 | 0.41053 | 0.99602 | -0.075646 | 0.99614 | -0.073325 | 37.594
22 | 0.26176 | 0.066636 | -0.26139 | -0.066401 | 0.0003687 | 0.00023522 | 0.39164 | 0.39164 | 0.39164 | 0.99547 | -0.086256 | 0.99393 | -0.11551 | 35.8646
23 | 0.19934 | 0.050753 | -0.19921 | -0.050667 | 0.00013467 | 8.5721e-05 | 0.29872 | 0.29872 | 0.29872 | 0.99393 | -0.11551 | 0.9932 | -0.12953 | 27.3553
24 | 0.062044 | 0.015648 | -0.061991 | -0.015613 | 5.3689e-05 | 3.4146e-05 | 0.092921 | 0.092921 | 0.092921 | 0.99393 | -0.11551 | 0.993 | -0.13361 | 25.5278
25 | 0.19189 | 0.048832 | -0.19176 | -0.04875 | 0.0001291 | 8.2141e-05 | 0.28775 | 0.28775 | 0.28775 | 0.9932 | -0.12953 | 0.99247 | -0.1435 | 26.3505
26 | 0.054834 | 0.01382 | -0.054779 | -0.013785 | 5.4584e-05 | 3.4655e-05 | 0.082197 | 0.082197 | 0.082197 | 0.993 | -0.13361 | 0.99192 | -0.15444 | 22.5816
27 | 0.18515 | 0.047094 | -0.18499 | -0.046991 | 0.00016289 | 0.0001036 | 0.27785 | 0.27785 | 0.27785 | 0.99247 | -0.1435 | 0.99152 | -0.16178 | 25.4438
28 | 0.014599 | 0.00366 | -0.014595 | -0.003658 | 3.583e-06 | 2.0488e-06 | 0.022181 | 0.022181 | 0.022181 | 0.9794 | -0.39672 | 0.97914 | -0.40187 | 6.0937
29 | 0.065097 | 0.016367 | -0.064962 | -0.016281 | 0.0001352 | 8.6065e-05 | 0.098921 | 0.098922 | 0.098922 | 0.9794 | -0.39672 | 0.97718 | -0.44031 | 27.1763
30 | -0.079696 | -0.020027 | 0.079839 | 0.020118 | 0.00014317 | 9.1298e-05 | 0.1211 | 0.1211 | 0.1211 | 0.9794 | -0.39672 | 0.98132 | -0.35916 | 33.2699
31 | 0.006592 | 0.0016521 | -0.0065913 | -0.0016519 | 6.1948e-07 | 1.8946e-07 | 0.010018 | 0.010018 | 0.010018 | 0.97914 | -0.40187 | 0.97904 | -0.40385 | 2.7522
32 | -0.083549 | -0.021048 | 0.083611 | 0.021087 | 6.1232e-05 | 3.906e-05 | 0.12673 | 0.12673 | 0.12673 | 0.98132 | -0.35916 | 0.98211 | -0.34385 | 34.8155
33 | -0.045753 | -0.011494 | 0.045785 | 0.011515 | 3.2062e-05 | 2.0287e-05 | 0.068765 | 0.068765 | 0.068765 | 0.9902 | -0.18757 | 0.99096 | -0.17289 | 18.8914
34 | 0.00489 | 0.0012254 | -0.0048898 | -0.0012254 | 2.4321e-07 | 1.166e-09 | 0.0073484 | 0.0073485 | 0.0073485 | 0.9902 | -0.18757 | 0.99015 | -0.18861 | 2.0188
35 | 0.040863 | 0.010269 | -0.040792 | -0.010224 | 7.0864e-05 | 4.471e-05 | 0.061416 | 0.061417 | 0.061417 | 0.9902 | -0.18757 | 0.98833 | -0.22396 | 16.8727
36 | -0.048175 | -0.012114 | 0.048217 | 0.01214 | 4.2506e-05 | 2.6925e-05 | 0.072353 | 0.072353 | 0.072353 | 0.99096 | -0.17289 | 0.99192 | -0.15444 | 19.8771
37 | 0.0048898 | 0.0012254 | -0.0048895 | -0.0012254 | 3.327e-07 | 1.626e-09 | 0.0073485 | 0.0073485 | 0.0073485 | 0.99015 | -0.18861 | 0.99008 | -0.19004 | 2.0188
38 | 0.037348 | 0.0093611 | -0.037348 | -0.0093608 | 5.3436e-07 | 3.3622e-07 | 0.056231 | 0.056231 | 0.056231 | 0.98833 | -0.22396 | 0.98831 | -0.22426 | 15.4482
39 | 0.18011 | 0.045627 | -0.17982 | -0.045444 | 0.00028782 | 0.000183 | 0.27107 | 0.27108 | 0.27108 | 0.98932 | -0.20397 | 0.9876 | -0.23729 | 24.8237
40 | -0.18011 | -0.045627 | 0.18048 | 0.04586 | 0.00036581 | 0.00023258 | 0.27107 | 0.27107 | 0.27107 | 0.98932 | -0.20397 | 0.99152 | -0.16178 | 24.8237
41 | 0.17342 | 0.04384 | -0.17338 | -0.043812 | 4.4939e-05 | 2.8559e-05 | 0.26143 | 0.26143 | 0.26143 | 0.9876 | -0.23729 | 0.98732 | -0.2427 | 23.9407
42 | -0.009163 | -0.0022965 | 0.0091647 | 0.0022973 | 1.7024e-06 | 7.8416e-07 | 0.0138 | 0.0138 | 0.0138 | 0.98805 | -0.22941 | 0.98825 | -0.22551 | 3.7911
43 | -0.010906 | -0.0027337 | 0.010907 | 0.0027341 | 6.4992e-07 | 3.336e-07 | 0.016422 | 0.016422 | 0.016422 | 0.98825 | -0.22551 | 0.98831 | -0.22426 | 4.5115
44 | -0.088048 | -0.022199 | 0.088118 | 0.022244 | 7.0425e-05 | 4.4939e-05 | 0.13345 | 0.13345 | 0.13345 | 0.98211 | -0.34385 | 0.98296 | -0.32715 | 36.6624

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40578 | 0.10282

## res_load
| p_mw | q_mvar
0 | 0.0048452 | 0.0012143
1 | 0.0054724 | 0.0013715
2 | 0.0065358 | 0.001638
3 | 0.0044861 | 0.0011243
4 | 0.0035327 | 0.00088538
5 | 0.0060326 | 0.0015119
6 | 0.0034847 | 0.00087335
7 | 0.0064893 | 0.0016264
8 | 0.021228 | 0.0053202
9 | 0.0067734 | 0.0016976
10 | 0.01011 | 0.0025339
11 | 0.016108 | 0.0040372
12 | 0.011288 | 0.0028291
13 | 0.0054537 | 0.0013668
14 | 0.010166 | 0.0025479
15 | 0.013081 | 0.0032784
16 | 0.0094913 | 0.0023787
17 | 0.027979 | 0.0070122
18 | 0.0086712 | 0.0021732
19 | 0.0039677 | 0.0009944
20 | 0.003742 | 0.00093785
21 | 0.0073241 | 0.0018356
22 | 0.0071568 | 0.0017937
23 | 0.0066042 | 0.0016552
24 | 0.0080034 | 0.0020059
25 | 0.064962 | 0.016281
26 | 0.0037103 | 0.00092989
27 | 0.0023895 | 0.00059885
28 | 0.003444 | 0.00086314
29 | 0.0048895 | 0.0012254
30 | 0.0063996 | 0.0016039
31 | 0.0045123 | 0.0011309
32 | 0.0065623 | 0.0016447
33 | 0.014239 | 0.0035686
34 | 0.009163 | 0.0022965
35 | 0.0017416 | 0.00043648
36 | 0.026441 | 0.0066267
37 | 0.0065913 | 0.0016519
38 | 0.0044372 | 0.0011121
39 | 0.018162 | 0.0045518
40 | 0.0044777 | 0.0011222

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1