## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-257_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-257_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-257_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-257_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-257_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-257_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_2701-257_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2701-257_0_4_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_2701-257_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2701-257_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2701-257_0_4_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_2701-257_0_4_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_2701-257_0_4_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_2701-257_0_4_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_2701-257_0_4_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_2701-257_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2701-257_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2701-257_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2701-257_0_4_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_2701-257_0_4_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_2701-257_0_4_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_2701-257_0_4_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_2701-257_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_2701-257_0_4_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_2701-257_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_2701-257_0_4_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_2701-257_0_4_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_2701-257_0_4_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_2701-257_0_4_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_2701-257_0_4_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_2701-257_0_4_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_2701-257_0_4_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_2701-257_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_MV_559_0_node_15 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-257_0_4_load_0 | 0 | 0.0028364 | 0.00071087 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-257_0_4_load_1 | 1 | 0.011326 | 0.0028386 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-257_0_4_load_2 | 2 | 0.01848 | 0.0046316 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-257_0_4_load_3 | 3 | 0.0096973 | 0.0024304 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-257_0_4_load_4 | 4 | 0.0085572 | 0.0021446 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-257_0_4_load_8 | 5 | 0.0097483 | 0.0024432 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-257_0_4_load_16 | 7 | 0.0095614 | 0.0023963 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-257_0_4_load_6 | 8 | 0.050552 | 0.01267 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-257_0_4_load_7 | 9 | 0.0099147 | 0.0024849 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-257_0_4_load_14 | 10 | 0.0079469 | 0.0019917 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-257_0_4_load_18 | 11 | 0.011604 | 0.0029083 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-257_0_4_load_15 | 12 | 0.0091504 | 0.0022933 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-257_0_4_load_19 | 13 | 0.015441 | 0.0038698 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-257_0_4_load_17 | 14 | 0.0088284 | 0.0022126 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-257_0_4_load_9 | 15 | 0.02961 | 0.007421 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-257_0_4_load_12 | 17 | 0.012178 | 0.003052 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-257_0_4_load_22 | 18 | 0.033409 | 0.0083731 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-257_0_4_load_21 | 19 | 0.022658 | 0.0056785 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-257_0_4_load_20 | 22 | 0.010798 | 0.0027064 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-257_0_4_load_23 | 23 | 0.008234 | 0.0020636 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-257_0_4_load_24 | 24 | 0.0080454 | 0.0020164 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-257_0_4_load_36 | 27 | 0.029097 | 0.0072923 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-257_0_4_load_37 | 28 | 0.033243 | 0.0083314 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-257_0_4_load_34 | 29 | 0.032982 | 0.0082661 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-257_0_4_load_31 | 30 | 0.027519 | 0.006897 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-257_0_4_load_35 | 31 | 0.032697 | 0.0081945 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-257_0_4_load_32 | 32 | 0.033694 | 0.0084444 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-257_0_4_line_0 |  | 0 | 1 | 0.00029948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-257_0_4_line_1 |  | 0 | 2 | 0.0116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-257_0_4_line_2 |  | 1 | 3 | 5.8121e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-257_0_4_line_3 |  | 2 | 4 | 0.00034354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-257_0_4_line_4 |  | 3 | 5 | 0.009744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-257_0_4_line_5 |  | 4 | 6 | 0.0080518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-257_0_4_line_6 |  | 5 | 7 | 0.00017108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-257_0_4_line_7 |  | 6 | 8 | 0.019383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2701-257_0_4_line_8 |  | 6 | 9 | 0.011015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-257_0_4_line_9 |  | 7 | 14 | 0.0078225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-257_0_4_line_10 |  | 8 | 10 | 0.0010218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2701-257_0_4_line_11 |  | 9 | 11 | 0.0013126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-257_0_4_line_12 |  | 10 | 12 | 0.009238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2701-257_0_4_line_13 |  | 11 | 13 | 0.012902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-257_0_4_line_14 |  | 12 | 20 | 0.0092266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2701-257_0_4_line_15 |  | 13 | 22 | 0.00010928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-257_0_4_line_16 |  | 14 | 17 | 0.0094875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-257_0_4_line_17 |  | 15 | 16 | 0.0197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-257_0_4_line_18 |  | 16 | 17 | 0.013977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-257_0_4_line_19 |  | 18 | 19 | 0.0053349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-257_0_4_line_20 |  | 19 | 22 | 0.010553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-257_0_4_line_21 |  | 20 | 21 | 0.003634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2701-257_0_4_line_22 |  | 21 | 25 | 0.007192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2701-257_0_4_line_23 |  | 21 | 24 | 0.020665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-257_0_4_line_24 |  | 23 | 24 | 0.0068633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-257_0_4_line_25 |  | 25 | 26 | 0.022998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-257_0_4_line_26 |  | 25 | 27 | 0.020442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-257_0_4_line_27 |  | 26 | 30 | 0.0023085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-257_0_4_line_28 |  | 27 | 31 | 0.0035673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-257_0_4_line_29 |  | 28 | 29 | 0.0088398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-257_0_4_line_30 |  | 29 | 32 | 0.0073504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-257_0_4_line_31 |  | 30 | 32 | 0.0083746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-257_0_4_trafo_6 | 0.63 MVA 20/0.4 kV | 33 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2611877.8155 | 1268065.7474 | 2611877.6853 | 1268066.0171
1 | 2611877.8155 | 1268065.7474 | 2611882.856 | 1268055.3
2 | 2611877.6853 | 1268066.0171 | 2611877.6601 | 1268066.0694
3 | 2611883.0052 | 1268054.9906 | 2611882.856 | 1268055.3
4 | 2611877.6601 | 1268066.0694 | 2611873.426 | 1268074.8455
5 | 2611886.504 | 1268047.7387 | 2611883.0052 | 1268054.9906
6 | 2611873.426 | 1268074.8455 | 2611873.3516 | 1268074.9995
7 | 2611886.504 | 1268047.7387 | 2611894.5828 | 1268030.12
8 | 2611886.504 | 1268047.7387 | 2611876.4899 | 1268043.1511
9 | 2611869.9525 | 1268082.0449 | 2611873.3516 | 1268074.9995
10 | 2611895.0087 | 1268029.1912 | 2611894.5828 | 1268030.12
11 | 2611876.4899 | 1268043.1511 | 2611875.2965 | 1268042.6044
12 | 2611898.8591 | 1268020.7939 | 2611895.0087 | 1268029.1912
13 | 2611863.5668 | 1268037.2309 | 2611875.2965 | 1268042.6044
14 | 2611902.9884 | 1268012.547 | 2611900.4048 | 1268017.423 | 2611898.8591 | 1268020.7939
15 | 2611863.4675 | 1268037.1854 | 2611863.5668 | 1268037.2309
16 | 2611869.9525 | 1268082.0449 | 2611865.8299 | 1268090.5898
17 | 2611859.7593 | 1268103.1797 | 2611878.0596 | 1268110.4726
18 | 2611859.7593 | 1268103.1797 | 2611863.5984 | 1268095.2151 | 2611865.8299 | 1268090.5898
19 | 2611853.873 | 1268032.79 | 2611853.0823 | 1268032.4278 | 2611848.6721 | 1268031.7291
20 | 2611853.873 | 1268032.79 | 2611863.4675 | 1268037.1854
21 | 2611902.9884 | 1268012.547 | 2611904.0461 | 1268010.5477 | 2611904.7183 | 1268009.3482
22 | 2611907.5462 | 1268002.7381 | 2611905.7082 | 1268007.3487 | 2611904.7183 | 1268009.3482
23 | 2611904.7183 | 1268009.3482 | 2611886.2193 | 1268000.138
24 | 2611880.0754 | 1267997.0792 | 2611886.2193 | 1268000.138
25 | 2611907.5462 | 1268002.7381 | 2611886.8024 | 1267992.6784
26 | 2611907.5462 | 1268002.7381 | 2611914.2486 | 1267983.4257
27 | 2611886.8024 | 1267992.6784 | 2611884.7422 | 1267991.6369
28 | 2611915.4182 | 1267980.0556 | 2611914.2486 | 1267983.4257
29 | 2611870.7086 | 1267984.5423 | 2611862.8196 | 1267980.5541
30 | 2611877.2684 | 1267987.8585 | 2611870.7086 | 1267984.5423
31 | 2611884.7422 | 1267991.6369 | 2611877.2684 | 1267987.8585

## bus_geodata
| x | y | coords
0 | 2611877.8155 | 1268065.7474
1 | 2611877.6853 | 1268066.0171
2 | 2611882.856 | 1268055.3
3 | 2611877.6601 | 1268066.0694
4 | 2611883.0052 | 1268054.9906
5 | 2611873.426 | 1268074.8455
6 | 2611886.504 | 1268047.7387
7 | 2611873.3516 | 1268074.9995
8 | 2611894.5828 | 1268030.12
9 | 2611876.4899 | 1268043.1511
10 | 2611895.0087 | 1268029.1912
11 | 2611875.2965 | 1268042.6044
12 | 2611898.8591 | 1268020.7939
13 | 2611863.5668 | 1268037.2309
14 | 2611869.9525 | 1268082.0449
15 | 2611878.0596 | 1268110.4726
16 | 2611859.7593 | 1268103.1797
17 | 2611865.8299 | 1268090.5898
18 | 2611848.6721 | 1268031.7291
19 | 2611853.873 | 1268032.79
20 | 2611902.9884 | 1268012.547
21 | 2611904.7183 | 1268009.3482
22 | 2611863.4675 | 1268037.1854
23 | 2611880.0754 | 1267997.0792
24 | 2611886.2193 | 1268000.138
25 | 2611907.5462 | 1268002.7381
26 | 2611886.8024 | 1267992.6784
27 | 2611914.2486 | 1267983.4257
28 | 2611862.8196 | 1267980.5541
29 | 2611870.7086 | 1267984.5423
30 | 2611884.7422 | 1267991.6369
31 | 2611915.4182 | 1267980.0556
32 | 2611877.2684 | 1267987.8585
33 | 2611886.504 | 1268047.7387

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9961 | -0.074829 | 0.0028364 | 0.00071087
1 | 0.99608 | -0.075307 | 0.011326 | 0.0028386
2 | 0.9971 | -0.055737 | 0.01848 | 0.0046316
3 | 0.99608 | -0.075388 | 0.0096973 | 0.0024304
4 | 0.99713 | -0.055061 | 0.0085572 | 0.0021446
5 | 0.99545 | -0.087366 | 0.0097483 | 0.0024432
6 | 0.99802 | -0.038022 | 0 | 0
7 | 0.99544 | -0.087547 | 0.0095614 | 0.0023963
8 | 1 | 0 | -0.45088 | -0.11335
9 | 0.99698 | -0.058055 | 0.0099147 | 0.0024849
10 | 0.9999 | -0.0019825 | 0.0079469 | 0.0019917
11 | 0.99686 | -0.060217 | 0.011604 | 0.0029083
12 | 0.99899 | -0.019284 | 0.0091504 | 0.0022933
13 | 0.9959 | -0.07886 | 0.015441 | 0.0038698
14 | 0.99508 | -0.094514 | 0.0088284 | 0.0022126
15 | 0.99381 | -0.11908 | 0.02961 | 0.007421
16 | 0.99434 | -0.10879 | 0 | 0
17 | 0.99472 | -0.1015 | 0.012178 | 0.003052
18 | 0.99519 | -0.092528 | 0.033409 | 0.0083731
19 | 0.99535 | -0.089392 | 0.022658 | 0.0056785
20 | 0.99813 | -0.035856 | 0 | 0
21 | 0.99779 | -0.042391 | 0 | 0
22 | 0.99589 | -0.078989 | 0.010798 | 0.0027064
23 | 0.99743 | -0.049273 | 0.008234 | 0.0020636
24 | 0.99748 | -0.048283 | 0.0080454 | 0.0020164
25 | 0.99717 | -0.054312 | 0 | 0
26 | 0.99449 | -0.10582 | 0 | 0
27 | 0.99602 | -0.07648 | 0.029097 | 0.0072923
28 | 0.99275 | -0.13957 | 0.033243 | 0.0083314
29 | 0.99301 | -0.13438 | 0.032982 | 0.0082661
30 | 0.99422 | -0.11101 | 0.027519 | 0.006897
31 | 0.99591 | -0.078529 | 0.032697 | 0.0081945
32 | 0.99346 | -0.12578 | 0.033694 | 0.0084444
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.091048 | 0.022856 | -0.091046 | -0.022855 | 2.0779e-06 | 1.326e-06 | 0.13602 | 0.13602 | 0.13602 | 0.9961 | -0.074829 | 0.99608 | -0.075307 | 37.3691
1 | -0.093884 | -0.023567 | 0.09397 | 0.023622 | 8.5576e-05 | 5.4617e-05 | 0.14026 | 0.14026 | 0.14026 | 0.9961 | -0.074829 | 0.9971 | -0.055737 | 38.5331
2 | 0.07972 | 0.020016 | -0.079719 | -0.020016 | 3.0919e-07 | 1.9712e-07 | 0.1191 | 0.1191 | 0.1191 | 0.99608 | -0.075307 | 0.99608 | -0.075388 | 32.7209
3 | -0.11245 | -0.028253 | 0.11245 | 0.028256 | 3.6291e-06 | 2.3181e-06 | 0.16784 | 0.16784 | 0.16784 | 0.9971 | -0.055737 | 0.99713 | -0.055061 | 46.1098
4 | 0.070022 | 0.017586 | -0.069982 | -0.01756 | 3.9992e-05 | 2.5468e-05 | 0.10462 | 0.10462 | 0.10462 | 0.99608 | -0.075388 | 0.99545 | -0.087366 | 28.7411
5 | -0.12101 | -0.0304 | 0.12111 | 0.030463 | 9.8494e-05 | 6.2931e-05 | 0.18061 | 0.18061 | 0.18061 | 0.99713 | -0.055061 | 0.99802 | -0.038022 | 49.618
6 | 0.060234 | 0.015117 | -0.060233 | -0.015117 | 5.2018e-07 | 3.3069e-07 | 0.090046 | 0.090046 | 0.090046 | 0.99545 | -0.087366 | 0.99544 | -0.087547 | 24.7378
7 | -0.22515 | -0.056621 | 0.22556 | 0.056883 | 0.0004097 | 0.0002617 | 0.33576 | 0.33576 | 0.33576 | 0.99802 | -0.038022 | 1 | 0 | 46.1208
8 | 0.10404 | 0.026158 | -0.10394 | -0.026095 | 9.943e-05 | 6.3492e-05 | 0.15515 | 0.15515 | 0.15515 | 0.99802 | -0.038022 | 0.99698 | -0.058055 | 42.6237
9 | 0.050672 | 0.012721 | -0.050655 | -0.01271 | 1.6834e-05 | 1.0672e-05 | 0.075753 | 0.075753 | 0.075753 | 0.99544 | -0.087547 | 0.99508 | -0.094514 | 20.8113
10 | 0.22367 | 0.056468 | -0.22365 | -0.056454 | 2.1241e-05 | 1.3567e-05 | 0.33297 | 0.33297 | 0.33297 | 1 | 0 | 0.9999 | -0.0019825 | 45.7372
11 | 0.094026 | 0.02361 | -0.094016 | -0.023604 | 9.6962e-06 | 6.1885e-06 | 0.14035 | 0.14035 | 0.14035 | 0.99698 | -0.058055 | 0.99686 | -0.060217 | 38.5583
12 | 0.2157 | 0.054462 | -0.21552 | -0.054348 | 0.00017864 | 0.00011408 | 0.32114 | 0.32114 | 0.32114 | 0.9999 | -0.0019825 | 0.99899 | -0.019284 | 44.1128
13 | 0.082412 | 0.020695 | -0.082339 | -0.020649 | 7.3234e-05 | 4.6702e-05 | 0.12303 | 0.12303 | 0.12303 | 0.99686 | -0.060217 | 0.9959 | -0.07886 | 33.7996
14 | 0.20637 | 0.052055 | -0.20621 | -0.051951 | 0.00016359 | 0.00010446 | 0.30751 | 0.30751 | 0.30751 | 0.99899 | -0.019284 | 0.99813 | -0.035856 | 42.2406
15 | 0.066898 | 0.016779 | -0.066898 | -0.016779 | 4.0946e-07 | 2.6063e-07 | 0.09996 | 0.09996 | 0.09996 | 0.9959 | -0.07886 | 0.99589 | -0.078989 | 27.4616
16 | 0.041827 | 0.010497 | -0.041813 | -0.010488 | 1.392e-05 | 8.7859e-06 | 0.062551 | 0.062551 | 0.062551 | 0.99508 | -0.094514 | 0.99472 | -0.1015 | 17.1844
17 | -0.02961 | -0.007421 | 0.029625 | 0.00743 | 1.452e-05 | 9.0377e-06 | 0.044335 | 0.044335 | 0.044335 | 0.99381 | -0.11908 | 0.99434 | -0.10879 | 12.1798
18 | -0.029625 | -0.00743 | 0.029635 | 0.0074364 | 1.0302e-05 | 6.412e-06 | 0.044335 | 0.044334 | 0.044335 | 0.99434 | -0.10879 | 0.99472 | -0.1015 | 12.1798
19 | -0.033409 | -0.0083731 | 0.033414 | 0.0083762 | 4.9922e-06 | 3.1256e-06 | 0.049953 | 0.049953 | 0.049953 | 0.99519 | -0.092528 | 0.99535 | -0.089392 | 13.7235
20 | -0.056071 | -0.014055 | 0.056099 | 0.014072 | 2.7808e-05 | 1.766e-05 | 0.083826 | 0.083826 | 0.083826 | 0.99535 | -0.089392 | 0.99589 | -0.078989 | 23.029
21 | 0.20621 | 0.051951 | -0.20614 | -0.051909 | 6.4433e-05 | 4.1142e-05 | 0.30751 | 0.30751 | 0.30751 | 0.99813 | -0.035856 | 0.99779 | -0.042391 | 42.2406
22 | 0.18986 | 0.047827 | -0.18975 | -0.047758 | 0.00010817 | 6.9043e-05 | 0.28323 | 0.28323 | 0.28323 | 0.99779 | -0.042391 | 0.99717 | -0.054312 | 38.9046
23 | 0.016284 | 0.0040828 | -0.01628 | -0.0040802 | 4.5706e-06 | 2.6553e-06 | 0.024286 | 0.024286 | 0.024286 | 0.99779 | -0.042391 | 0.99748 | -0.048283 | 6.6719
24 | -0.008234 | -0.0020636 | 0.0082344 | 0.0020638 | 3.8836e-07 | 1.5897e-07 | 0.012284 | 0.012284 | 0.012284 | 0.99743 | -0.049273 | 0.99748 | -0.048283 | 3.3747
25 | 0.12789 | 0.032227 | -0.12757 | -0.032026 | 0.0003143 | 0.00020086 | 0.1909 | 0.1909 | 0.1909 | 0.99717 | -0.054312 | 0.99449 | -0.10582 | 52.4461
26 | 0.061862 | 0.01553 | -0.061796 | -0.015489 | 6.5339e-05 | 4.1551e-05 | 0.092322 | 0.092322 | 0.092322 | 0.99717 | -0.054312 | 0.99602 | -0.07648 | 25.3632
27 | 0.12757 | 0.032026 | -0.12754 | -0.032006 | 3.1549e-05 | 2.0162e-05 | 0.1909 | 0.1909 | 0.1909 | 0.99449 | -0.10582 | 0.99422 | -0.11101 | 52.4461
28 | 0.0327 | 0.0081965 | -0.032697 | -0.0081945 | 3.1926e-06 | 1.9968e-06 | 0.048853 | 0.048853 | 0.048853 | 0.99602 | -0.07648 | 0.99591 | -0.078529 | 13.4211
29 | -0.033243 | -0.0083314 | 0.033251 | 0.0083365 | 8.23e-06 | 5.1529e-06 | 0.049827 | 0.049827 | 0.049827 | 0.99275 | -0.13957 | 0.99301 | -0.13438 | 13.6887
30 | -0.066233 | -0.016603 | 0.06626 | 0.01662 | 2.7152e-05 | 1.7282e-05 | 0.09925 | 0.09925 | 0.09925 | 0.99301 | -0.13438 | 0.99346 | -0.12578 | 27.2665
31 | 0.10002 | 0.025109 | -0.099954 | -0.025064 | 7.0394e-05 | 4.4944e-05 | 0.14972 | 0.14972 | 0.14972 | 0.99422 | -0.11101 | 0.99346 | -0.12578 | 41.131

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50143 | 0.12602

## res_load
| p_mw | q_mvar
0 | 0.0028364 | 0.00071087
1 | 0.011326 | 0.0028386
2 | 0.01848 | 0.0046316
3 | 0.0096973 | 0.0024304
4 | 0.0085572 | 0.0021446
5 | 0.0097483 | 0.0024432
6 | 0.0095614 | 0.0023963
7 | 0.050552 | 0.01267
8 | 0.0099147 | 0.0024849
9 | 0.0079469 | 0.0019917
10 | 0.011604 | 0.0029083
11 | 0.0091504 | 0.0022933
12 | 0.015441 | 0.0038698
13 | 0.0088284 | 0.0022126
14 | 0.02961 | 0.007421
15 | 0.012178 | 0.003052
16 | 0.033409 | 0.0083731
17 | 0.022658 | 0.0056785
18 | 0.010798 | 0.0027064
19 | 0.008234 | 0.0020636
20 | 0.0080454 | 0.0020164
21 | 0.029097 | 0.0072923
22 | 0.033243 | 0.0083314
23 | 0.032982 | 0.0082661
24 | 0.027519 | 0.006897
25 | 0.032697 | 0.0081945
26 | 0.033694 | 0.0084444

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1