## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-26_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-26_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-26_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2701-26_0_4_node_16 | 0.4 | n |  | TRUE
4 | bus_LV_2701-26_0_4_node_30 | 0.4 | n |  | TRUE
5 | bus_LV_2701-26_0_4_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_2701-26_0_4_node_68 | 0.4 | n |  | TRUE
7 | bus_LV_2701-26_0_4_node_56 | 0.4 | n |  | TRUE
8 | bus_LV_2701-26_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_2701-26_0_4_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_2701-26_0_4_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_2701-26_0_4_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_2701-26_0_4_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_2701-26_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2701-26_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2701-26_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2701-26_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2701-26_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2701-26_0_4_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_2701-26_0_4_node_35 | 0.4 | n |  | TRUE
20 | bus_LV_2701-26_0_4_node_37 | 0.4 | n |  | TRUE
21 | bus_LV_2701-26_0_4_node_36 | 0.4 | n |  | TRUE
22 | bus_LV_2701-26_0_4_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_2701-26_0_4_node_59 | 0.4 | n |  | TRUE
24 | bus_LV_2701-26_0_4_node_74 | 0.4 | n |  | TRUE
25 | bus_LV_2701-26_0_4_node_66 | 0.4 | n |  | TRUE
26 | bus_LV_2701-26_0_4_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_2701-26_0_4_node_67 | 0.4 | n |  | TRUE
28 | bus_LV_2701-26_0_4_node_77 | 0.4 | n |  | TRUE
29 | bus_LV_2701-26_0_4_node_61 | 0.4 | n |  | TRUE
30 | bus_LV_2701-26_0_4_node_73 | 0.4 | n |  | TRUE
31 | bus_LV_2701-26_0_4_node_60 | 0.4 | n |  | TRUE
32 | bus_LV_2701-26_0_4_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_2701-26_0_4_node_42 | 0.4 | n |  | TRUE
34 | bus_LV_2701-26_0_4_node_57 | 0.4 | n |  | TRUE
35 | bus_LV_2701-26_0_4_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_2701-26_0_4_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_2701-26_0_4_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_2701-26_0_4_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_2701-26_0_4_node_52 | 0.4 | n |  | TRUE
40 | bus_LV_2701-26_0_4_node_51 | 0.4 | n |  | TRUE
41 | bus_LV_2701-26_0_4_node_45 | 0.4 | n |  | TRUE
42 | bus_LV_2701-26_0_4_node_46 | 0.4 | n |  | TRUE
43 | bus_LV_2701-26_0_4_node_47 | 0.4 | n |  | TRUE
44 | bus_LV_2701-26_0_4_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_2701-26_0_4_node_53 | 0.4 | n |  | TRUE
46 | bus_LV_2701-26_0_4_node_75 | 0.4 | n |  | TRUE
47 | bus_LV_2701-26_0_4_node_58 | 0.4 | n |  | TRUE
48 | bus_MV_570_0_node_37 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-26_0_4_load_0 | 0 | 0.028696 | 0.0071919 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-26_0_4_load_1 | 1 | 0.0024925 | 0.00062469 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-26_0_4_load_68 | 6 | 0.0017581 | 0.00044061 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-26_0_4_load_11 | 8 | 0.0068426 | 0.0017149 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-26_0_4_load_14 | 10 | 0.00086819 | 0.00021759 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-26_0_4_load_26 | 12 | 0.015395 | 0.0038584 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-26_0_4_load_8 | 13 | 0.057003 | 0.014286 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-26_0_4_load_9 | 14 | 0.0094929 | 0.0023791 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-26_0_4_load_12 | 16 | 0.0053748 | 0.0013471 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-26_0_4_load_13 | 17 | 0.024828 | 0.0062225 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-26_0_4_load_27 | 18 | 0.0023439 | 0.00058744 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-26_0_4_load_36 | 21 | 0.012657 | 0.0031722 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-26_0_4_load_28 | 22 | 0.0017699 | 0.00044357 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-26_0_4_load_74 | 24 | 0.00046767 | 0.00011721 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-26_0_4_load_66 | 25 | 0.00082614 | 0.00020705 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-26_0_4_load_77 | 28 | 0.0015308 | 0.00038365 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-26_0_4_load_73 | 30 | 0.001106 | 0.00027719 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-26_0_4_load_60 | 31 | 0.0056026 | 0.0014042 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-26_0_4_load_42 | 33 | 0.0011063 | 0.00027727 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-26_0_4_load_57 | 34 | 0.0027447 | 0.0006879 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-26_0_4_load_50 | 35 | 0.00070354 | 0.00017632 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-26_0_4_load_40 | 36 | 0.0032432 | 0.00081281 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-26_0_4_load_41 | 37 | 0.001143 | 0.00028645 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-26_0_4_load_43 | 38 | 0.0011802 | 0.00029579 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-26_0_4_load_52 | 39 | 0.001147 | 0.00028746 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-26_0_4_load_51 | 40 | 0.0023436 | 0.00058736 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-26_0_4_load_45 | 41 | 0.046194 | 0.011577 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-26_0_4_load_46 | 42 | 0.007902 | 0.0019804 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-26_0_4_load_53 | 45 | 0.0088149 | 0.0022092 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-26_0_4_load_75 | 46 | 0.069429 | 0.017401 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-26_0_4_load_58 | 47 | 0.0056616 | 0.0014189 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-26_0_4_line_0 |  | 0 | 1 | 0.007683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-26_0_4_line_1 |  | 1 | 2 | 0.091801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-26_0_4_line_2 |  | 2 | 3 | 0.011653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-26_0_4_line_3 |  | 3 | 9 | 0.065018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-26_0_4_line_4 |  | 3 | 10 | 0.18123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-26_0_4_line_5 |  | 4 | 5 | 0.053178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-26_0_4_line_6 |  | 4 | 6 | 0.045488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-26_0_4_line_7 |  | 5 | 7 | 0.036315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2701-26_0_4_line_8 |  | 5 | 8 | 0.02835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_2701-26_0_4_line_9 |  | 6 | 11 | 0.042105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-26_0_4_line_10 |  | 7 | 23 | 0.26375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2701-26_0_4_line_11 |  | 7 | 24 | 0.034858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-26_0_4_line_12 |  | 8 | 14 | 0.038819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2701-26_0_4_line_13 |  | 9 | 11 | 0.031616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-26_0_4_line_14 |  | 9 | 12 | 0.050746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-26_0_4_line_15 |  | 12 | 18 | 0.10882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-26_0_4_line_16 |  | 13 | 14 | 0.074816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2701-26_0_4_line_17 |  | 13 | 15 | 0.063624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-26_0_4_line_18 |  | 15 | 16 | 0.026626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-26_0_4_line_19 |  | 15 | 17 | 0.086262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-26_0_4_line_20 |  | 18 | 22 | 0.049294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-26_0_4_line_21 |  | 19 | 20 | 0.19838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2701-26_0_4_line_22 |  | 19 | 21 | 0.041577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-26_0_4_line_23 |  | 20 | 25 | 0.054312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2701-26_0_4_line_24 |  | 23 | 34 | 0.048006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_2701-26_0_4_line_25 |  | 24 | 46 | 0.00074556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-26_0_4_line_26 |  | 25 | 27 | 0.014192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2701-26_0_4_line_27 |  | 26 | 27 | 0.012466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-26_0_4_line_28 |  | 26 | 28 | 0.015644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-26_0_4_line_29 |  | 27 | 35 | 0.01583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_2701-26_0_4_line_30 |  | 29 | 30 | 0.015443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2701-26_0_4_line_31 |  | 29 | 31 | 0.014518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2701-26_0_4_line_32 |  | 30 | 32 | 0.01027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_2701-26_0_4_line_33 |  | 31 | 47 | 0.014391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_2701-26_0_4_line_34 |  | 32 | 33 | 0.016869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2701-26_0_4_line_35 |  | 33 | 36 | 0.0044293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_2701-26_0_4_line_36 |  | 34 | 47 | 0.006691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_2701-26_0_4_line_37 |  | 35 | 43 | 0.018142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_2701-26_0_4_line_38 |  | 36 | 37 | 0.0039516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2701-26_0_4_line_39 |  | 37 | 38 | 0.0094894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2701-26_0_4_line_40 |  | 38 | 39 | 0.0033773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2701-26_0_4_line_41 |  | 39 | 40 | 0.016297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2701-26_0_4_line_42 |  | 40 | 44 | 0.00096494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2701-26_0_4_line_43 |  | 41 | 42 | 0.0071377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-26_0_4_line_44 |  | 41 | 43 | 0.028321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2701-26_0_4_line_45 |  | 43 | 44 | 0.031183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2701-26_0_4_line_46 |  | 44 | 45 | 0.006141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-26_0_4_trafo_8 | 0.63 MVA 20/0.4 kV | 48 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2611160.6912 | 1270352.5304 | 2611160.3345 | 1270350.7337 | 2611159.7584 | 1270344.9109
1 | 2611177.0358 | 1270258.5664 | 2611172.7947 | 1270261.5828 | 2611168.8016 | 1270264.6886 | 2611166.4624 | 1270268.4757 | 2611165.2812 | 1270272.532 | 2611159.1809 | 1270316.107 | 2611158.7029 | 1270334.2412 | 2611159.7584 | 1270344.9109
2 | 2611178.2628 | 1270270.1547 | 2611177.0358 | 1270258.5664
3 | 2611178.2628 | 1270270.1547 | 2611180.8067 | 1270265.5784 | 2611184.6662 | 1270261.4717 | 2611189.8623 | 1270258.7017 | 2611213.4238 | 1270251.0407 | 2611235.9014 | 1270243.7224
4 | 2611178.2628 | 1270270.1547 | 2611176.8277 | 1270277.1903 | 2611178.3977 | 1270294.3832 | 2611180.5148 | 1270308.7085 | 2611183.6246 | 1270323.1913 | 2611207.2107 | 1270409.9529 | 2611219.9437 | 1270445.3078
5 | 2611313.9324 | 1270218.8751 | 2611319.5107 | 1270216.9622 | 2611320.9034 | 1270216.4645 | 2611322.9961 | 1270215.768 | 2611355.273 | 1270206.3674 | 2611356.5903 | 1270205.9918 | 2611356.944 | 1270205.9036 | 2611364.8253 | 1270203.4836
6 | 2611313.9324 | 1270218.8751 | 2611315.719 | 1270224.8717 | 2611315.0946 | 1270232.7761 | 2611300.0082 | 1270238.1178 | 2611298.6839 | 1270246.1544 | 2611291.8178 | 1270248.1579
7 | 2611364.8253 | 1270203.4836 | 2611374.4754 | 1270200.6 | 2611375.4013 | 1270200.3016 | 2611380.445 | 1270198.6545 | 2611381.258 | 1270198.3892 | 2611399.5055 | 1270192.3866
8 | 2611364.8253 | 1270203.4836 | 2611374.0978 | 1270230.2743
9 | 2611251.3981 | 1270259.9522 | 2611291.8178 | 1270248.1579
10 | 2611399.5055 | 1270192.3866 | 2611509.2768 | 1270156.5062 | 2611522.3104 | 1270150.8163 | 2611528.5223 | 1270148.1042 | 2611539.9444 | 1270143.234 | 2611541.4753 | 1270145.1828 | 2611543.4811 | 1270146.6545 | 2611545.8041 | 1270147.5263 | 2611548.2863 | 1270147.7535 | 2611550.7322 | 1270147.3135 | 2611554.1014 | 1270155.6148 | 2611555.4352 | 1270158.386 | 2611588.1053 | 1270225.3416 | 2611590.0456 | 1270241.1121
11 | 2611399.5055 | 1270192.3866 | 2611409.3847 | 1270225.8152
12 | 2611387.5935 | 1270266.6659 | 2611378.6963 | 1270243.5608 | 2611374.0978 | 1270230.2743
13 | 2611251.3981 | 1270259.9522 | 2611247.2933 | 1270242.6099 | 2611246.6058 | 1270240.1846 | 2611245.5369 | 1270240.5384 | 2611244.5733 | 1270240.8479 | 2611235.9014 | 1270243.7224
14 | 2611235.9014 | 1270243.7224 | 2611239.0415 | 1270254.0357 | 2611238.0544 | 1270262.8178 | 2611230.5831 | 1270271.2986 | 2611214.2183 | 1270276.4714 | 2611212.6313 | 1270278.6098
15 | 2611230.8398 | 1270381.6934 | 2611205.492 | 1270288.2299 | 2611212.6313 | 1270278.6098
16 | 2611387.5935 | 1270266.6659 | 2611395.7413 | 1270287.8249 | 2611414.6193 | 1270336.4297
17 | 2611437.6544 | 1270395.7376 | 2611414.6193 | 1270336.4297
18 | 2611437.6544 | 1270395.7376 | 2611432.0833 | 1270397.9395 | 2611428.0405 | 1270399.5329 | 2611412.8869 | 1270405.5098
19 | 2611437.6544 | 1270395.7376 | 2611469.3427 | 1270475.9687
20 | 2611243.7425 | 1270429.2689 | 2611230.8398 | 1270381.6934
21 | 2611498.3841 | 1270443.4554 | 2611507.3792 | 1270440.6819 | 2611507.1415 | 1270435.2665 | 2611511.6181 | 1270434.9972 | 2611516.1022 | 1270434.7168 | 2611515.2565 | 1270420.8164 | 2611571.4872 | 1270418.146 | 2611593.343 | 1270417.1101 | 2611598.5734 | 1270389.0893 | 2611601.1752 | 1270366.5784 | 2611602.0314 | 1270351.8697 | 2611602.297 | 1270335.3029
22 | 2611498.3841 | 1270443.4554 | 2611485.8239 | 1270422.5718 | 2611479.7271 | 1270406.481
23 | 2611602.297 | 1270335.3029 | 2611559.0951 | 1270338.0762 | 2611548.1878 | 1270339.654
24 | 2611590.0456 | 1270241.1121 | 2611542.8069 | 1270249.6595
25 | 2611409.596 | 1270226.5302 | 2611409.3847 | 1270225.8152
26 | 2611534.1421 | 1270341.6858 | 2611548.1878 | 1270339.654
27 | 2611534.1421 | 1270341.6858 | 2611534.2834 | 1270354.1505
28 | 2611534.2834 | 1270354.1505 | 2611534.0076 | 1270368.3266 | 2611535.4689 | 1270368.2255
29 | 2611534.1421 | 1270341.6858 | 2611524.7358 | 1270343.0463 | 2611518.4841 | 1270344.0115
30 | 2611549.4117 | 1270284.6416 | 2611552.0434 | 1270299.8592
31 | 2611549.4117 | 1270284.6416 | 2611546.7183 | 1270270.376
32 | 2611553.7934 | 1270309.9792 | 2611552.0434 | 1270299.8592
33 | 2611544.0483 | 1270256.2344 | 2611546.7183 | 1270270.376
34 | 2611553.7934 | 1270309.9792 | 2611537.013 | 1270311.706
35 | 2611532.607 | 1270312.1594 | 2611537.013 | 1270311.706
36 | 2611542.8069 | 1270249.6595 | 2611544.0483 | 1270256.2344
37 | 2611504.9875 | 1270339.4943 | 2611507.0968 | 1270345.7696 | 2611518.4841 | 1270344.0115
38 | 2611532.607 | 1270312.1594 | 2611528.6762 | 1270312.5639
39 | 2611528.6762 | 1270312.5639 | 2611524.5233 | 1270312.9912 | 2611519.2091 | 1270313.0572
40 | 2611515.8384 | 1270312.8888 | 2611518.3318 | 1270313.0681 | 2611519.2091 | 1270313.0572
41 | 2611499.957 | 1270309.3718 | 2611513.405 | 1270312.7139 | 2611515.8384 | 1270312.8888
42 | 2611499.957 | 1270309.3718 | 2611499.0205 | 1270309.139
43 | 2611478.4576 | 1270349.4056 | 2611481.0402 | 1270356.0598
44 | 2611504.9875 | 1270339.4943 | 2611478.4576 | 1270349.4056 | 2611478.4576 | 1270349.4056
45 | 2611499.0205 | 1270309.139 | 2611500.1258 | 1270324.9857 | 2611504.9875 | 1270339.4943
46 | 2611493.0805 | 1270307.5153 | 2611499.0205 | 1270309.139

## bus_geodata
| x | y | coords
0 | 2611160.6912 | 1270352.5304
1 | 2611159.7584 | 1270344.9109
2 | 2611177.0358 | 1270258.5664
3 | 2611178.2628 | 1270270.1547
4 | 2611313.9324 | 1270218.8751
5 | 2611364.8253 | 1270203.4836
6 | 2611291.8178 | 1270248.1579
7 | 2611399.5055 | 1270192.3866
8 | 2611374.0978 | 1270230.2743
9 | 2611235.9014 | 1270243.7224
10 | 2611219.9437 | 1270445.3078
11 | 2611251.3981 | 1270259.9522
12 | 2611212.6314 | 1270278.6098
13 | 2611414.6193 | 1270336.4297
14 | 2611387.5935 | 1270266.6659
15 | 2611437.6544 | 1270395.7376
16 | 2611412.8869 | 1270405.5098
17 | 2611469.3427 | 1270475.9687
18 | 2611230.8398 | 1270381.6934
19 | 2611498.3841 | 1270443.4554
20 | 2611602.297 | 1270335.3029
21 | 2611479.7271 | 1270406.481
22 | 2611243.7425 | 1270429.2689
23 | 2611590.0456 | 1270241.1121
24 | 2611409.3847 | 1270225.8152
25 | 2611548.1878 | 1270339.654
26 | 2611534.2834 | 1270354.1505
27 | 2611534.1421 | 1270341.6858
28 | 2611535.4689 | 1270368.2255
29 | 2611549.4117 | 1270284.6416
30 | 2611552.0434 | 1270299.8592
31 | 2611546.7183 | 1270270.376
32 | 2611553.7934 | 1270309.9792
33 | 2611537.013 | 1270311.706
34 | 2611542.8069 | 1270249.6595
35 | 2611518.4841 | 1270344.0115
36 | 2611532.607 | 1270312.1594
37 | 2611528.6762 | 1270312.5639
38 | 2611519.2091 | 1270313.0572
39 | 2611515.8384 | 1270312.8888
40 | 2611499.9569 | 1270309.3718
41 | 2611478.4576 | 1270349.4056
42 | 2611481.0402 | 1270356.0598
43 | 2611504.9875 | 1270339.4943
44 | 2611499.0205 | 1270309.139
45 | 2611493.0805 | 1270307.5153
46 | 2611409.596 | 1270226.5302
47 | 2611544.0483 | 1270256.2344
48 | 2611437.6544 | 1270395.7376

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97602 | -0.4616 | 0.028696 | 0.0071919
1 | 0.97622 | -0.45757 | 0.0024925 | 0.00062469
2 | 0.97888 | -0.40534 | 0 | 0
3 | 0.97922 | -0.39873 | 0 | 0
4 | 0.98693 | -0.24878 | 0 | 0
5 | 0.98957 | -0.19816 | 0 | 0
6 | 0.98468 | -0.2923 | 0.0017581 | 0.00044061
7 | 0.98761 | -0.23569 | 0 | 0
8 | 0.99156 | -0.16001 | 0.0068426 | 0.0017149
9 | 0.98116 | -0.36091 | 0 | 0
10 | 0.97907 | -0.4016 | 0.00086819 | 0.00021759
11 | 0.98267 | -0.33143 | 0 | 0
12 | 0.98024 | -0.37886 | 0.015395 | 0.0038584
13 | 1 | 0 | -0.28017 | -0.071649
14 | 0.99437 | -0.10647 | 0.0094929 | 0.0023791
15 | 0.99825 | -0.033557 | 0 | 0
16 | 0.99812 | -0.036061 | 0.0053748 | 0.0013471
17 | 0.9963 | -0.071093 | 0.024828 | 0.0062225
18 | 0.97983 | -0.38699 | 0.0023439 | 0.00058744
19 | 0.97205 | -0.53892 | 0 | 0
20 | 0.97322 | -0.51577 | 0 | 0
21 | 0.97156 | -0.54863 | 0.012657 | 0.0031722
22 | 0.97975 | -0.38857 | 0.0017699 | 0.00044357
23 | 0.9791 | -0.40045 | 0 | 0
24 | 0.98537 | -0.27933 | 0.00046767 | 0.00011721
25 | 0.97343 | -0.51155 | 0.00082614 | 0.00020705
26 | 0.97348 | -0.51073 | 0 | 0
27 | 0.97349 | -0.51038 | 0 | 0
28 | 0.97345 | -0.51117 | 0.0015308 | 0.00038365
29 | 0.9765 | -0.45117 | 0 | 0
30 | 0.97607 | -0.45964 | 0.001106 | 0.00027719
31 | 0.97691 | -0.44322 | 0.0056026 | 0.0014042
32 | 0.97579 | -0.4652 | 0 | 0
33 | 0.97532 | -0.47435 | 0.0011063 | 0.00027727
34 | 0.97755 | -0.43074 | 0.0027447 | 0.0006879
35 | 0.97357 | -0.50892 | 0.00070354 | 0.00017632
36 | 0.9752 | -0.47672 | 0.0032432 | 0.00081281
37 | 0.9751 | -0.47876 | 0.001143 | 0.00028645
38 | 0.97485 | -0.4836 | 0.0011802 | 0.00029579
39 | 0.97477 | -0.48529 | 0.001147 | 0.00028746
40 | 0.97436 | -0.49337 | 0.0023436 | 0.00058736
41 | 0.97223 | -0.53538 | 0.046194 | 0.011577
42 | 0.97218 | -0.53642 | 0.007902 | 0.0019804
43 | 0.97366 | -0.50717 | 0 | 0
44 | 0.97433 | -0.49383 | 0 | 0
45 | 0.97428 | -0.49483 | 0.0088149 | 0.0022092
46 | 0.98532 | -0.28026 | 0.069429 | 0.017401
47 | 0.97734 | -0.43485 | 0.0056616 | 0.0014189
48 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.028696 | -0.0071919 | 0.028702 | 0.0071954 | 5.5145e-06 | 3.4332e-06 | 0.043749 | 0.043749 | 0.043749 | 0.97602 | -0.4616 | 0.97622 | -0.45757 | 12.0191
1 | -0.031194 | -0.00782 | 0.031272 | 0.0078687 | 7.7831e-05 | 4.8661e-05 | 0.047549 | 0.047548 | 0.047549 | 0.97622 | -0.45757 | 0.97888 | -0.40534 | 13.0628
2 | -0.031272 | -0.0078687 | 0.031282 | 0.0078749 | 9.8796e-06 | 6.1764e-06 | 0.047548 | 0.047548 | 0.047548 | 0.97888 | -0.40534 | 0.97922 | -0.39873 | 13.0627
3 | -0.03215 | -0.0080903 | 0.032208 | 0.0081267 | 5.8223e-05 | 3.6443e-05 | 0.048867 | 0.048867 | 0.048867 | 0.97922 | -0.39873 | 0.98116 | -0.36091 | 13.425
4 | 0.00086831 | 0.00021539 | -0.00086819 | -0.00021759 | 1.1825e-07 | -2.2038e-06 | 0.0013187 | 0.0013195 | 0.0013195 | 0.97922 | -0.39873 | 0.97907 | -0.4016 | 0.3625
5 | -0.053776 | -0.013645 | 0.053908 | 0.013729 | 0.00013129 | 8.3344e-05 | 0.08114 | 0.081139 | 0.08114 | 0.98693 | -0.24878 | 0.98957 | -0.19816 | 22.2911
6 | 0.053776 | 0.013645 | -0.053664 | -0.013574 | 0.0001123 | 7.1294e-05 | 0.08114 | 0.08114 | 0.08114 | 0.98693 | -0.24878 | 0.98468 | -0.2923 | 22.2911
7 | 0.17567 | 0.044722 | -0.17535 | -0.04452 | 0.00031733 | 0.00020169 | 0.2644 | 0.2644 | 0.2644 | 0.98957 | -0.19816 | 0.98761 | -0.23569 | 24.2123
8 | -0.22957 | -0.05845 | 0.23 | 0.05872 | 0.00042311 | 0.00026969 | 0.34554 | 0.34554 | 0.34554 | 0.98957 | -0.19816 | 0.99156 | -0.16001 | 31.6426
9 | 0.051906 | 0.013133 | -0.051809 | -0.013072 | 9.7257e-05 | 6.171e-05 | 0.078483 | 0.078483 | 0.078483 | 0.98468 | -0.2923 | 0.98267 | -0.33143 | 21.5613
10 | 0.1053 | 0.026907 | -0.10447 | -0.026385 | 0.00083186 | 0.00052235 | 0.15884 | 0.15885 | 0.15885 | 0.98761 | -0.23569 | 0.9791 | -0.40045 | 14.5463
11 | 0.070045 | 0.017612 | -0.0699 | -0.01752 | 0.00014565 | 9.2769e-05 | 0.10556 | 0.10556 | 0.10556 | 0.98761 | -0.23569 | 0.98537 | -0.27933 | 28.999
12 | -0.23684 | -0.060435 | 0.23745 | 0.060826 | 0.00061429 | 0.00039164 | 0.3558 | 0.3558 | 0.3558 | 0.99156 | -0.16001 | 0.99437 | -0.10647 | 32.5829
13 | -0.051736 | -0.013025 | 0.051809 | 0.013072 | 7.3029e-05 | 4.6339e-05 | 0.078483 | 0.078483 | 0.078483 | 0.98116 | -0.36091 | 0.98267 | -0.33143 | 21.5614
14 | 0.019527 | 0.0048986 | -0.019511 | -0.0048885 | 1.6692e-05 | 1.0043e-05 | 0.029617 | 0.029617 | 0.029617 | 0.98116 | -0.36091 | 0.98024 | -0.37886 | 8.1365
15 | 0.0041155 | 0.0010301 | -0.0041139 | -0.0010305 | 1.5926e-06 | -3.5195e-07 | 0.0062469 | 0.0062474 | 0.0062474 | 0.98024 | -0.37886 | 0.97983 | -0.38699 | 1.7163
16 | 0.24823 | 0.064022 | -0.24695 | -0.063205 | 0.0012803 | 0.0008165 | 0.37001 | 0.37001 | 0.37001 | 1 | 0 | 0.99437 | -0.10647 | 33.8837
17 | 0.030297 | 0.0076272 | -0.030248 | -0.007597 | 4.8517e-05 | 3.0217e-05 | 0.045094 | 0.045094 | 0.045094 | 1 | 0 | 0.99825 | -0.033557 | 12.3885
18 | 0.0053755 | 0.0013471 | -0.0053748 | -0.0013471 | 6.4107e-07 | 6.2238e-08 | 0.0080128 | 0.0080129 | 0.0080129 | 0.99825 | -0.033557 | 0.99812 | -0.036061 | 2.2013
19 | 0.024873 | 0.0062499 | -0.024828 | -0.0062225 | 4.448e-05 | 2.7342e-05 | 0.037081 | 0.037082 | 0.037082 | 0.99825 | -0.033557 | 0.9963 | -0.071093 | 10.1873
20 | 0.00177 | 0.00044303 | -0.0017699 | -0.00044357 | 1.3355e-07 | -5.3535e-07 | 0.0026878 | 0.002688 | 0.002688 | 0.97983 | -0.38699 | 0.97975 | -0.38857 | 0.73847
21 | -0.012663 | -0.0031755 | 0.012677 | 0.0031795 | 1.3977e-05 | 4.021e-06 | 0.019385 | 0.019384 | 0.019385 | 0.97205 | -0.53892 | 0.97322 | -0.51577 | 2.6628
22 | 0.012663 | 0.0031755 | -0.012657 | -0.0031722 | 5.8592e-06 | 3.2348e-06 | 0.019385 | 0.019386 | 0.019386 | 0.97205 | -0.53892 | 0.97156 | -0.54863 | 5.3257
23 | -0.012677 | -0.0031795 | 0.01268 | 0.0031791 | 2.5507e-06 | -3.9263e-07 | 0.019384 | 0.019383 | 0.019384 | 0.97322 | -0.51577 | 0.97343 | -0.51155 | 1.7751
24 | 0.10447 | 0.026385 | -0.10432 | -0.02629 | 0.00015141 | 9.5095e-05 | 0.15885 | 0.15885 | 0.15885 | 0.9791 | -0.40045 | 0.97755 | -0.43074 | 14.5464
25 | 0.069432 | 0.017402 | -0.069429 | -0.017401 | 3.0736e-06 | 1.9576e-06 | 0.10485 | 0.10485 | 0.10485 | 0.98537 | -0.27933 | 0.98532 | -0.28026 | 28.805
26 | -0.013506 | -0.0033861 | 0.013507 | 0.0033861 | 7.5616e-07 | -4.5373e-08 | 0.020646 | 0.020646 | 0.020646 | 0.97343 | -0.51155 | 0.97349 | -0.51038 | 1.8906
27 | -0.0015308 | -0.00038348 | 0.0015309 | 0.00038334 | 2.5594e-08 | -1.3861e-07 | 0.0023399 | 0.0023398 | 0.0023399 | 0.97348 | -0.51073 | 0.97349 | -0.51038 | 0.64283
28 | 0.0015308 | 0.00038348 | -0.0015308 | -0.00038365 | 3.212e-08 | -1.7393e-07 | 0.0023399 | 0.00234 | 0.00234 | 0.97348 | -0.51073 | 0.97345 | -0.51117 | 0.64285
29 | -0.015037 | -0.0037694 | 0.015039 | 0.0037695 | 1.0454e-06 | 7.8583e-08 | 0.022985 | 0.022985 | 0.022985 | 0.97349 | -0.51038 | 0.97357 | -0.50892 | 2.1049
30 | 0.090218 | 0.022721 | -0.090181 | -0.022698 | 3.6505e-05 | 2.2784e-05 | 0.13752 | 0.13752 | 0.13752 | 0.9765 | -0.45117 | 0.97607 | -0.45964 | 12.593
31 | -0.090218 | -0.022721 | 0.090252 | 0.022742 | 3.4317e-05 | 2.1418e-05 | 0.13752 | 0.13752 | 0.13752 | 0.9765 | -0.45117 | 0.97691 | -0.44322 | 12.593
32 | 0.089075 | 0.022421 | -0.089052 | -0.022406 | 2.3685e-05 | 1.4774e-05 | 0.13583 | 0.13583 | 0.13583 | 0.97607 | -0.45964 | 0.97579 | -0.4652 | 12.4386
33 | -0.095855 | -0.024147 | 0.095893 | 0.024171 | 3.8372e-05 | 2.4017e-05 | 0.14605 | 0.14605 | 0.14605 | 0.97691 | -0.44322 | 0.97734 | -0.43485 | 13.3744
34 | 0.089052 | 0.022406 | -0.089013 | -0.022382 | 3.8903e-05 | 2.4266e-05 | 0.13583 | 0.13583 | 0.13583 | 0.97579 | -0.4652 | 0.97532 | -0.47435 | 12.4386
35 | 0.087906 | 0.022105 | -0.087896 | -0.022098 | 9.9626e-06 | 6.2103e-06 | 0.13414 | 0.13414 | 0.13414 | 0.97532 | -0.47435 | 0.9752 | -0.47672 | 12.2841
36 | 0.10157 | 0.025602 | -0.10155 | -0.025589 | 2.0008e-05 | 1.2554e-05 | 0.15467 | 0.15467 | 0.15467 | 0.97755 | -0.43074 | 0.97734 | -0.43485 | 14.1638
37 | -0.015742 | -0.0039458 | 0.015743 | 0.003946 | 1.3128e-06 | 1.6336e-07 | 0.024061 | 0.02406 | 0.024061 | 0.97357 | -0.50892 | 0.97366 | -0.50717 | 2.2033
38 | 0.084653 | 0.021286 | -0.084645 | -0.021281 | 8.2445e-06 | 5.1286e-06 | 0.12919 | 0.12919 | 0.12919 | 0.9752 | -0.47672 | 0.9751 | -0.47876 | 11.8309
39 | 0.083502 | 0.020994 | -0.083483 | -0.020982 | 1.9267e-05 | 1.1976e-05 | 0.12745 | 0.12745 | 0.12745 | 0.9751 | -0.47876 | 0.97485 | -0.4836 | 11.6712
40 | 0.082302 | 0.020686 | -0.082296 | -0.020682 | 6.6647e-06 | 4.1391e-06 | 0.12565 | 0.12565 | 0.12565 | 0.97485 | -0.4836 | 0.97477 | -0.48529 | 11.5062
41 | 0.081149 | 0.020395 | -0.081118 | -0.020375 | 3.127e-05 | 1.9404e-05 | 0.1239 | 0.1239 | 0.1239 | 0.97477 | -0.48529 | 0.97436 | -0.49337 | 11.3459
42 | 0.078774 | 0.019788 | -0.078772 | -0.019787 | 1.7461e-06 | 1.0815e-06 | 0.12032 | 0.12032 | 0.12032 | 0.97436 | -0.49337 | 0.97433 | -0.49383 | 11.0181
43 | 0.0079024 | 0.0019806 | -0.007902 | -0.0019804 | 3.9156e-07 | 1.6209e-07 | 0.012095 | 0.012095 | 0.012095 | 0.97223 | -0.53538 | 0.97218 | -0.53642 | 3.3228
44 | -0.054096 | -0.013558 | 0.054169 | 0.013604 | 7.2803e-05 | 4.6242e-05 | 0.082796 | 0.082795 | 0.082796 | 0.97223 | -0.53538 | 0.97366 | -0.50717 | 22.746
45 | -0.069912 | -0.01755 | 0.069957 | 0.017577 | 4.4506e-05 | 2.732e-05 | 0.10686 | 0.10686 | 0.10686 | 0.97366 | -0.50717 | 0.97433 | -0.49383 | 9.7853
46 | 0.0088153 | 0.0022094 | -0.0088149 | -0.0022092 | 4.1739e-07 | 1.9065e-07 | 0.013463 | 0.013463 | 0.013463 | 0.97433 | -0.49383 | 0.97428 | -0.49483 | 3.6986

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33718 | 0.085936

## res_load
| p_mw | q_mvar
0 | 0.028696 | 0.0071919
1 | 0.0024925 | 0.00062469
2 | 0.0017581 | 0.00044061
3 | 0.0068426 | 0.0017149
4 | 0.00086819 | 0.00021759
5 | 0.015395 | 0.0038584
6 | 0.057003 | 0.014286
7 | 0.0094929 | 0.0023791
8 | 0.0053748 | 0.0013471
9 | 0.024828 | 0.0062225
10 | 0.0023439 | 0.00058744
11 | 0.012657 | 0.0031722
12 | 0.0017699 | 0.00044357
13 | 0.00046767 | 0.00011721
14 | 0.00082614 | 0.00020705
15 | 0.0015308 | 0.00038365
16 | 0.001106 | 0.00027719
17 | 0.0056026 | 0.0014042
18 | 0.0011063 | 0.00027727
19 | 0.0027447 | 0.0006879
20 | 0.00070354 | 0.00017632
21 | 0.0032432 | 0.00081281
22 | 0.001143 | 0.00028645
23 | 0.0011802 | 0.00029579
24 | 0.001147 | 0.00028746
25 | 0.0023436 | 0.00058736
26 | 0.046194 | 0.011577
27 | 0.007902 | 0.0019804
28 | 0.0088149 | 0.0022092
29 | 0.069429 | 0.017401
30 | 0.0056616 | 0.0014189

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1