## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-270_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-270_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-270_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-270_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-270_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-270_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2701-270_0_6_node_45 | 0.4 | n |  | TRUE
7 | bus_LV_2701-270_0_6_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_2701-270_0_6_node_47 | 0.4 | n |  | TRUE
9 | bus_LV_2701-270_0_6_node_43 | 0.4 | n |  | TRUE
10 | bus_LV_2701-270_0_6_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_2701-270_0_6_node_48 | 0.4 | n |  | TRUE
12 | bus_LV_2701-270_0_6_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2701-270_0_6_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2701-270_0_6_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2701-270_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2701-270_0_6_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2701-270_0_6_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_2701-270_0_6_node_82 | 0.4 | n |  | TRUE
19 | bus_LV_2701-270_0_6_node_83 | 0.4 | n |  | TRUE
20 | bus_LV_2701-270_0_6_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_2701-270_0_6_node_84 | 0.4 | n |  | TRUE
22 | bus_LV_2701-270_0_6_node_80 | 0.4 | n |  | TRUE
23 | bus_LV_2701-270_0_6_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2701-270_0_6_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2701-270_0_6_node_49 | 0.4 | n |  | TRUE
26 | bus_LV_2701-270_0_6_node_50 | 0.4 | n |  | TRUE
27 | bus_LV_2701-270_0_6_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_2701-270_0_6_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_2701-270_0_6_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2701-270_0_6_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_2701-270_0_6_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2701-270_0_6_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_2701-270_0_6_node_64 | 0.4 | n |  | TRUE
34 | bus_LV_2701-270_0_6_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_2701-270_0_6_node_40 | 0.4 | n |  | TRUE
36 | bus_LV_2701-270_0_6_node_60 | 0.4 | n |  | TRUE
37 | bus_LV_2701-270_0_6_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_2701-270_0_6_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_2701-270_0_6_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_2701-270_0_6_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_2701-270_0_6_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_2701-270_0_6_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_2701-270_0_6_node_76 | 0.4 | n |  | TRUE
44 | bus_LV_2701-270_0_6_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_2701-270_0_6_node_77 | 0.4 | n |  | TRUE
46 | bus_LV_2701-270_0_6_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_2701-270_0_6_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_2701-270_0_6_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_2701-270_0_6_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_2701-270_0_6_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_2701-270_0_6_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_2701-270_0_6_node_78 | 0.4 | n |  | TRUE
53 | bus_LV_2701-270_0_6_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_2701-270_0_6_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_2701-270_0_6_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_2701-270_0_6_node_66 | 0.4 | n |  | TRUE
57 | bus_LV_2701-270_0_6_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_2701-270_0_6_node_58 | 0.4 | n |  | TRUE
59 | bus_LV_2701-270_0_6_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_2701-270_0_6_node_57 | 0.4 | n |  | TRUE
61 | bus_LV_2701-270_0_6_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_2701-270_0_6_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_2701-270_0_6_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_2701-270_0_6_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_2701-270_0_6_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_2701-270_0_6_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_2701-270_0_6_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_2701-270_0_6_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_2701-270_0_6_node_75 | 0.4 | n |  | TRUE
70 | bus_LV_2701-270_0_6_node_73 | 0.4 | n |  | TRUE
71 | bus_LV_2701-270_0_6_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_2701-270_0_6_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_2701-270_0_6_node_74 | 0.4 | n |  | TRUE
74 | bus_LV_2701-270_0_6_node_71 | 0.4 | n |  | TRUE
75 | bus_LV_2701-270_0_6_node_69 | 0.4 | n |  | TRUE
76 | bus_LV_2701-270_0_6_node_68 | 0.4 | n |  | TRUE
77 | bus_LV_2701-270_0_6_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_2701-270_0_6_node_72 | 0.4 | n |  | TRUE
79 | bus_LV_2701-270_0_6_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_2701-270_0_6_node_79 | 0.4 | n |  | TRUE
81 | bus_MV_570_0_node_36 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-270_0_6_load_0 | 0 | 0.0037502 | 0.00093989 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-270_0_6_load_1 | 1 | 0.0036844 | 0.00092339 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-270_0_6_load_3 | 3 | 0.0036844 | 0.00092339 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-270_0_6_load_4 | 4 | 0.0082212 | 0.0020604 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-270_0_6_load_5 | 5 | 0.011834 | 0.0029659 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-270_0_6_load_45 | 6 | 0.0036882 | 0.00092434 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-270_0_6_load_22 | 7 | 0.012965 | 0.0032494 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-270_0_6_load_47 | 8 | 0.0054977 | 0.0013778 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-270_0_6_load_43 | 9 | 0.0037042 | 0.00092836 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-270_0_6_load_48 | 11 | 0.005491 | 0.0013762 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-270_0_6_load_6 | 12 | 0.0055754 | 0.0013973 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-270_0_6_load_7 | 14 | 0.011846 | 0.0029689 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-270_0_6_load_10 | 15 | 0.0055801 | 0.0013985 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-270_0_6_load_15 | 17 | 0.010941 | 0.0027421 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-270_0_6_load_82 | 18 | 0.0097789 | 0.0024508 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-270_0_6_load_83 | 19 | 0.00286 | 0.00071678 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-270_0_6_load_13 | 20 | 0.020789 | 0.0052101 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-270_0_6_load_84 | 21 | 0.0034185 | 0.00085675 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-270_0_6_load_80 | 22 | 0.0097795 | 0.002451 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-270_0_6_load_14 | 23 | 0.0081109 | 0.0020328 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-270_0_6_load_16 | 24 | 0.0071708 | 0.0017972 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-270_0_6_load_49 | 25 | 0.0064236 | 0.0016099 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-270_0_6_load_50 | 26 | 0.04215 | 0.010564 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-270_0_6_load_17 | 27 | 0.0035148 | 0.00088089 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-270_0_6_load_18 | 28 | 0.0016276 | 0.00040791 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-270_0_6_load_19 | 29 | 0.01041 | 0.0026091 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-270_0_6_load_20 | 30 | 0.0041876 | 0.0010495 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-270_0_6_load_39 | 32 | 0.0068453 | 0.0017156 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-270_0_6_load_64 | 33 | 0.0050641 | 0.0012692 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-270_0_6_load_61 | 34 | 0.0045249 | 0.001134 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-270_0_6_load_40 | 35 | 0.0042994 | 0.0010775 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-270_0_6_load_60 | 36 | 0.0051567 | 0.0012924 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-270_0_6_load_23 | 37 | 0.0058788 | 0.0014734 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-270_0_6_load_24 | 38 | 0.0058958 | 0.0014776 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-270_0_6_load_25 | 39 | 0.013426 | 0.003365 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-270_0_6_load_26 | 40 | 0.0078121 | 0.0019579 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-270_0_6_load_27 | 41 | 0.0078 | 0.0019549 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-270_0_6_load_36 | 42 | 0.0098452 | 0.0024674 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-270_0_6_load_76 | 43 | 0.0048496 | 0.0012154 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-270_0_6_load_34 | 44 | 0.0048384 | 0.0012126 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-270_0_6_load_77 | 45 | 0.011638 | 0.0029168 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2701-270_0_6_load_28 | 46 | 0.012988 | 0.0032551 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2701-270_0_6_load_29 | 47 | 0.005126 | 0.0012847 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2701-270_0_6_load_30 | 48 | 0.0044105 | 0.0011054 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2701-270_0_6_load_31 | 49 | 0.0041133 | 0.0010309 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2701-270_0_6_load_32 | 50 | 0.006414 | 0.0016075 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2701-270_0_6_load_41 | 51 | 0.002739 | 0.00068646 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2701-270_0_6_load_78 | 52 | 0.0028799 | 0.00072178 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2701-270_0_6_load_33 | 53 | 0.0058945 | 0.0014773 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2701-270_0_6_load_37 | 55 | 0.014944 | 0.0037452 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2701-270_0_6_load_66 | 56 | 0.0097949 | 0.0024548 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2701-270_0_6_load_67 | 57 | 0.0062074 | 0.0015557 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2701-270_0_6_load_58 | 58 | 0.0095712 | 0.0023988 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2701-270_0_6_load_56 | 59 | 0.010256 | 0.0025703 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2701-270_0_6_load_57 | 60 | 0.01514 | 0.0037943 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2701-270_0_6_load_42 | 61 | 0.0073926 | 0.0018528 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2701-270_0_6_load_44 | 62 | 0.0048925 | 0.0012262 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2701-270_0_6_load_46 | 63 | 0.0091828 | 0.0023014 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2701-270_0_6_load_51 | 64 | 0.0075646 | 0.0018959 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2701-270_0_6_load_52 | 65 | 0.0074303 | 0.0018622 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2701-270_0_6_load_53 | 66 | 0.0071889 | 0.0018017 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2701-270_0_6_load_54 | 67 | 0.0042868 | 0.0010744 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2701-270_0_6_load_55 | 68 | 0.013459 | 0.0033732 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2701-270_0_6_load_75 | 69 | 0.0042257 | 0.001059 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2701-270_0_6_load_73 | 70 | 0.023335 | 0.0058483 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2701-270_0_6_load_62 | 71 | 0.0021998 | 0.00055132 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2701-270_0_6_load_63 | 72 | 0.0042181 | 0.0010572 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2701-270_0_6_load_74 | 73 | 0.0042117 | 0.0010556 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2701-270_0_6_load_71 | 74 | 0.0048045 | 0.0012041 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2701-270_0_6_load_69 | 75 | 0.0067166 | 0.0016833 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2701-270_0_6_load_68 | 76 | 0.019401 | 0.0048624 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2701-270_0_6_load_70 | 77 | 0.0051471 | 0.00129 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2701-270_0_6_load_72 | 78 | 0.0078398 | 0.0019648 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2701-270_0_6_load_81 | 79 | 0.0097964 | 0.0024552 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2701-270_0_6_load_79 | 80 | 0.002866 | 0.0007183 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 52 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-270_0_6_line_0 |  | 0 | 1 | 0.0072208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2701-270_0_6_line_1 |  | 0 | 2 | 0.022779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2701-270_0_6_line_2 |  | 1 | 3 | 0.0069997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2701-270_0_6_line_3 |  | 2 | 4 | 0.015079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2701-270_0_6_line_4 |  | 2 | 5 | 0.020283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-270_0_6_line_5 |  | 3 | 6 | 0.0070017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2701-270_0_6_line_6 |  | 4 | 7 | 0.011756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2701-270_0_6_line_7 |  | 5 | 8 | 0.018141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-270_0_6_line_8 |  | 6 | 9 | 0.0070209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_2701-270_0_6_line_9 |  | 7 | 10 | 0.0034521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2701-270_0_6_line_10 |  | 8 | 11 | 0.018003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-270_0_6_line_11 |  | 9 | 61 | 0.0085544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_2701-270_0_6_line_12 |  | 10 | 17 | 0.010535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2701-270_0_6_line_13 |  | 10 | 14 | 0.016723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-270_0_6_line_14 |  | 11 | 15 | 0.018136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-270_0_6_line_15 |  | 12 | 13 | 0.02326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-270_0_6_line_16 |  | 13 | 15 | 0.017518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-270_0_6_line_17 |  | 13 | 16 | 0.0633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-270_0_6_line_18 |  | 16 | 18 | 0.0018593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-270_0_6_line_19 |  | 16 | 19 | 0.017256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-270_0_6_line_20 |  | 17 | 20 | 0.0061894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2701-270_0_6_line_21 |  | 18 | 22 | 0.017251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-270_0_6_line_22 |  | 19 | 21 | 0.0006422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-270_0_6_line_23 |  | 20 | 23 | 0.0060773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2701-270_0_6_line_24 |  | 22 | 80 | 0.0018617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-270_0_6_line_25 |  | 23 | 24 | 0.008444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2701-270_0_6_line_26 |  | 24 | 25 | 0.0030759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2701-270_0_6_line_27 |  | 25 | 26 | 0.0033826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2701-270_0_6_line_28 |  | 26 | 52 | 0.012881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2701-270_0_6_line_29 |  | 27 | 28 | 0.0030506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-270_0_6_line_30 |  | 27 | 29 | 0.010972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-270_0_6_line_31 |  | 28 | 30 | 0.0066571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-270_0_6_line_32 |  | 29 | 31 | 0.010041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-270_0_6_line_33 |  | 30 | 32 | 4.214e-07 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-270_0_6_line_34 |  | 31 | 33 | 0.018083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-270_0_6_line_35 |  | 31 | 34 | 0.015911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-270_0_6_line_36 |  | 32 | 35 | 0.0067623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_2701-270_0_6_line_37 |  | 34 | 36 | 0.00039575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-270_0_6_line_38 |  | 35 | 51 | 0.0021445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2701-270_0_6_line_39 |  | 36 | 71 | 0.011897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2701-270_0_6_line_40 |  | 37 | 38 | 0.018932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2701-270_0_6_line_41 |  | 37 | 39 | 0.0050382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-270_0_6_line_42 |  | 38 | 40 | 0.0068337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-270_0_6_line_43 |  | 39 | 41 | 0.0072369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-270_0_6_line_44 |  | 40 | 42 | 0.0045445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2701-270_0_6_line_45 |  | 41 | 43 | 0.004969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2701-270_0_6_line_46 |  | 42 | 44 | 0.0058744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2701-270_0_6_line_47 |  | 43 | 45 | 0.017257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2701-270_0_6_line_48 |  | 44 | 53 | 0.017261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2701-270_0_6_line_49 |  | 45 | 58 | 0.017259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2701-270_0_6_line_50 |  | 46 | 47 | 0.0029362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_2701-270_0_6_line_51 |  | 46 | 48 | 0.0055925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_2701-270_0_6_line_52 |  | 47 | 49 | 0.0020698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_2701-270_0_6_line_53 |  | 48 | 50 | 0.0076343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_2701-270_0_6_line_54 |  | 49 | 51 | 0.0094489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_2701-270_0_6_line_55 |  | 50 | 52 | 0.0016655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_2701-270_0_6_line_56 |  | 53 | 54 | 0.034528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2701-270_0_6_line_57 |  | 54 | 55 | 0.034714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2701-270_0_6_line_58 |  | 55 | 56 | 0.00012608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2701-270_0_6_line_59 |  | 56 | 57 | 0.020961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2701-270_0_6_line_60 |  | 57 | 63 | 0.014229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2701-270_0_6_line_61 |  | 59 | 60 | 0.016597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2701-270_0_6_line_62 |  | 60 | 68 | 0.017494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2701-270_0_6_line_63 |  | 61 | 62 | 0.011193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2701-270_0_6_line_64 |  | 62 | 63 | 0.000202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2701-270_0_6_line_65 |  | 64 | 65 | 0.0019483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2701-270_0_6_line_66 |  | 64 | 66 | 0.0082871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2701-270_0_6_line_67 |  | 65 | 67 | 0.0065548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2701-270_0_6_line_68 |  | 66 | 68 | 0.0027736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2701-270_0_6_line_69 |  | 67 | 69 | 0.0065002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2701-270_0_6_line_70 |  | 69 | 70 | 0.0055432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2701-270_0_6_line_71 |  | 70 | 73 | 0.00095803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2701-270_0_6_line_72 |  | 71 | 72 | 0.0065022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2701-270_0_6_line_73 |  | 72 | 73 | 0.0065046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2701-270_0_6_line_74 |  | 74 | 75 | 0.021851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2701-270_0_6_line_75 |  | 75 | 76 | 0.015891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2701-270_0_6_line_76 |  | 76 | 77 | 0.0035431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2701-270_0_6_line_77 |  | 77 | 78 | 0.015334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2701-270_0_6_line_78 |  | 78 | 79 | 0.016185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2701-270_0_6_line_79 |  | 79 | 80 | 0.016141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-270_0_6_trafo_78 | 0.63 MVA 20/0.4 kV | 81 | 52 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2611455.9274 | 1269971.9065 | 2611449.1433 | 1269974.3797
1 | 2611477.3294 | 1269964.108 | 2611476.7121 | 1269964.3292 | 2611455.9274 | 1269971.9065
2 | 2611449.1433 | 1269974.3797 | 2611442.567 | 1269976.7771
3 | 2611477.3294 | 1269964.108 | 2611472.2515 | 1269949.9098
4 | 2611477.3294 | 1269964.108 | 2611496.2734 | 1269956.8609
5 | 2611435.9888 | 1269979.1753 | 2611442.567 | 1269976.7771
6 | 2611468.2927 | 1269938.8408 | 2611472.2515 | 1269949.9098
7 | 2611496.2734 | 1269956.8609 | 2611513.2173 | 1269950.379
8 | 2611435.9888 | 1269979.1753 | 2611429.3925 | 1269981.58
9 | 2611467.1301 | 1269935.5903 | 2611468.2927 | 1269938.8408
10 | 2611513.2173 | 1269950.379 | 2611530.0321 | 1269943.9465
11 | 2611421.3555 | 1269984.51 | 2611429.3925 | 1269981.58
12 | 2611467.1301 | 1269935.5903 | 2611463.5835 | 1269925.6706
13 | 2611467.1301 | 1269935.5903 | 2611482.7363 | 1269929.5823
14 | 2611530.0321 | 1269943.9465 | 2611546.9711 | 1269937.4664
15 | 2611563.3332 | 1269931.207 | 2611553.3945 | 1269915.8768 | 2611550.6791 | 1269911.6908
16 | 2611563.3332 | 1269931.207 | 2611546.9711 | 1269937.4664
17 | 2611563.3332 | 1269931.207 | 2611582.9012 | 1269923.7176 | 2611572.1096 | 1269882.7676
18 | 2611572.1096 | 1269882.7676 | 2611571.5888 | 1269880.9827
19 | 2611572.1096 | 1269882.7676 | 2611573.9991 | 1269882.2153 | 2611588.6855 | 1269877.9717
20 | 2611461.4998 | 1269919.8425 | 2611463.5835 | 1269925.6706
21 | 2611567.2764 | 1269864.2832 | 2611570.2039 | 1269876.237 | 2611571.5888 | 1269880.9827
22 | 2611589.3024 | 1269877.7934 | 2611588.6855 | 1269877.9717
23 | 2611461.4998 | 1269919.8425 | 2611459.4538 | 1269914.1199
24 | 2611566.8335 | 1269862.475 | 2611567.2764 | 1269864.2832
25 | 2611456.6111 | 1269906.1688 | 2611459.4538 | 1269914.1199
26 | 2611456.6111 | 1269906.1688 | 2611455.5755 | 1269903.2724
27 | 2611454.4367 | 1269900.0872 | 2611455.5755 | 1269903.2724
28 | 2611454.4367 | 1269900.0872 | 2611451.528 | 1269891.9515 | 2611450.0789 | 1269887.9662
29 | 2611434.732 | 1269845.758 | 2611433.6896 | 1269842.8911
30 | 2611429.9405 | 1269832.5799 | 2611433.6896 | 1269842.8911
31 | 2611434.732 | 1269845.758 | 2611437.0069 | 1269852.0144
32 | 2611426.5094 | 1269823.1435 | 2611429.9405 | 1269832.5799
33 | 2611437.0069 | 1269852.0144 | 2611437.007 | 1269852.0148
34 | 2611426.5094 | 1269823.1435 | 2611424.4896 | 1269817.1465 | 2611420.5016 | 1269806.0892
35 | 2611426.5094 | 1269823.1435 | 2611425.8996 | 1269823.3425 | 2611411.3426 | 1269827.9528
36 | 2611437.007 | 1269852.0148 | 2611439.3178 | 1269858.3701
37 | 2611410.9653 | 1269828.0723 | 2611411.3426 | 1269827.9528
38 | 2611439.3178 | 1269858.3701 | 2611440.0506 | 1269860.3855
39 | 2611410.9653 | 1269828.0723 | 2611399.6231 | 1269831.6645
40 | 2611313.608 | 1269930.3614 | 2611320.0497 | 1269948.164
41 | 2611311.8937 | 1269925.6238 | 2611313.608 | 1269930.3614
42 | 2611322.375 | 1269954.5899 | 2611320.0497 | 1269948.164
43 | 2611309.4313 | 1269918.8186 | 2611311.8937 | 1269925.6238
44 | 2611322.375 | 1269954.5899 | 2611323.9212 | 1269958.8633
45 | 2611309.4313 | 1269918.8186 | 2611307.7406 | 1269914.1461
46 | 2611323.9212 | 1269958.8633 | 2611325.92 | 1269964.3872
47 | 2611301.8688 | 1269897.9187 | 2611307.7406 | 1269914.1461
48 | 2611325.92 | 1269964.3872 | 2611331.7931 | 1269980.618
49 | 2611301.8688 | 1269897.9187 | 2611295.9962 | 1269881.6891
50 | 2611443.9867 | 1269871.2108 | 2611444.99 | 1269873.9703
51 | 2611446.901 | 1269879.2262 | 2611444.99 | 1269873.9703
52 | 2611443.2794 | 1269869.2656 | 2611443.9867 | 1269871.2108
53 | 2611446.901 | 1269879.2262 | 2611449.5098 | 1269886.4009
54 | 2611443.2794 | 1269869.2656 | 2611440.0506 | 1269860.3855
55 | 2611450.0789 | 1269887.9662 | 2611449.5098 | 1269886.4009
56 | 2611344.8556 | 1270012.3989 | 2611343.5158 | 1270008.8049 | 2611342.8347 | 1270006.98 | 2611339.8332 | 1270002.838 | 2611331.7931 | 1269980.618
57 | 2611344.8556 | 1270012.3989 | 2611377.4698 | 1270000.509
58 | 2611377.4698 | 1270000.509 | 2611377.5882 | 1270000.4658
59 | 2611377.5882 | 1270000.4658 | 2611397.2815 | 1269993.2864
60 | 2611410.6498 | 1269988.4129 | 2611397.2815 | 1269993.2864
61 | 2611323.6781 | 1269855.7168 | 2611339.5 | 1269850.7059
62 | 2611339.5 | 1269850.7059 | 2611356.178 | 1269845.4239
63 | 2611421.3555 | 1269984.51 | 2611410.8395 | 1269988.3437
64 | 2611410.6498 | 1269988.4129 | 2611410.8395 | 1269988.3437
65 | 2611366.7225 | 1269842.0843 | 2611368.5799 | 1269841.4961
66 | 2611366.7225 | 1269842.0843 | 2611358.8221 | 1269844.5864
67 | 2611374.8288 | 1269839.517 | 2611368.5799 | 1269841.4961
68 | 2611356.178 | 1269845.4239 | 2611358.8221 | 1269844.5864
69 | 2611374.8288 | 1269839.517 | 2611381.0256 | 1269837.5544
70 | 2611386.3101 | 1269835.8808 | 2611381.0256 | 1269837.5544
71 | 2611386.3101 | 1269835.8808 | 2611387.2234 | 1269835.5915
72 | 2611393.4244 | 1269833.6276 | 2611399.6231 | 1269831.6645
73 | 2611387.2234 | 1269835.5915 | 2611393.4244 | 1269833.6276
74 | 2611550.8739 | 1269797.3073 | 2611545.6761 | 1269776.0831
75 | 2611554.654 | 1269812.7423 | 2611550.8739 | 1269797.3073
76 | 2611554.654 | 1269812.7423 | 2611555.4968 | 1269816.1837
77 | 2611559.1442 | 1269831.0774 | 2611555.4968 | 1269816.1837
78 | 2611559.1442 | 1269831.0774 | 2611562.9941 | 1269846.7974
79 | 2611566.8335 | 1269862.475 | 2611562.9941 | 1269846.7974

## bus_geodata
| x | y | coords
0 | 2611455.9274 | 1269971.9065
1 | 2611449.1433 | 1269974.3797
2 | 2611477.3294 | 1269964.108
3 | 2611442.567 | 1269976.7771
4 | 2611472.2515 | 1269949.9098
5 | 2611496.2734 | 1269956.8609
6 | 2611435.9888 | 1269979.1753
7 | 2611468.2927 | 1269938.8408
8 | 2611513.2173 | 1269950.379
9 | 2611429.3925 | 1269981.58
10 | 2611467.1301 | 1269935.5903
11 | 2611530.0321 | 1269943.9465
12 | 2611550.6791 | 1269911.6908
13 | 2611563.3332 | 1269931.207
14 | 2611482.7363 | 1269929.5823
15 | 2611546.9711 | 1269937.4664
16 | 2611572.1096 | 1269882.7676
17 | 2611463.5835 | 1269925.6706
18 | 2611571.5888 | 1269880.9827
19 | 2611588.6855 | 1269877.9717
20 | 2611461.4998 | 1269919.8425
21 | 2611589.3024 | 1269877.7934
22 | 2611567.2764 | 1269864.2832
23 | 2611459.4538 | 1269914.1199
24 | 2611456.6111 | 1269906.1688
25 | 2611455.5755 | 1269903.2724
26 | 2611454.4367 | 1269900.0872
27 | 2611433.6896 | 1269842.8911
28 | 2611434.732 | 1269845.758
29 | 2611429.9405 | 1269832.5799
30 | 2611437.0069 | 1269852.0144
31 | 2611426.5094 | 1269823.1435
32 | 2611437.007 | 1269852.0148
33 | 2611420.5016 | 1269806.0892
34 | 2611411.3426 | 1269827.9528
35 | 2611439.3178 | 1269858.3701
36 | 2611410.9653 | 1269828.0723
37 | 2611313.608 | 1269930.3614
38 | 2611320.0497 | 1269948.164
39 | 2611311.8937 | 1269925.6238
40 | 2611322.375 | 1269954.5899
41 | 2611309.4313 | 1269918.8186
42 | 2611323.9212 | 1269958.8633
43 | 2611307.7406 | 1269914.1461
44 | 2611325.92 | 1269964.3872
45 | 2611301.8688 | 1269897.9187
46 | 2611444.99 | 1269873.9703
47 | 2611443.9867 | 1269871.2108
48 | 2611446.901 | 1269879.2262
49 | 2611443.2794 | 1269869.2656
50 | 2611449.5098 | 1269886.4009
51 | 2611440.0506 | 1269860.3855
52 | 2611450.0789 | 1269887.9662
53 | 2611331.7931 | 1269980.618
54 | 2611344.8556 | 1270012.3989
55 | 2611377.4698 | 1270000.509
56 | 2611377.5882 | 1270000.4658
57 | 2611397.2815 | 1269993.2864
58 | 2611295.9962 | 1269881.6891
59 | 2611323.6781 | 1269855.7168
60 | 2611339.5 | 1269850.7059
61 | 2611421.3555 | 1269984.51
62 | 2611410.8395 | 1269988.3437
63 | 2611410.6498 | 1269988.4129
64 | 2611366.7225 | 1269842.0843
65 | 2611368.5799 | 1269841.4961
66 | 2611358.8221 | 1269844.5864
67 | 2611374.8288 | 1269839.517
68 | 2611356.178 | 1269845.4239
69 | 2611381.0256 | 1269837.5544
70 | 2611386.3101 | 1269835.8808
71 | 2611399.6231 | 1269831.6645
72 | 2611393.4244 | 1269833.6276
73 | 2611387.2234 | 1269835.5915
74 | 2611545.6761 | 1269776.0831
75 | 2611550.8739 | 1269797.3073
76 | 2611554.654 | 1269812.7423
77 | 2611555.4968 | 1269816.1837
78 | 2611559.1442 | 1269831.0774
79 | 2611562.9941 | 1269846.7974
80 | 2611566.8335 | 1269862.475
81 | 2611467.1301 | 1269935.5903

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99081 | -0.17488 | 0.0037502 | 0.00093989
1 | 0.99047 | -0.18149 | 0.0036844 | 0.00092339
2 | 0.99192 | -0.15355 | 0 | 0
3 | 0.99014 | -0.18775 | 0.0036844 | 0.00092339
4 | 0.9932 | -0.12912 | 0.0082212 | 0.0020604
5 | 0.98974 | -0.19547 | 0.011834 | 0.0029659
6 | 0.98982 | -0.19386 | 0.0036882 | 0.00092434
7 | 0.99423 | -0.10954 | 0.012965 | 0.0032494
8 | 0.98798 | -0.22928 | 0.0054977 | 0.0013778
9 | 0.98951 | -0.19984 | 0.0037042 | 0.00092836
10 | 0.99454 | -0.10354 | 0 | 0
11 | 0.98632 | -0.26118 | 0.005491 | 0.0013762
12 | 0.98319 | -0.32171 | 0.0055754 | 0.0013973
13 | 0.98331 | -0.31938 | 0 | 0
14 | 0.99436 | -0.10703 | 0.011846 | 0.0029689
15 | 0.98474 | -0.29163 | 0.0055801 | 0.0013985
16 | 0.97847 | -0.41388 | 0 | 0
17 | 0.99554 | -0.084513 | 0.010941 | 0.0027421
18 | 0.97833 | -0.41646 | 0.0097789 | 0.0024508
19 | 0.97837 | -0.41585 | 0.00286 | 0.00071678
20 | 0.99615 | -0.072955 | 0.020789 | 0.0052101
21 | 0.97836 | -0.41589 | 0.0034185 | 0.00085675
22 | 0.97727 | -0.43733 | 0.0097795 | 0.002451
23 | 0.99679 | -0.060881 | 0.0081109 | 0.0020328
24 | 0.99769 | -0.04373 | 0.0071708 | 0.0017972
25 | 0.99803 | -0.037362 | 0.0064236 | 0.0016099
26 | 0.9984 | -0.030237 | 0.04215 | 0.010564
27 | 0.99678 | -0.061477 | 0.0035148 | 0.00088089
28 | 0.99715 | -0.054406 | 0.0016276 | 0.00040791
29 | 0.99549 | -0.086275 | 0.01041 | 0.0026091
30 | 0.99797 | -0.038803 | 0.0041876 | 0.0010495
31 | 0.9944 | -0.10718 | 0 | 0
32 | 0.99797 | -0.038802 | 0.0068453 | 0.0017156
33 | 0.99432 | -0.1088 | 0.0050641 | 0.0012692
34 | 0.99275 | -0.13898 | 0.0045249 | 0.001134
35 | 0.99842 | -0.030235 | 0.0042994 | 0.0010775
36 | 0.99271 | -0.13974 | 0.0051567 | 0.0012924
37 | 0.97484 | -0.48504 | 0.0058788 | 0.0014734
38 | 0.97578 | -0.4666 | 0.0058958 | 0.0014776
39 | 0.97462 | -0.48941 | 0.013426 | 0.003365
40 | 0.97615 | -0.45921 | 0.0078121 | 0.0019579
41 | 0.97439 | -0.49391 | 0.0078 | 0.0019549
42 | 0.97643 | -0.45366 | 0.0098452 | 0.0024674
43 | 0.97427 | -0.49629 | 0.0048496 | 0.0012154
44 | 0.97685 | -0.44542 | 0.0048384 | 0.0012126
45 | 0.97393 | -0.50301 | 0.011638 | 0.0029168
46 | 0.99919 | -0.015378 | 0.012988 | 0.0032551
47 | 0.99905 | -0.018131 | 0.005126 | 0.0012847
48 | 0.99949 | -0.0097131 | 0.0044105 | 0.0011054
49 | 0.99895 | -0.020011 | 0.0041133 | 0.0010309
50 | 0.99991 | -0.0017898 | 0.006414 | 0.0016075
51 | 0.99851 | -0.028371 | 0.002739 | 0.00068646
52 | 1 | 0 | -0.59674 | -0.15177
53 | 0.97816 | -0.41974 | 0.0058945 | 0.0014773
54 | 0.98097 | -0.36489 | 0 | 0
55 | 0.9838 | -0.31007 | 0.014944 | 0.0037452
56 | 0.98381 | -0.30983 | 0.0097949 | 0.0024548
57 | 0.98599 | -0.26758 | 0.0062074 | 0.0015557
58 | 0.97378 | -0.50605 | 0.0095712 | 0.0023988
59 | 0.9881 | -0.22911 | 0.010256 | 0.0025703
60 | 0.98826 | -0.22608 | 0.01514 | 0.0037943
61 | 0.98895 | -0.2105 | 0.0073926 | 0.0018528
62 | 0.98758 | -0.23696 | 0.0048925 | 0.0012262
63 | 0.98756 | -0.23742 | 0.0091828 | 0.0023014
64 | 0.98911 | -0.20943 | 0.0075646 | 0.0018959
65 | 0.98921 | -0.20757 | 0.0074303 | 0.0018622
66 | 0.98876 | -0.21623 | 0.0071889 | 0.0018017
67 | 0.98957 | -0.20044 | 0.0042868 | 0.0010744
68 | 0.98866 | -0.21815 | 0.013459 | 0.0033732
69 | 0.98996 | -0.19289 | 0.0042257 | 0.001059
70 | 0.99032 | -0.18603 | 0.023335 | 0.0058483
71 | 0.99158 | -0.16155 | 0.0021998 | 0.00055132
72 | 0.99098 | -0.17324 | 0.0042181 | 0.0010572
73 | 0.9904 | -0.18445 | 0.0042117 | 0.0010556
74 | 0.97482 | -0.48551 | 0.0048045 | 0.0012041
75 | 0.97492 | -0.48358 | 0.0067166 | 0.0016833
76 | 0.97509 | -0.48023 | 0.019401 | 0.0048624
77 | 0.97519 | -0.47822 | 0.0051471 | 0.00129
78 | 0.97571 | -0.46809 | 0.0078398 | 0.0019648
79 | 0.97637 | -0.45508 | 0.0097964 | 0.0024552
80 | 0.97717 | -0.43925 | 0.002866 | 0.0007183
81 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.15616 | 0.039732 | -0.15611 | -0.039701 | 4.9736e-05 | 3.1552e-05 | 0.23474 | 0.23474 | 0.23474 | 0.99081 | -0.17488 | 0.99047 | -0.18149 | 21.4963
1 | -0.15991 | -0.040672 | 0.16008 | 0.040777 | 0.00016451 | 0.00010441 | 0.24037 | 0.24037 | 0.24037 | 0.99081 | -0.17488 | 0.99192 | -0.15355 | 22.012
2 | 0.15243 | 0.038778 | -0.15238 | -0.038748 | 4.5966e-05 | 2.9148e-05 | 0.2292 | 0.2292 | 0.2292 | 0.99047 | -0.18149 | 0.99014 | -0.18775 | 20.9894
3 | -0.27783 | -0.070817 | 0.27816 | 0.071026 | 0.00032808 | 0.00020939 | 0.41721 | 0.41721 | 0.41721 | 0.99192 | -0.15355 | 0.9932 | -0.12912 | 38.2056
4 | 0.11775 | 0.03004 | -0.11752 | -0.029888 | 0.00023785 | 0.00015196 | 0.17683 | 0.17683 | 0.17683 | 0.99192 | -0.15355 | 0.98974 | -0.19547 | 48.5809
5 | 0.1487 | 0.037825 | -0.14865 | -0.037797 | 4.3784e-05 | 2.7752e-05 | 0.22367 | 0.22367 | 0.22367 | 0.99014 | -0.18775 | 0.98982 | -0.19386 | 20.4824
6 | -0.28638 | -0.073087 | 0.28665 | 0.07326 | 0.0002711 | 0.00017305 | 0.42952 | 0.42952 | 0.42952 | 0.9932 | -0.12912 | 0.99423 | -0.10954 | 39.3335
7 | 0.10568 | 0.026922 | -0.10551 | -0.026812 | 0.00017208 | 0.0001099 | 0.15904 | 0.15904 | 0.15904 | 0.98974 | -0.19547 | 0.98798 | -0.22928 | 43.693
8 | 0.14497 | 0.036873 | -0.14492 | -0.036846 | 4.1755e-05 | 2.6452e-05 | 0.21812 | 0.21812 | 0.21812 | 0.98982 | -0.19386 | 0.98951 | -0.19984 | 19.9747
9 | -0.29962 | -0.076509 | 0.2997 | 0.076565 | 8.6966e-05 | 5.5524e-05 | 0.44893 | 0.44893 | 0.44893 | 0.99423 | -0.10954 | 0.99454 | -0.10354 | 41.1105
10 | 0.10001 | 0.025434 | -0.099858 | -0.025336 | 0.00015345 | 9.7978e-05 | 0.15076 | 0.15076 | 0.15076 | 0.98798 | -0.22928 | 0.98632 | -0.26118 | 41.4183
11 | 0.14122 | 0.035918 | -0.14115 | -0.035872 | 7.2465e-05 | 4.6158e-05 | 0.21255 | 0.21255 | 0.21255 | 0.98951 | -0.19984 | 0.98895 | -0.2105 | 29.1968
12 | -0.31155 | -0.079534 | 0.31184 | 0.079718 | 0.00028676 | 0.00018312 | 0.46665 | 0.46665 | 0.46665 | 0.99454 | -0.10354 | 0.99554 | -0.084513 | 42.7338
13 | 0.011848 | 0.0029699 | -0.011846 | -0.0029689 | 1.9706e-06 | 1.0442e-06 | 0.017727 | 0.017727 | 0.017727 | 0.99454 | -0.10354 | 0.99436 | -0.10703 | 4.87
14 | 0.094367 | 0.02396 | -0.094229 | -0.023872 | 0.00013806 | 8.8129e-05 | 0.14248 | 0.14248 | 0.14248 | 0.98632 | -0.26118 | 0.98474 | -0.29163 | 39.1425
15 | -0.0055754 | -0.0013973 | 0.005576 | 0.0013974 | 6.2103e-07 | 1.0245e-07 | 0.0084381 | 0.008438 | 0.0084381 | 0.98319 | -0.32171 | 0.98331 | -0.31938 | 2.3181
16 | -0.088531 | -0.022398 | 0.088649 | 0.022474 | 0.00011804 | 7.5325e-05 | 0.13405 | 0.13405 | 0.13405 | 0.98331 | -0.31938 | 0.98474 | -0.29163 | 36.826
17 | 0.082955 | 0.021001 | -0.082581 | -0.020762 | 0.00037452 | 0.0002389 | 0.12561 | 0.12561 | 0.12561 | 0.98331 | -0.31938 | 0.97847 | -0.41388 | 34.508
18 | 0.076302 | 0.019188 | -0.076292 | -0.019182 | 9.392e-06 | 5.9875e-06 | 0.11606 | 0.11606 | 0.11606 | 0.97847 | -0.41388 | 0.97833 | -0.41646 | 31.8847
19 | 0.0062791 | 0.0015737 | -0.0062785 | -0.0015735 | 5.9004e-07 | 1.6091e-07 | 0.009549 | 0.0095491 | 0.0095491 | 0.97847 | -0.41388 | 0.97837 | -0.41585 | 2.6234
20 | -0.32278 | -0.08246 | 0.32296 | 0.082575 | 0.00018049 | 0.00011527 | 0.48301 | 0.48301 | 0.48301 | 0.99554 | -0.084513 | 0.99615 | -0.072955 | 44.2313
21 | 0.066513 | 0.016732 | -0.066447 | -0.016689 | 6.6235e-05 | 4.2174e-05 | 0.10119 | 0.10119 | 0.10119 | 0.97833 | -0.41646 | 0.97727 | -0.43733 | 27.7986
22 | 0.0034185 | 0.00085675 | -0.0034185 | -0.00085675 | 6.5101e-09 | -3.8982e-09 | 0.0051992 | 0.0051992 | 0.0051992 | 0.97837 | -0.41585 | 0.97836 | -0.41589 | 1.4284
23 | -0.34375 | -0.087785 | 0.34395 | 0.087913 | 0.00020075 | 0.00012824 | 0.51406 | 0.51406 | 0.51406 | 0.99615 | -0.072955 | 0.99679 | -0.060881 | 47.075
24 | 0.056668 | 0.014238 | -0.056662 | -0.014235 | 5.199e-06 | 3.304e-06 | 0.086296 | 0.086296 | 0.086296 | 0.97727 | -0.43733 | 0.97717 | -0.43925 | 23.7078
25 | -0.35206 | -0.089946 | 0.35235 | 0.090133 | 0.00029222 | 0.00018669 | 0.52617 | 0.52617 | 0.52617 | 0.99679 | -0.060881 | 0.99769 | -0.04373 | 48.1837
26 | -0.35952 | -0.09193 | 0.35963 | 0.092001 | 0.00011082 | 7.0802e-05 | 0.53686 | 0.53686 | 0.53686 | 0.99769 | -0.04373 | 0.99803 | -0.037362 | 49.1631
27 | -0.36606 | -0.093611 | 0.36618 | 0.093691 | 0.00012626 | 8.0671e-05 | 0.54644 | 0.54644 | 0.54644 | 0.99803 | -0.037362 | 0.9984 | -0.030237 | 50.0401
28 | -0.40833 | -0.10426 | 0.40893 | 0.10464 | 0.00059766 | 0.00038199 | 0.60926 | 0.60926 | 0.60926 | 0.9984 | -0.030237 | 1 | 0 | 55.7928
29 | -0.13296 | -0.033623 | 0.13301 | 0.033652 | 4.5118e-05 | 2.8836e-05 | 0.19859 | 0.19859 | 0.19859 | 0.99678 | -0.061477 | 0.99715 | -0.054406 | 54.5587
30 | 0.12945 | 0.032742 | -0.12929 | -0.032644 | 0.00015381 | 9.8293e-05 | 0.19335 | 0.19335 | 0.19335 | 0.99678 | -0.061477 | 0.99549 | -0.086275 | 53.1172
31 | -0.13463 | -0.03406 | 0.13474 | 0.034124 | 0.00010088 | 6.4476e-05 | 0.20102 | 0.20102 | 0.20102 | 0.99715 | -0.054406 | 0.99797 | -0.038803 | 55.2259
32 | 0.11888 | 0.030035 | -0.11876 | -0.029959 | 0.00011901 | 7.6038e-05 | 0.17779 | 0.17779 | 0.17779 | 0.99549 | -0.086275 | 0.9944 | -0.10718 | 48.8423
33 | -0.13892 | -0.035174 | 0.13892 | 0.035174 | 6.7886e-09 | 4.3447e-09 | 0.20727 | 0.20727 | 0.20727 | 0.99797 | -0.038803 | 0.99797 | -0.038802 | 56.9413
34 | 0.0050644 | 0.0012692 | -0.0050641 | -0.0012692 | 3.8945e-07 | 1.4684e-08 | 0.0075784 | 0.0075785 | 0.0075785 | 0.9944 | -0.10718 | 0.99432 | -0.1088 | 2.082
35 | 0.1137 | 0.02869 | -0.11353 | -0.028579 | 0.00017286 | 0.00011042 | 0.17021 | 0.17021 | 0.17021 | 0.9944 | -0.10718 | 0.99275 | -0.13898 | 46.7603
36 | -0.14577 | -0.03689 | 0.14583 | 0.036928 | 5.9966e-05 | 3.8202e-05 | 0.21747 | 0.21747 | 0.21747 | 0.99797 | -0.038802 | 0.99842 | -0.030235 | 29.8726
37 | 0.109 | 0.027445 | -0.109 | -0.027443 | 3.9636e-06 | 2.5316e-06 | 0.16343 | 0.16343 | 0.16343 | 0.99275 | -0.13898 | 0.99271 | -0.13974 | 44.8971
38 | -0.15013 | -0.038005 | 0.15014 | 0.038014 | 1.3436e-05 | 8.5148e-06 | 0.22388 | 0.22388 | 0.22388 | 0.99842 | -0.030235 | 0.99851 | -0.028371 | 20.5019
39 | 0.10384 | 0.02615 | -0.10373 | -0.026081 | 0.00010815 | 6.9065e-05 | 0.1557 | 0.1557 | 0.1557 | 0.99271 | -0.13974 | 0.99158 | -0.16155 | 42.7736
40 | -0.053192 | -0.013342 | 0.053239 | 0.013371 | 4.6808e-05 | 2.9721e-05 | 0.081198 | 0.081198 | 0.081198 | 0.97484 | -0.48504 | 0.97578 | -0.4666 | 22.307
41 | 0.047314 | 0.011868 | -0.047304 | -0.011862 | 9.8553e-06 | 6.2446e-06 | 0.072224 | 0.072224 | 0.072224 | 0.97484 | -0.48504 | 0.97462 | -0.48941 | 19.8418
42 | -0.059135 | -0.014849 | 0.059156 | 0.014862 | 2.0844e-05 | 1.3255e-05 | 0.090188 | 0.090188 | 0.090188 | 0.97578 | -0.4666 | 0.97615 | -0.45921 | 24.777
43 | 0.033877 | 0.008497 | -0.03387 | -0.0084925 | 7.2609e-06 | 4.5568e-06 | 0.051725 | 0.051725 | 0.051725 | 0.97462 | -0.48941 | 0.97439 | -0.49391 | 14.2102
44 | -0.066968 | -0.01682 | 0.066986 | 0.016831 | 1.7764e-05 | 1.1312e-05 | 0.1021 | 0.1021 | 0.1021 | 0.97615 | -0.45921 | 0.97643 | -0.45366 | 28.0486
45 | 0.02607 | 0.0065376 | -0.026067 | -0.0065358 | 2.9537e-06 | 1.8285e-06 | 0.039814 | 0.039814 | 0.039814 | 0.97439 | -0.49391 | 0.97427 | -0.49629 | 10.9378
46 | -0.076831 | -0.019299 | 0.076861 | 0.019318 | 3.0207e-05 | 1.9259e-05 | 0.1171 | 0.1171 | 0.1171 | 0.97643 | -0.45366 | 0.97685 | -0.44542 | 32.1704
47 | 0.021217 | 0.0053203 | -0.021211 | -0.0053162 | 6.7962e-06 | 4.1348e-06 | 0.032407 | 0.032407 | 0.032407 | 0.97427 | -0.49629 | 0.97393 | -0.50301 | 8.9029
48 | -0.081699 | -0.020531 | 0.0818 | 0.020595 | 0.00010028 | 6.3964e-05 | 0.12447 | 0.12447 | 0.12447 | 0.97685 | -0.44542 | 0.97816 | -0.41974 | 34.1952
49 | 0.0095726 | 0.0023994 | -0.0095712 | -0.0023988 | 1.3845e-06 | 6.7132e-07 | 0.014626 | 0.014626 | 0.014626 | 0.97393 | -0.50301 | 0.97378 | -0.50605 | 4.018
50 | 0.16222 | 0.041077 | -0.16219 | -0.041064 | 2.1445e-05 | 1.361e-05 | 0.24172 | 0.24172 | 0.24172 | 0.99919 | -0.015378 | 0.99905 | -0.018131 | 22.1359
51 | -0.1752 | -0.044333 | 0.17525 | 0.044363 | 4.7645e-05 | 3.0273e-05 | 0.26107 | 0.26107 | 0.26107 | 0.99919 | -0.015378 | 0.99949 | -0.0097131 | 23.9071
52 | 0.15707 | 0.039779 | -0.15705 | -0.03977 | 1.4178e-05 | 8.9923e-06 | 0.23409 | 0.23409 | 0.23409 | 0.99905 | -0.018131 | 0.99895 | -0.020011 | 21.4367
53 | -0.17966 | -0.045468 | 0.17973 | 0.045512 | 6.8352e-05 | 4.3445e-05 | 0.26763 | 0.26763 | 0.26763 | 0.99949 | -0.0097131 | 0.99991 | -0.0017898 | 24.5084
54 | 0.15294 | 0.038739 | -0.15288 | -0.0387 | 6.1379e-05 | 3.8911e-05 | 0.22796 | 0.22796 | 0.22796 | 0.99895 | -0.020011 | 0.99851 | -0.028371 | 20.8757
55 | -0.18614 | -0.047119 | 0.18616 | 0.047129 | 1.5995e-05 | 1.0171e-05 | 0.27718 | 0.27718 | 0.27718 | 0.99991 | -0.0017898 | 1 | 0 | 25.3825
56 | -0.087694 | -0.022072 | 0.087925 | 0.022219 | 0.00023055 | 0.00014712 | 0.13344 | 0.13344 | 0.13344 | 0.97816 | -0.41974 | 0.98097 | -0.36489 | 36.6586
57 | -0.087925 | -0.022219 | 0.088157 | 0.022367 | 0.00023179 | 0.0001479 | 0.13344 | 0.13344 | 0.13344 | 0.98097 | -0.36489 | 0.9838 | -0.31007 | 36.6585
58 | -0.1031 | -0.026112 | 0.1031 | 0.026113 | 1.1512e-06 | 7.3515e-07 | 0.15604 | 0.15604 | 0.15604 | 0.9838 | -0.31007 | 0.98381 | -0.30983 | 42.8679
59 | -0.1129 | -0.028568 | 0.11313 | 0.028714 | 0.00022945 | 0.00014658 | 0.17085 | 0.17085 | 0.17085 | 0.98381 | -0.30983 | 0.98599 | -0.26758 | 46.938
60 | -0.11933 | -0.03027 | 0.11951 | 0.030381 | 0.00017331 | 0.00011074 | 0.18022 | 0.18022 | 0.18022 | 0.98599 | -0.26758 | 0.98756 | -0.23742 | 49.5115
61 | -0.010256 | -0.0025703 | 0.010257 | 0.0025711 | 1.4846e-06 | 7.375e-07 | 0.015445 | 0.015444 | 0.015445 | 0.9881 | -0.22911 | 0.98826 | -0.22608 | 4.243
62 | -0.025397 | -0.0063654 | 0.025406 | 0.0063713 | 9.5933e-06 | 5.9155e-06 | 0.03824 | 0.03824 | 0.03824 | 0.98826 | -0.22608 | 0.98866 | -0.21815 | 10.5055
63 | 0.13375 | 0.034019 | -0.13358 | -0.03391 | 0.0001703 | 0.00010885 | 0.20143 | 0.20143 | 0.20143 | 0.98895 | -0.2105 | 0.98758 | -0.23696 | 55.3379
64 | 0.12869 | 0.032684 | -0.12869 | -0.032682 | 2.8527e-06 | 1.8231e-06 | 0.19406 | 0.19406 | 0.19406 | 0.98758 | -0.23696 | 0.98756 | -0.23742 | 53.3127
65 | -0.053638 | -0.013454 | 0.053643 | 0.013457 | 4.7578e-06 | 3.02e-06 | 0.080696 | 0.080696 | 0.080696 | 0.98911 | -0.20943 | 0.98921 | -0.20757 | 22.1693
66 | 0.046073 | 0.011558 | -0.046058 | -0.011549 | 1.4932e-05 | 9.4499e-06 | 0.069316 | 0.069316 | 0.069316 | 0.98911 | -0.20943 | 0.98876 | -0.21623 | 19.0429
67 | -0.061073 | -0.015319 | 0.061094 | 0.015332 | 2.0748e-05 | 1.3194e-05 | 0.091873 | 0.091873 | 0.091873 | 0.98921 | -0.20757 | 0.98957 | -0.20044 | 25.2399
68 | 0.038869 | 0.0097468 | -0.038866 | -0.0097446 | 3.5591e-06 | 2.2423e-06 | 0.058497 | 0.058497 | 0.058497 | 0.98876 | -0.21623 | 0.98866 | -0.21815 | 16.0707
69 | -0.06538 | -0.016407 | 0.065404 | 0.016422 | 2.3563e-05 | 1.4997e-05 | 0.098319 | 0.098319 | 0.098319 | 0.98957 | -0.20044 | 0.98996 | -0.19289 | 27.0108
70 | -0.06963 | -0.017481 | 0.069652 | 0.017495 | 2.2774e-05 | 1.4504e-05 | 0.10467 | 0.10467 | 0.10467 | 0.98996 | -0.19289 | 0.99032 | -0.18603 | 28.7557
71 | -0.092987 | -0.023343 | 0.092994 | 0.023348 | 7.0147e-06 | 4.4771e-06 | 0.13973 | 0.13973 | 0.13973 | 0.99032 | -0.18603 | 0.9904 | -0.18445 | 38.3882
72 | 0.10153 | 0.02553 | -0.10148 | -0.025494 | 5.6628e-05 | 3.6158e-05 | 0.15239 | 0.15239 | 0.15239 | 0.99158 | -0.16155 | 0.99098 | -0.17324 | 41.8667
73 | 0.097258 | 0.024437 | -0.097206 | -0.024403 | 5.2038e-05 | 3.322e-05 | 0.14606 | 0.14606 | 0.14606 | 0.99098 | -0.17324 | 0.9904 | -0.18445 | 40.1266
74 | -0.0048045 | -0.0012041 | 0.004805 | 0.0012041 | 4.4073e-07 | 9.6186e-09 | 0.0073339 | 0.0073338 | 0.0073339 | 0.97482 | -0.48551 | 0.97492 | -0.48358 | 2.0148
75 | -0.011522 | -0.0028875 | 0.011523 | 0.0028885 | 1.8428e-06 | 9.8122e-07 | 0.017585 | 0.017585 | 0.017585 | 0.97492 | -0.48358 | 0.97509 | -0.48023 | 4.8311
76 | -0.030925 | -0.0077509 | 0.030928 | 0.0077527 | 2.9591e-06 | 1.8496e-06 | 0.047192 | 0.047192 | 0.047192 | 0.97509 | -0.48023 | 0.97519 | -0.47822 | 12.9649
77 | -0.036075 | -0.0090427 | 0.036092 | 0.0090537 | 1.7423e-05 | 1.096e-05 | 0.055046 | 0.055046 | 0.055046 | 0.97519 | -0.47822 | 0.97571 | -0.46809 | 15.1225
78 | -0.043932 | -0.011019 | 0.043959 | 0.011036 | 2.7246e-05 | 1.7235e-05 | 0.067002 | 0.067002 | 0.067002 | 0.97571 | -0.46809 | 0.97637 | -0.45508 | 18.4072
79 | -0.053756 | -0.013491 | 0.053796 | 0.013517 | 4.0632e-05 | 2.5802e-05 | 0.081932 | 0.081932 | 0.081932 | 0.97637 | -0.45508 | 0.97717 | -0.43925 | 22.5088

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59962 | 0.15249

## res_load
| p_mw | q_mvar
0 | 0.0037502 | 0.00093989
1 | 0.0036844 | 0.00092339
2 | 0.0036844 | 0.00092339
3 | 0.0082212 | 0.0020604
4 | 0.011834 | 0.0029659
5 | 0.0036882 | 0.00092434
6 | 0.012965 | 0.0032494
7 | 0.0054977 | 0.0013778
8 | 0.0037042 | 0.00092836
9 | 0.005491 | 0.0013762
10 | 0.0055754 | 0.0013973
11 | 0.011846 | 0.0029689
12 | 0.0055801 | 0.0013985
13 | 0.010941 | 0.0027421
14 | 0.0097789 | 0.0024508
15 | 0.00286 | 0.00071678
16 | 0.020789 | 0.0052101
17 | 0.0034185 | 0.00085675
18 | 0.0097795 | 0.002451
19 | 0.0081109 | 0.0020328
20 | 0.0071708 | 0.0017972
21 | 0.0064236 | 0.0016099
22 | 0.04215 | 0.010564
23 | 0.0035148 | 0.00088089
24 | 0.0016276 | 0.00040791
25 | 0.01041 | 0.0026091
26 | 0.0041876 | 0.0010495
27 | 0.0068453 | 0.0017156
28 | 0.0050641 | 0.0012692
29 | 0.0045249 | 0.001134
30 | 0.0042994 | 0.0010775
31 | 0.0051567 | 0.0012924
32 | 0.0058788 | 0.0014734
33 | 0.0058958 | 0.0014776
34 | 0.013426 | 0.003365
35 | 0.0078121 | 0.0019579
36 | 0.0078 | 0.0019549
37 | 0.0098452 | 0.0024674
38 | 0.0048496 | 0.0012154
39 | 0.0048384 | 0.0012126
40 | 0.011638 | 0.0029168
41 | 0.012988 | 0.0032551
42 | 0.005126 | 0.0012847
43 | 0.0044105 | 0.0011054
44 | 0.0041133 | 0.0010309
45 | 0.006414 | 0.0016075
46 | 0.002739 | 0.00068646
47 | 0.0028799 | 0.00072178
48 | 0.0058945 | 0.0014773
49 | 0.014944 | 0.0037452
50 | 0.0097949 | 0.0024548
51 | 0.0062074 | 0.0015557
52 | 0.0095712 | 0.0023988
53 | 0.010256 | 0.0025703
54 | 0.01514 | 0.0037943
55 | 0.0073926 | 0.0018528
56 | 0.0048925 | 0.0012262
57 | 0.0091828 | 0.0023014
58 | 0.0075646 | 0.0018959
59 | 0.0074303 | 0.0018622
60 | 0.0071889 | 0.0018017
61 | 0.0042868 | 0.0010744
62 | 0.013459 | 0.0033732
63 | 0.0042257 | 0.001059
64 | 0.023335 | 0.0058483
65 | 0.0021998 | 0.00055132
66 | 0.0042181 | 0.0010572
67 | 0.0042117 | 0.0010556
68 | 0.0048045 | 0.0012041
69 | 0.0067166 | 0.0016833
70 | 0.019401 | 0.0048624
71 | 0.0051471 | 0.00129
72 | 0.0078398 | 0.0019648
73 | 0.0097964 | 0.0024552
74 | 0.002866 | 0.0007183

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1