## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-273_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-273_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-273_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2701-273_0_4_node_21 | 0.4 | n |  | TRUE
4 | bus_LV_2701-273_0_4_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_2701-273_0_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_2701-273_0_4_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_2701-273_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2701-273_0_4_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_2701-273_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2701-273_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_2701-273_0_4_node_22 | 0.4 | n |  | TRUE
12 | bus_LV_2701-273_0_4_node_4 | 0.4 | n |  | TRUE
13 | bus_LV_2701-273_0_4_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_2701-273_0_4_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_2701-273_0_4_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_2701-273_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2701-273_0_4_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_2701-273_0_4_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_2701-273_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2701-273_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_2701-273_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2701-273_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2701-273_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_2701-273_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_2701-273_0_4_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_2701-273_0_4_node_27 | 0.4 | n |  | TRUE
27 | bus_MV_570_0_node_67 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-273_0_4_load_0 | 0 | 0.099619 | 0.024967 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-273_0_4_load_21 | 3 | 0.09975 | 0.025 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-273_0_4_load_24 | 8 | 0.013181 | 0.0033034 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-273_0_4_load_22 | 11 | 0.030943 | 0.007755 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-273_0_4_load_4 | 12 | 0.06159 | 0.015436 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-273_0_4_load_23 | 13 | 0.008373 | 0.0020985 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-273_0_4_load_29 | 14 | 0.0093236 | 0.0023367 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-273_0_4_load_28 | 15 | 0.010333 | 0.0025896 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-273_0_4_load_13 | 16 | 0.056884 | 0.014256 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-273_0_4_load_25 | 17 | 0.0060496 | 0.0015162 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-273_0_4_load_14 | 19 | 0.0081344 | 0.0020387 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-273_0_4_load_16 | 20 | 0.0086248 | 0.0021616 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-273_0_4_load_18 | 21 | 0.0086244 | 0.0021615 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-273_0_4_load_17 | 22 | 0.0077416 | 0.0019402 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-273_0_4_load_19 | 23 | 0.010746 | 0.0026933 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-273_0_4_load_30 | 25 | 0.0048974 | 0.0012274 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-273_0_4_load_27 | 26 | 0.0046589 | 0.0011676 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-273_0_4_line_0 |  | 0 | 1 | 0.010171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-273_0_4_line_1 |  | 1 | 2 | 0.036069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-273_0_4_line_2 |  | 2 | 3 | 0.022116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-273_0_4_line_3 |  | 3 | 4 | 0.019899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2701-273_0_4_line_4 |  | 4 | 5 | 0.055729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2701-273_0_4_line_5 |  | 5 | 6 | 0.006981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2701-273_0_4_line_6 |  | 6 | 16 | 0.012605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-273_0_4_line_7 |  | 6 | 10 | 0.003725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-273_0_4_line_8 |  | 7 | 8 | 0.072764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-273_0_4_line_9 |  | 7 | 9 | 0.074287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-273_0_4_line_10 |  | 8 | 13 | 0.0027771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-273_0_4_line_11 |  | 9 | 12 | 0.093094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-273_0_4_line_12 |  | 10 | 11 | 0.030545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-273_0_4_line_13 |  | 11 | 13 | 0.015184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-273_0_4_line_14 |  | 14 | 15 | 0.0068376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-273_0_4_line_15 |  | 15 | 24 | 0.037112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-273_0_4_line_16 |  | 16 | 19 | 0.019724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-273_0_4_line_17 |  | 17 | 18 | 0.011299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-273_0_4_line_18 |  | 18 | 26 | 0.044595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-273_0_4_line_19 |  | 18 | 24 | 0.008358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-273_0_4_line_20 |  | 19 | 20 | 0.018939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-273_0_4_line_21 |  | 20 | 21 | 0.017944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-273_0_4_line_22 |  | 21 | 22 | 0.018418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-273_0_4_line_23 |  | 22 | 23 | 0.017357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-273_0_4_line_24 |  | 23 | 24 | 0.017737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-273_0_4_line_25 |  | 24 | 25 | 0.017163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-273_0_4_trafo_9 | 0.63 MVA 20/0.4 kV | 27 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2611281.0053 | 1270142.9587 | 2611275.9515 | 1270134.1317
1 | 2611281.0053 | 1270142.9587 | 2611288.5186 | 1270156.0823 | 2611290.2792 | 1270159.8994 | 2611292.879 | 1270165.5639 | 2611298.7506 | 1270163.696 | 2611302.9133 | 1270162.4364
2 | 2611302.9133 | 1270162.4364 | 2611324.0336 | 1270155.8748
3 | 2611339.9006 | 1270156.625 | 2611338.3447 | 1270151.9409 | 2611337.3822 | 1270151.7278 | 2611324.0336 | 1270155.8748
4 | 2611339.9006 | 1270156.625 | 2611354.248 | 1270152.2604 | 2611355.9193 | 1270151.6743 | 2611356.4839 | 1270151.4752 | 2611362.4011 | 1270149.4073 | 2611362.913 | 1270149.2303 | 2611377.8712 | 1270144.1554 | 2611382.1157 | 1270135.5574 | 2611379.9677 | 1270133.6742 | 2611378.4612 | 1270130.7248
5 | 2611384.9811 | 1270128.1799 | 2611378.4612 | 1270130.7248
6 | 2611384.9811 | 1270128.1799 | 2611380.7726 | 1270116.2984
7 | 2611384.9811 | 1270128.1799 | 2611388.1974 | 1270130.0763
8 | 2611502.6946 | 1270090.2576 | 2611492.0568 | 1270094.0841 | 2611476.7874 | 1270100.4925 | 2611459.8784 | 1270106.5975 | 2611434.2943 | 1270114.9775
9 | 2611502.6946 | 1270090.2576 | 2611504.4725 | 1270096.7323 | 2611505.8471 | 1270101.7274 | 2611512.8129 | 1270102.0967 | 2611514.9785 | 1270102.6568 | 2611517.5486 | 1270104.1184 | 2611520.0652 | 1270106.0358 | 2611521.7767 | 1270107.9515 | 2611529.2994 | 1270123.7218 | 2611530.4233 | 1270126.0701 | 2611530.9232 | 1270128.2281 | 2611531.218 | 1270131.3531 | 2611531.1604 | 1270133.9104 | 2611530.8329 | 1270135.989 | 2611529.3892 | 1270139.4442 | 2611526.2552 | 1270141.7064 | 2611526.6293 | 1270142.7745 | 2611528.5223 | 1270148.1042
10 | 2611431.6552 | 1270115.8419 | 2611434.2943 | 1270114.9775
11 | 2611528.5223 | 1270148.1042 | 2611522.3104 | 1270150.8163 | 2611509.2768 | 1270156.5062 | 2611440.7504 | 1270178.9051
12 | 2611388.1974 | 1270130.0763 | 2611417.2251 | 1270120.5684
13 | 2611431.6552 | 1270115.8419 | 2611417.2251 | 1270120.5684
14 | 2611379.7231 | 1269999.6875 | 2611386.1471 | 1269997.3456
15 | 2611344.8556 | 1270012.3989 | 2611379.7231 | 1269999.6875
16 | 2611380.7726 | 1270116.2984 | 2611374.1871 | 1270097.7066
17 | 2611336.9284 | 1270015.119 | 2611340.7487 | 1270025.7529
18 | 2611336.9284 | 1270015.119 | 2611332.9486 | 1270007.1835 | 2611320.9126 | 1269973.555
19 | 2611336.9284 | 1270015.119 | 2611344.8556 | 1270012.3989
20 | 2611374.1871 | 1270097.7066 | 2611367.8635 | 1270079.854
21 | 2611367.8635 | 1270079.854 | 2611361.8723 | 1270062.9397
22 | 2611355.7228 | 1270045.5787 | 2611361.8723 | 1270062.9397
23 | 2611349.9277 | 1270029.2181 | 2611355.7228 | 1270045.5787
24 | 2611344.8556 | 1270012.3989 | 2611347.1606 | 1270018.7967 | 2611348.5375 | 1270022.6242 | 2611348.3678 | 1270024.8144 | 2611349.9277 | 1270029.2181
25 | 2611344.8556 | 1270012.3989 | 2611343.5158 | 1270008.8049 | 2611342.8347 | 1270006.98 | 2611339.8332 | 1270002.838 | 2611337.7017 | 1269996.9473

## bus_geodata
| x | y | coords
0 | 2611275.9515 | 1270134.1317
1 | 2611281.0053 | 1270142.9587
2 | 2611302.9133 | 1270162.4364
3 | 2611324.0336 | 1270155.8748
4 | 2611339.9006 | 1270156.625
5 | 2611378.4612 | 1270130.7248
6 | 2611384.9811 | 1270128.1799
7 | 2611502.6946 | 1270090.2576
8 | 2611434.2943 | 1270114.9775
9 | 2611528.5223 | 1270148.1042
10 | 2611388.1974 | 1270130.0763
11 | 2611417.2251 | 1270120.5684
12 | 2611440.7504 | 1270178.9051
13 | 2611431.6552 | 1270115.8419
14 | 2611386.1471 | 1269997.3456
15 | 2611379.7231 | 1269999.6875
16 | 2611380.7726 | 1270116.2984
17 | 2611340.7487 | 1270025.7529
18 | 2611336.9284 | 1270015.119
19 | 2611374.1871 | 1270097.7066
20 | 2611367.8635 | 1270079.854
21 | 2611361.8723 | 1270062.9397
22 | 2611355.7228 | 1270045.5787
23 | 2611349.9277 | 1270029.2181
24 | 2611344.8556 | 1270012.3989
25 | 2611337.7017 | 1269996.9473
26 | 2611320.9126 | 1269973.555
27 | 2611382.1157 | 1270135.5574

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98683 | -0.25343 | 0.099619 | 0.024967
1 | 0.98776 | -0.23531 | 0 | 0
2 | 0.99107 | -0.17133 | 0 | 0
3 | 0.99309 | -0.13232 | 0.09975 | 0.025
4 | 0.99491 | -0.097324 | 0 | 0
5 | 1 | 0 | -0.45498 | -0.11511
6 | 0.9992 | -0.015229 | 0 | 0
7 | 0.9901 | -0.18898 | 0 | 0
8 | 0.99425 | -0.10962 | 0.013181 | 0.0033034
9 | 0.98587 | -0.27068 | 0 | 0
10 | 0.99881 | -0.022651 | 0 | 0
11 | 0.99561 | -0.083734 | 0.030943 | 0.007755
12 | 0.98057 | -0.37406 | 0.06159 | 0.015436
13 | 0.99444 | -0.10596 | 0.008373 | 0.0020985
14 | 0.99103 | -0.17271 | 0.0093236 | 0.0023367
15 | 0.99109 | -0.17158 | 0.010333 | 0.0025896
16 | 0.99764 | -0.045208 | 0.056884 | 0.014256
17 | 0.99161 | -0.16144 | 0.0060496 | 0.0015162
18 | 0.99167 | -0.16023 | 0 | 0
19 | 0.99621 | -0.072582 | 0.0081344 | 0.0020387
20 | 0.99498 | -0.096229 | 0.0086248 | 0.0021616
21 | 0.99396 | -0.11596 | 0.0086244 | 0.0021615
22 | 0.99306 | -0.13344 | 0.0077416 | 0.0019402
23 | 0.99232 | -0.14756 | 0.010746 | 0.0026933
24 | 0.99175 | -0.15864 | 0 | 0
25 | 0.99168 | -0.16013 | 0.0048974 | 0.0012274
26 | 0.99148 | -0.16391 | 0.0046589 | 0.0011676
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.099619 | -0.024967 | 0.099706 | 0.025022 | 8.6065e-05 | 5.4952e-05 | 0.15021 | 0.15021 | 0.15021 | 0.98683 | -0.25343 | 0.98776 | -0.23531 | 41.2674
1 | -0.099706 | -0.025022 | 0.10001 | 0.025217 | 0.0003052 | 0.00019486 | 0.15021 | 0.15021 | 0.15021 | 0.98776 | -0.23531 | 0.99107 | -0.17133 | 41.2674
2 | -0.10001 | -0.025217 | 0.1002 | 0.025336 | 0.00018713 | 0.00011948 | 0.15021 | 0.15021 | 0.15021 | 0.99107 | -0.17133 | 0.99309 | -0.13232 | 41.2673
3 | -0.19995 | -0.050336 | 0.20028 | 0.05055 | 0.00033508 | 0.00021393 | 0.29968 | 0.29968 | 0.29968 | 0.99309 | -0.13232 | 0.99491 | -0.097324 | 41.1642
4 | -0.20028 | -0.05055 | 0.20122 | 0.051149 | 0.00093839 | 0.00059911 | 0.29968 | 0.29967 | 0.29968 | 0.99491 | -0.097324 | 1 | 0 | 41.1642
5 | 0.25211 | 0.063957 | -0.25192 | -0.063839 | 0.00018447 | 0.00011788 | 0.37541 | 0.37541 | 0.37541 | 1 | 0 | 0.9992 | -0.015229 | 51.5675
6 | 0.13657 | 0.034437 | -0.13637 | -0.034312 | 0.00019565 | 0.00012505 | 0.20345 | 0.20345 | 0.20345 | 0.9992 | -0.015229 | 0.99764 | -0.045208 | 55.8925
7 | 0.11536 | 0.029402 | -0.11532 | -0.029375 | 4.1307e-05 | 2.6388e-05 | 0.17196 | 0.17196 | 0.17196 | 0.9992 | -0.015229 | 0.99881 | -0.022651 | 47.2427
8 | -0.062138 | -0.015785 | 0.062377 | 0.015936 | 0.00023835 | 0.00015161 | 0.093463 | 0.093462 | 0.093463 | 0.9901 | -0.18898 | 0.99425 | -0.10962 | 25.6765
9 | 0.062138 | 0.015785 | -0.061895 | -0.01563 | 0.00024334 | 0.00015479 | 0.093463 | 0.093463 | 0.093463 | 0.9901 | -0.18898 | 0.98587 | -0.27068 | 25.6766
10 | -0.075557 | -0.01924 | 0.075571 | 0.019248 | 1.3342e-05 | 8.503e-06 | 0.11319 | 0.11319 | 0.11319 | 0.99425 | -0.10962 | 0.99444 | -0.10596 | 31.0957
11 | 0.061895 | 0.01563 | -0.06159 | -0.015436 | 0.00030495 | 0.00019399 | 0.093463 | 0.093463 | 0.093463 | 0.98587 | -0.27068 | 0.98057 | -0.37406 | 25.6767
12 | 0.11532 | 0.029375 | -0.11498 | -0.029159 | 0.00033872 | 0.00021638 | 0.17196 | 0.17196 | 0.17196 | 0.99881 | -0.022651 | 0.99561 | -0.083734 | 47.2427
13 | 0.084034 | 0.021404 | -0.083944 | -0.021347 | 8.9995e-05 | 5.74e-05 | 0.12572 | 0.12572 | 0.12572 | 0.99561 | -0.083734 | 0.99444 | -0.10596 | 34.5377
14 | -0.0093236 | -0.0023367 | 0.0093241 | 0.0023369 | 5.025e-07 | 2.335e-07 | 0.013999 | 0.013999 | 0.013999 | 0.99103 | -0.17271 | 0.99109 | -0.17158 | 3.8459
15 | -0.019657 | -0.0049265 | 0.019669 | 0.0049338 | 1.2122e-05 | 7.2793e-06 | 0.029513 | 0.029512 | 0.029513 | 0.99109 | -0.17158 | 0.99175 | -0.15864 | 8.1078
16 | 0.079487 | 0.020056 | -0.079383 | -0.019989 | 0.00010405 | 6.6332e-05 | 0.1186 | 0.1186 | 0.1186 | 0.99764 | -0.045208 | 0.99621 | -0.072582 | 32.5838
17 | -0.0060496 | -0.0015162 | 0.0060499 | 0.0015162 | 3.492e-07 | 7.7714e-08 | 0.0090781 | 0.009078 | 0.0090781 | 0.99161 | -0.16144 | 0.99167 | -0.16023 | 2.494
18 | 0.0046597 | 0.0011676 | -0.0046589 | -0.0011676 | 8.1757e-07 | -5.1997e-08 | 0.0069919 | 0.0069921 | 0.0069921 | 0.99167 | -0.16023 | 0.99148 | -0.16391 | 1.9209
19 | -0.01071 | -0.0026838 | 0.01071 | 0.0026842 | 8.094e-07 | 4.1017e-07 | 0.01607 | 0.01607 | 0.01607 | 0.99167 | -0.16023 | 0.99175 | -0.15864 | 4.4148
20 | 0.071248 | 0.017951 | -0.071168 | -0.017899 | 8.0488e-05 | 5.1266e-05 | 0.10645 | 0.10645 | 0.10645 | 0.99621 | -0.072582 | 0.99498 | -0.096229 | 29.2458
21 | 0.062543 | 0.015738 | -0.062484 | -0.0157 | 5.8897e-05 | 3.7462e-05 | 0.093556 | 0.093556 | 0.093556 | 0.99498 | -0.096229 | 0.99396 | -0.11596 | 25.7023
22 | 0.05386 | 0.013539 | -0.053815 | -0.01351 | 4.4919e-05 | 2.851e-05 | 0.080645 | 0.080645 | 0.080645 | 0.99396 | -0.11596 | 0.99306 | -0.13344 | 22.1553
23 | 0.046073 | 0.01157 | -0.046042 | -0.01155 | 3.1029e-05 | 1.9634e-05 | 0.069045 | 0.069045 | 0.069045 | 0.99306 | -0.13344 | 0.99232 | -0.14756 | 18.9684
24 | 0.035296 | 0.0088572 | -0.035277 | -0.0088455 | 1.8634e-05 | 1.1697e-05 | 0.052931 | 0.052931 | 0.052931 | 0.99232 | -0.14756 | 0.99175 | -0.15864 | 14.5414
25 | 0.0048977 | 0.0012274 | -0.0048974 | -0.0012274 | 3.4755e-07 | 9.8359e-10 | 0.0073485 | 0.0073485 | 0.0073485 | 0.99175 | -0.15864 | 0.99168 | -0.16013 | 2.0188

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45498 | 0.11511

## res_load
| p_mw | q_mvar
0 | 0.099619 | 0.024967
1 | 0.09975 | 0.025
2 | 0.013181 | 0.0033034
3 | 0.030943 | 0.007755
4 | 0.06159 | 0.015436
5 | 0.008373 | 0.0020985
6 | 0.0093236 | 0.0023367
7 | 0.010333 | 0.0025896
8 | 0.056884 | 0.014256
9 | 0.0060496 | 0.0015162
10 | 0.0081344 | 0.0020387
11 | 0.0086248 | 0.0021616
12 | 0.0086244 | 0.0021615
13 | 0.0077416 | 0.0019402
14 | 0.010746 | 0.0026933
15 | 0.0048974 | 0.0012274
16 | 0.0046589 | 0.0011676

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1