## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-277_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-277_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-277_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2701-277_0_3_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_2701-277_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-277_0_3_node_42 | 0.4 | n |  | TRUE
6 | bus_LV_2701-277_0_3_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_2701-277_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2701-277_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_2701-277_0_3_node_35 | 0.4 | n |  | TRUE
10 | bus_LV_2701-277_0_3_node_33 | 0.4 | n |  | TRUE
11 | bus_LV_2701-277_0_3_node_34 | 0.4 | n |  | TRUE
12 | bus_LV_2701-277_0_3_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_2701-277_0_3_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_2701-277_0_3_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_2701-277_0_3_node_32 | 0.4 | n |  | TRUE
16 | bus_LV_2701-277_0_3_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_2701-277_0_3_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_2701-277_0_3_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_2701-277_0_3_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_2701-277_0_3_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_2701-277_0_3_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_2701-277_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2701-277_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2701-277_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2701-277_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_2701-277_0_3_node_41 | 0.4 | n |  | TRUE
27 | bus_LV_2701-277_0_3_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_2701-277_0_3_node_40 | 0.4 | n |  | TRUE
29 | bus_LV_2701-277_0_3_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2701-277_0_3_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2701-277_0_3_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_2701-277_0_3_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_2701-277_0_3_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_2701-277_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_2701-277_0_3_node_43 | 0.4 | n |  | TRUE
36 | bus_LV_2701-277_0_3_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_2701-277_0_3_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_2701-277_0_3_node_39 | 0.4 | n |  | TRUE
39 | bus_MV_572_0_node_24 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-277_0_3_load_0 | 0 | 0.0097158 | 0.002435 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-277_0_3_load_3 | 2 | 0.013853 | 0.0034719 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-277_0_3_load_42 | 5 | 0.00021464 | 5.3793e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-277_0_3_load_26 | 6 | 0.0020702 | 0.00051883 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-277_0_3_load_6 | 7 | 0.023473 | 0.0058828 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-277_0_3_load_11 | 12 | 0.0080429 | 0.0020158 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-277_0_3_load_24 | 13 | 0.010481 | 0.0026267 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-277_0_3_load_32 | 15 | 0.059158 | 0.014826 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-277_0_3_load_27 | 16 | 0.0045346 | 0.0011365 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-277_0_3_load_22 | 17 | 0.02563 | 0.0064236 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-277_0_3_load_38 | 19 | 0.023967 | 0.0060066 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-277_0_3_load_8 | 20 | 0.0058556 | 0.0014675 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-277_0_3_load_9 | 21 | 0.0028143 | 0.00070532 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-277_0_3_load_13 | 22 | 0.00076756 | 0.00019237 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-277_0_3_load_41 | 26 | 0.00045704 | 0.00011455 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-277_0_3_load_31 | 27 | 0.0019271 | 0.00048299 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-277_0_3_load_40 | 28 | 0.00073936 | 0.0001853 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-277_0_3_load_17 | 29 | 0.05794 | 0.014521 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-277_0_3_load_18 | 30 | 0.02704 | 0.0067768 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-277_0_3_load_20 | 32 | 0.04997 | 0.012524 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-277_0_3_load_43 | 35 | 0.0031356 | 0.00078587 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-277_0_3_load_29 | 36 | 0.0011227 | 0.00028137 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-277_0_3_load_25 | 37 | 0.031751 | 0.0079576 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-277_0_3_load_39 | 38 | 0.03005 | 0.0075313 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-277_0_3_line_0 |  | 0 | 1 | 0.050513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-277_0_3_line_1 |  | 1 | 2 | 0.031071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-277_0_3_line_2 |  | 1 | 3 | 0.015903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-277_0_3_line_3 |  | 3 | 6 | 0.006749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-277_0_3_line_4 |  | 3 | 4 | 0.015878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-277_0_3_line_5 |  | 4 | 5 | 0.089529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-277_0_3_line_6 |  | 6 | 12 | 0.020192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-277_0_3_line_7 |  | 6 | 13 | 0.016474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-277_0_3_line_8 |  | 7 | 8 | 0.037786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-277_0_3_line_9 |  | 8 | 9 | 0.087761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_2701-277_0_3_line_10 |  | 8 | 10 | 0.043497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2701-277_0_3_line_11 |  | 8 | 11 | 0.033614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-277_0_3_line_12 |  | 9 | 17 | 0.034281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2701-277_0_3_line_13 |  | 10 | 14 | 0.007636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-277_0_3_line_14 |  | 10 | 15 | 0.076471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-277_0_3_line_15 |  | 11 | 16 | 0.024008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-277_0_3_line_16 |  | 12 | 21 | 0.025277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-277_0_3_line_17 |  | 13 | 37 | 0.030408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-277_0_3_line_18 |  | 14 | 18 | 0.05915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-277_0_3_line_19 |  | 15 | 27 | 0.13721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-277_0_3_line_20 |  | 16 | 37 | 0.042579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-277_0_3_line_21 |  | 17 | 31 | 0.056925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-277_0_3_line_22 |  | 18 | 19 | 0.052116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-277_0_3_line_23 |  | 20 | 21 | 0.050038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-277_0_3_line_24 |  | 22 | 23 | 0.0072951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-277_0_3_line_25 |  | 23 | 24 | 0.007282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-277_0_3_line_26 |  | 24 | 25 | 0.02018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-277_0_3_line_27 |  | 24 | 26 | 0.020979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-277_0_3_line_28 |  | 25 | 27 | 0.0086686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-277_0_3_line_29 |  | 26 | 28 | 0.009154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-277_0_3_line_30 |  | 28 | 38 | 0.039217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-277_0_3_line_31 |  | 29 | 30 | 0.00011163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-277_0_3_line_32 |  | 29 | 31 | 0.042352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-277_0_3_line_33 |  | 30 | 32 | 0.081081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-277_0_3_line_34 |  | 31 | 33 | 0.017976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-277_0_3_line_35 |  | 32 | 34 | 0.047768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-277_0_3_line_36 |  | 33 | 35 | 0.021668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-277_0_3_line_37 |  | 34 | 36 | 0.07016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-277_0_3_trafo_22 | 0.63 MVA 20/0.4 kV | 39 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2611565.0579 | 1269235.1292 | 2611563.3295 | 1269184.6455
1 | 2611565.0579 | 1269235.1292 | 2611534.0215 | 1269236.6032
2 | 2611565.0579 | 1269235.1292 | 2611573.4558 | 1269234.7342 | 2611573.8701 | 1269242.2181
3 | 2611572.6609 | 1269248.7981 | 2611572.8179 | 1269245.4739 | 2611573.8701 | 1269242.2181
4 | 2611573.8701 | 1269242.2181 | 2611573.4558 | 1269234.7342 | 2611581.8381 | 1269234.6394
5 | 2611581.8381 | 1269234.6394 | 2611669.9192 | 1269230.0529 | 2611671.2461 | 1269229.9886
6 | 2611572.6609 | 1269248.7981 | 2611592.8288 | 1269247.8151
7 | 2611572.6609 | 1269248.7981 | 2611556.2069 | 1269249.6008
8 | 2611434.1378 | 1269241.3469 | 2611471.8816 | 1269239.5544
9 | 2611495.468 | 1269288.2094 | 2611452.3015 | 1269268.6345 | 2611432.7926 | 1269256.1325 | 2611435.2985 | 1269255.9817 | 2611435.1077 | 1269253.4684 | 2611434.8376 | 1269249.176 | 2611434.1378 | 1269241.3469
10 | 2611429.9622 | 1269280.2441 | 2611429.1151 | 1269262.9858 | 2611429.364 | 1269258.7277 | 2611430.3461 | 1269256.706 | 2611432.7926 | 1269256.1325 | 2611435.2985 | 1269255.9817 | 2611435.1077 | 1269253.4684 | 2611434.8376 | 1269249.176 | 2611434.1378 | 1269241.3469
11 | 2611434.1378 | 1269241.3469 | 2611434.8376 | 1269249.176 | 2611446.7121 | 1269248.5762 | 2611459.3267 | 1269254.3268
12 | 2611495.468 | 1269288.2094 | 2611495.3508 | 1269294.3246 | 2611502.1142 | 1269302.5769 | 2611518.2046 | 1269309.4463
13 | 2611422.8239 | 1269283.0101 | 2611424.2395 | 1269282.468 | 2611429.9622 | 1269280.2441
14 | 2611429.9622 | 1269280.2441 | 2611433.5062 | 1269299.7424 | 2611435.7515 | 1269309.8539 | 2611447.066 | 1269354.7451
15 | 2611459.3267 | 1269254.3268 | 2611483.3066 | 1269253.157
16 | 2611592.8288 | 1269247.8151 | 2611618.0754 | 1269246.5845
17 | 2611556.2069 | 1269249.6008 | 2611525.8346 | 1269251.0824
18 | 2611422.8239 | 1269283.0101 | 2611421.5739 | 1269283.4969 | 2611415.7608 | 1269285.754 | 2611412.757 | 1269286.6377 | 2611407.2252 | 1269283.4471 | 2611406.2106 | 1269282.867 | 2611398.2202 | 1269310.1264 | 2611394.6458 | 1269322.0836
19 | 2611447.066 | 1269354.7451 | 2611480.5998 | 1269487.7927
20 | 2611525.8346 | 1269251.0824 | 2611483.3066 | 1269253.157
21 | 2611570.5578 | 1269331.7971 | 2611518.2046 | 1269309.4463
22 | 2611394.6458 | 1269322.0836 | 2611390.2914 | 1269336.6522 | 2611384.6425 | 1269351.4184 | 2611378.8725 | 1269362.6598 | 2611374.23 | 1269369.7379
23 | 2611668.0542 | 1269244.1484 | 2611618.0754 | 1269246.5845
24 | 2611465.8285 | 1269487.6709 | 2611458.9272 | 1269490.0354
25 | 2611465.8285 | 1269487.6709 | 2611472.7401 | 1269485.3159
26 | 2611472.7401 | 1269485.3159 | 2611475.9131 | 1269498.0532 | 2611482.7184 | 1269496.1984
27 | 2611472.7401 | 1269485.3159 | 2611467.7255 | 1269464.9452
28 | 2611482.7184 | 1269496.1984 | 2611480.5998 | 1269487.7927
29 | 2611467.7255 | 1269464.9452 | 2611465.5374 | 1269456.0565
30 | 2611455.7876 | 1269418.0712 | 2611464.125 | 1269450.3189 | 2611465.5374 | 1269456.0565
31 | 2611553.4552 | 1269370.6646 | 2611553.5001 | 1269370.5624
32 | 2611570.5578 | 1269331.7971 | 2611569.4015 | 1269334.4189 | 2611553.5001 | 1269370.5624
33 | 2611553.4552 | 1269370.6646 | 2611535.5058 | 1269411.463 | 2611568.9778 | 1269426.0411
34 | 2611570.5578 | 1269331.7971 | 2611573.6187 | 1269324.8426 | 2611576.0674 | 1269319.2879 | 2611577.7981 | 1269315.344
35 | 2611612.7726 | 1269445.1151 | 2611568.9778 | 1269426.0411
36 | 2611577.7981 | 1269315.344 | 2611584.6393 | 1269318.315 | 2611597.6774 | 1269323.9636
37 | 2611612.7726 | 1269445.1151 | 2611640.6595 | 1269380.7359

## bus_geodata
| x | y | coords
0 | 2611563.3295 | 1269184.6455
1 | 2611565.0579 | 1269235.1292
2 | 2611534.0215 | 1269236.6032
3 | 2611573.8701 | 1269242.2181
4 | 2611581.8381 | 1269234.6394
5 | 2611671.2461 | 1269229.9886
6 | 2611572.6609 | 1269248.7981
7 | 2611471.8816 | 1269239.5544
8 | 2611434.1378 | 1269241.3469
9 | 2611495.468 | 1269288.2094
10 | 2611429.9622 | 1269280.2441
11 | 2611459.3267 | 1269254.3268
12 | 2611592.8288 | 1269247.8151
13 | 2611556.2069 | 1269249.6008
14 | 2611422.8239 | 1269283.0101
15 | 2611447.066 | 1269354.7451
16 | 2611483.3066 | 1269253.157
17 | 2611518.2046 | 1269309.4463
18 | 2611394.6458 | 1269322.0836
19 | 2611374.23 | 1269369.7379
20 | 2611668.0542 | 1269244.1484
21 | 2611618.0754 | 1269246.5845
22 | 2611458.9272 | 1269490.0354
23 | 2611465.8285 | 1269487.6709
24 | 2611472.7401 | 1269485.3159
25 | 2611482.7184 | 1269496.1984
26 | 2611467.7255 | 1269464.9452
27 | 2611480.5998 | 1269487.7927
28 | 2611465.5374 | 1269456.0565
29 | 2611553.5001 | 1269370.5624
30 | 2611553.4552 | 1269370.6646
31 | 2611570.5578 | 1269331.7971
32 | 2611568.9778 | 1269426.0411
33 | 2611577.7981 | 1269315.344
34 | 2611612.7726 | 1269445.1151
35 | 2611597.6774 | 1269323.9636
36 | 2611640.6596 | 1269380.7359
37 | 2611525.8346 | 1269251.0824
38 | 2611455.7876 | 1269418.0712
39 | 2611495.468 | 1269288.2094

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97574 | -0.46675 | 0.0097158 | 0.002435
1 | 0.9762 | -0.45777 | 0 | 0
2 | 0.9758 | -0.46564 | 0.013853 | 0.0034719
3 | 0.97655 | -0.45091 | 0 | 0
4 | 0.97655 | -0.45098 | 0 | 0
5 | 0.97653 | -0.45133 | 0.00021464 | 5.3793e-05
6 | 0.9767 | -0.44798 | 0.0020702 | 0.00051883
7 | 0.98616 | -0.26363 | 0.023473 | 0.0058828
8 | 0.98698 | -0.24775 | 0 | 0
9 | 0.99634 | -0.068939 | 0 | 0
10 | 0.98461 | -0.29342 | 0 | 0
11 | 0.98419 | -0.30164 | 0 | 0
12 | 0.97638 | -0.45415 | 0.0080429 | 0.0020158
13 | 0.97735 | -0.43517 | 0.010481 | 0.0026267
14 | 0.98444 | -0.29671 | 0 | 0
15 | 0.97799 | -0.42229 | 0.059158 | 0.014826
16 | 0.9822 | -0.34031 | 0.0045346 | 0.0011365
17 | 1 | 0 | -0.37725 | -0.096656
18 | 0.98313 | -0.32224 | 0 | 0
19 | 0.98198 | -0.34479 | 0.023967 | 0.0060066
20 | 0.97591 | -0.46352 | 0.0058556 | 0.0014675
21 | 0.97618 | -0.45816 | 0.0028143 | 0.00070532
22 | 0.97277 | -0.52476 | 0.00076756 | 0.00019237
23 | 0.97277 | -0.52465 | 0 | 0
24 | 0.97278 | -0.52455 | 0 | 0
25 | 0.97338 | -0.51266 | 0 | 0
26 | 0.97216 | -0.53663 | 0.00045704 | 0.00011455
27 | 0.97364 | -0.50755 | 0.0019271 | 0.00048299
28 | 0.9719 | -0.54183 | 0.00073936 | 0.0001853
29 | 0.98741 | -0.24162 | 0.05794 | 0.014521
30 | 0.9874 | -0.24178 | 0.02704 | 0.0067768
31 | 0.99271 | -0.13914 | 0 | 0
32 | 0.98358 | -0.31613 | 0.04997 | 0.012524
33 | 0.99266 | -0.14014 | 0 | 0
34 | 0.98353 | -0.3171 | 0 | 0
35 | 0.99259 | -0.14134 | 0.0031356 | 0.00078587
36 | 0.98346 | -0.31852 | 0.0011227 | 0.00028137
37 | 0.97885 | -0.40578 | 0.031751 | 0.0079576
38 | 0.9708 | -0.5636 | 0.03005 | 0.0075313
39 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0097158 | -0.002435 | 0.00972 | 0.002437 | 4.1585e-06 | 2.0302e-06 | 0.014817 | 0.014816 | 0.014817 | 0.97574 | -0.46675 | 0.9762 | -0.45777 | 4.0705
1 | 0.013858 | 0.0034749 | -0.013853 | -0.0034719 | 5.1998e-06 | 2.9396e-06 | 0.021125 | 0.021125 | 0.021125 | 0.9762 | -0.45777 | 0.9758 | -0.46564 | 5.8036
2 | -0.023578 | -0.0059119 | 0.023586 | 0.0059167 | 7.7035e-06 | 4.7313e-06 | 0.035941 | 0.035941 | 0.035941 | 0.9762 | -0.45777 | 0.97655 | -0.45091 | 9.874
3 | -0.023801 | -0.0059691 | 0.023804 | 0.0059712 | 3.329e-06 | 2.0461e-06 | 0.036268 | 0.036268 | 0.036268 | 0.97655 | -0.45091 | 0.9767 | -0.44798 | 9.9637
4 | 0.00021464 | 5.2477e-05 | -0.00021464 | -5.2676e-05 | 6.3524e-10 | -1.9825e-07 | 0.00032659 | 0.00032666 | 0.00032666 | 0.97655 | -0.45091 | 0.97655 | -0.45098 | 0.089743
5 | 0.00021464 | 5.2676e-05 | -0.00021464 | -5.3793e-05 | 3.5869e-09 | -1.1178e-06 | 0.00032666 | 0.00032706 | 0.00032706 | 0.97655 | -0.45098 | 0.97653 | -0.45133 | 0.089852
6 | 0.016721 | 0.0041926 | -0.016716 | -0.0041897 | 4.9141e-06 | 2.8924e-06 | 0.025475 | 0.025475 | 0.025475 | 0.9767 | -0.44798 | 0.97638 | -0.45415 | 6.9987
7 | -0.042595 | -0.010683 | 0.042621 | 0.010699 | 2.6018e-05 | 1.6445e-05 | 0.064897 | 0.064897 | 0.064897 | 0.9767 | -0.44798 | 0.97735 | -0.43517 | 17.8288
8 | -0.023473 | -0.0058828 | 0.023491 | 0.0058937 | 1.7775e-05 | 1.0894e-05 | 0.035418 | 0.035418 | 0.035418 | 0.98616 | -0.26363 | 0.98698 | -0.24775 | 9.7302
9 | -0.2318 | -0.058835 | 0.23382 | 0.06012 | 0.0020128 | 0.0012859 | 0.34974 | 0.34974 | 0.34974 | 0.98698 | -0.24775 | 0.99634 | -0.068939 | 48.0416
10 | 0.11818 | 0.030049 | -0.11793 | -0.029884 | 0.00025938 | 0.00016489 | 0.17833 | 0.17834 | 0.17834 | 0.98698 | -0.24775 | 0.98461 | -0.29342 | 24.4966
11 | 0.090128 | 0.022892 | -0.089895 | -0.022743 | 0.00023311 | 0.00014876 | 0.13599 | 0.13599 | 0.13599 | 0.98698 | -0.24775 | 0.98419 | -0.30164 | 37.3601
12 | -0.23382 | -0.06012 | 0.2346 | 0.060623 | 0.00078624 | 0.0005023 | 0.34974 | 0.34974 | 0.34974 | 0.99634 | -0.068939 | 1 | 0 | 48.0415
13 | 0.024026 | 0.0060428 | -0.024022 | -0.0060404 | 3.7767e-06 | 2.32e-06 | 0.036317 | 0.036317 | 0.036317 | 0.98461 | -0.29342 | 0.98444 | -0.29671 | 9.9772
14 | 0.0939 | 0.023841 | -0.093321 | -0.023472 | 0.00057838 | 0.0003692 | 0.14202 | 0.14202 | 0.14202 | 0.98461 | -0.29342 | 0.97799 | -0.42229 | 39.0161
15 | 0.089895 | 0.022743 | -0.089729 | -0.022637 | 0.0001665 | 0.00010626 | 0.13599 | 0.13599 | 0.13599 | 0.98419 | -0.30164 | 0.9822 | -0.34031 | 37.3601
16 | 0.008673 | 0.0021739 | -0.0086713 | -0.0021732 | 1.656e-06 | 7.4379e-07 | 0.013218 | 0.013218 | 0.013218 | 0.97638 | -0.45415 | 0.97618 | -0.45816 | 3.6313
17 | -0.053102 | -0.013326 | 0.053176 | 0.013373 | 7.4546e-05 | 4.7328e-05 | 0.080854 | 0.080854 | 0.080854 | 0.97735 | -0.43517 | 0.97885 | -0.40578 | 22.2126
18 | 0.024022 | 0.0060404 | -0.023993 | -0.0060225 | 2.9255e-05 | 1.7972e-05 | 0.036317 | 0.036317 | 0.036317 | 0.98444 | -0.29671 | 0.98313 | -0.32224 | 9.9772
19 | 0.034163 | 0.0086455 | -0.034024 | -0.0085581 | 0.00013918 | 8.7363e-05 | 0.05201 | 0.05201 | 0.05201 | 0.97799 | -0.42229 | 0.97364 | -0.50755 | 14.2886
20 | 0.085194 | 0.021501 | -0.084928 | -0.021331 | 0.00026621 | 0.00016983 | 0.12912 | 0.12912 | 0.12912 | 0.9822 | -0.34031 | 0.97885 | -0.40578 | 35.4729
21 | 0.141 | 0.036033 | -0.14006 | -0.035431 | 0.00094193 | 0.0006021 | 0.21006 | 0.21006 | 0.21006 | 1 | 0 | 0.99271 | -0.13914 | 57.7089
22 | 0.023993 | 0.0060225 | -0.023967 | -0.0060066 | 2.5777e-05 | 1.5837e-05 | 0.036317 | 0.036317 | 0.036317 | 0.98313 | -0.32224 | 0.98198 | -0.34479 | 9.9773
23 | -0.0058556 | -0.0014675 | 0.0058571 | 0.0014679 | 1.4957e-06 | 3.3188e-07 | 0.0089283 | 0.008928 | 0.0089283 | 0.97591 | -0.46352 | 0.97618 | -0.45816 | 2.4528
24 | -0.00076756 | -0.00019237 | 0.00076757 | 0.00019228 | 3.7712e-09 | -8.8152e-08 | 0.0011741 | 0.0011741 | 0.0011741 | 0.97277 | -0.52476 | 0.97277 | -0.52465 | 0.32256
25 | -0.00076757 | -0.00019228 | 0.00076757 | 0.00019219 | 3.7642e-09 | -8.7994e-08 | 0.0011741 | 0.0011741 | 0.0011741 | 0.97277 | -0.52465 | 0.97278 | -0.52455 | 0.32255
26 | -0.032071 | -0.0080588 | 0.032089 | 0.0080703 | 1.8218e-05 | 1.1409e-05 | 0.049065 | 0.049065 | 0.049065 | 0.97278 | -0.52455 | 0.97338 | -0.51266 | 13.4795
27 | 0.031303 | 0.0078667 | -0.031285 | -0.0078554 | 1.8044e-05 | 1.1288e-05 | 0.047891 | 0.047891 | 0.047891 | 0.97278 | -0.52455 | 0.97216 | -0.53663 | 13.1569
28 | -0.032089 | -0.0080703 | 0.032097 | 0.0080752 | 7.8257e-06 | 4.9007e-06 | 0.049065 | 0.049065 | 0.049065 | 0.97338 | -0.51266 | 0.97364 | -0.50755 | 13.4794
29 | 0.030828 | 0.0077408 | -0.030821 | -0.007736 | 7.645e-06 | 4.7793e-06 | 0.047192 | 0.047192 | 0.047192 | 0.97216 | -0.53663 | 0.9719 | -0.54183 | 12.9648
30 | 0.030081 | 0.0075507 | -0.03005 | -0.0075313 | 3.12e-05 | 1.9482e-05 | 0.04606 | 0.04606 | 0.04606 | 0.9719 | -0.54183 | 0.9708 | -0.5636 | 12.6538
31 | 0.078315 | 0.019696 | -0.078315 | -0.019696 | 5.8331e-07 | 3.7189e-07 | 0.11805 | 0.11805 | 0.11805 | 0.98741 | -0.24162 | 0.9874 | -0.24178 | 32.43
32 | -0.13625 | -0.034217 | 0.13692 | 0.034645 | 0.00066979 | 0.00042812 | 0.20536 | 0.20536 | 0.20536 | 0.98741 | -0.24162 | 0.99271 | -0.13914 | 56.4176
33 | 0.051275 | 0.012919 | -0.051093 | -0.012804 | 0.00018166 | 0.00011523 | 0.077296 | 0.077296 | 0.077296 | 0.9874 | -0.24178 | 0.98358 | -0.31613 | 21.2353
34 | 0.003136 | 0.00078556 | -0.0031358 | -0.0007857 | 1.4894e-07 | -1.3707e-07 | 0.0047005 | 0.0047006 | 0.0047006 | 0.99271 | -0.13914 | 0.99266 | -0.14014 | 1.2914
35 | 0.0011228 | 0.00027995 | -0.0011227 | -0.00028053 | 5.1661e-08 | -5.7318e-07 | 0.0016981 | 0.0016983 | 0.0016983 | 0.98358 | -0.31613 | 0.98353 | -0.3171 | 0.46657
36 | 0.0031358 | 0.0007857 | -0.0031356 | -0.00078587 | 1.7954e-07 | -1.6518e-07 | 0.0047006 | 0.0047007 | 0.0047007 | 0.99266 | -0.14014 | 0.99259 | -0.14134 | 1.2914
37 | 0.0011227 | 0.00028053 | -0.0011227 | -0.00028137 | 7.59e-08 | -8.4173e-07 | 0.0016983 | 0.0016986 | 0.0016986 | 0.98353 | -0.3171 | 0.98346 | -0.31852 | 0.46666

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40289 | 0.10308

## res_load
| p_mw | q_mvar
0 | 0.0097158 | 0.002435
1 | 0.013853 | 0.0034719
2 | 0.00021464 | 5.3793e-05
3 | 0.0020702 | 0.00051883
4 | 0.023473 | 0.0058828
5 | 0.0080429 | 0.0020158
6 | 0.010481 | 0.0026267
7 | 0.059158 | 0.014826
8 | 0.0045346 | 0.0011365
9 | 0.02563 | 0.0064236
10 | 0.023967 | 0.0060066
11 | 0.0058556 | 0.0014675
12 | 0.0028143 | 0.00070532
13 | 0.00076756 | 0.00019237
14 | 0.00045704 | 0.00011455
15 | 0.0019271 | 0.00048299
16 | 0.00073936 | 0.0001853
17 | 0.05794 | 0.014521
18 | 0.02704 | 0.0067768
19 | 0.04997 | 0.012524
20 | 0.0031356 | 0.00078587
21 | 0.0011227 | 0.00028137
22 | 0.031751 | 0.0079576
23 | 0.03005 | 0.0075313

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1