## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-282_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-282_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-282_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-282_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-282_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-282_0_4_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_2701-282_0_4_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_2701-282_0_4_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_2701-282_0_4_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_2701-282_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_2701-282_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2701-282_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2701-282_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2701-282_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2701-282_0_4_node_54 | 0.4 | n |  | TRUE
15 | bus_LV_2701-282_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2701-282_0_4_node_53 | 0.4 | n |  | TRUE
17 | bus_LV_2701-282_0_4_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_2701-282_0_4_node_52 | 0.4 | n |  | TRUE
19 | bus_LV_2701-282_0_4_node_47 | 0.4 | n |  | TRUE
20 | bus_LV_2701-282_0_4_node_51 | 0.4 | n |  | TRUE
21 | bus_LV_2701-282_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_2701-282_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2701-282_0_4_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_2701-282_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2701-282_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_2701-282_0_4_node_43 | 0.4 | n |  | TRUE
27 | bus_LV_2701-282_0_4_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_2701-282_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_2701-282_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_2701-282_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_2701-282_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_2701-282_0_4_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_2701-282_0_4_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_2701-282_0_4_node_48 | 0.4 | n |  | TRUE
35 | bus_LV_2701-282_0_4_node_49 | 0.4 | n |  | TRUE
36 | bus_LV_2701-282_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_2701-282_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_2701-282_0_4_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_2701-282_0_4_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_2701-282_0_4_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_2701-282_0_4_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_2701-282_0_4_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_2701-282_0_4_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_2701-282_0_4_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_2701-282_0_4_node_56 | 0.4 | n |  | TRUE
46 | bus_LV_2701-282_0_4_node_61 | 0.4 | n |  | TRUE
47 | bus_LV_2701-282_0_4_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_2701-282_0_4_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_2701-282_0_4_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_2701-282_0_4_node_55 | 0.4 | n |  | TRUE
51 | bus_LV_2701-282_0_4_node_59 | 0.4 | n |  | TRUE
52 | bus_LV_2701-282_0_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_2701-282_0_4_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_2701-282_0_4_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_2701-282_0_4_node_57 | 0.4 | n |  | TRUE
56 | bus_LV_2701-282_0_4_node_58 | 0.4 | n |  | TRUE
57 | bus_MV_559_0_node_36 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-282_0_4_load_0 | 0 | 0.025144 | 0.0063018 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-282_0_4_load_1 | 1 | 0.004596 | 0.0011519 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-282_0_4_load_2 | 2 | 0.0046006 | 0.001153 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-282_0_4_load_3 | 3 | 0.017532 | 0.0043941 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-282_0_4_load_4 | 4 | 0.0046014 | 0.0011532 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-282_0_4_load_15 | 5 | 0.0045984 | 0.0011525 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-282_0_4_load_12 | 7 | 0.023059 | 0.0057791 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-282_0_4_load_10 | 9 | 0.0016615 | 0.00041642 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-282_0_4_load_5 | 10 | 0.0040504 | 0.0010151 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-282_0_4_load_8 | 13 | 0.0022262 | 0.00055793 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-282_0_4_load_54 | 14 | 0.0052475 | 0.0013151 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-282_0_4_load_9 | 15 | 0.0016595 | 0.0004159 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-282_0_4_load_53 | 16 | 0.012419 | 0.0031125 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-282_0_4_load_50 | 17 | 0.0090305 | 0.0022632 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-282_0_4_load_52 | 18 | 0.0089724 | 0.0022487 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-282_0_4_load_47 | 19 | 0.0063893 | 0.0016013 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-282_0_4_load_51 | 20 | 0.028351 | 0.0071053 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-282_0_4_load_16 | 21 | 0.01169 | 0.0029299 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-282_0_4_load_17 | 22 | 0.0099356 | 0.0024901 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-282_0_4_load_18 | 23 | 0.0054894 | 0.0013758 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-282_0_4_load_19 | 24 | 0.0085254 | 0.0021367 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-282_0_4_load_43 | 26 | 0.0083322 | 0.0020882 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-282_0_4_load_31 | 27 | 0.0052829 | 0.001324 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-282_0_4_load_21 | 28 | 0.0025855 | 0.000648 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-282_0_4_load_22 | 29 | 0.0040539 | 0.001016 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-282_0_4_load_23 | 30 | 0.0019124 | 0.0004793 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-282_0_4_load_24 | 31 | 0.0034828 | 0.00087288 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-282_0_4_load_25 | 32 | 0.0024296 | 0.0006089 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-282_0_4_load_34 | 33 | 0.0026845 | 0.0006728 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-282_0_4_load_48 | 34 | 0.002423 | 0.00060726 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-282_0_4_load_49 | 35 | 0.0025305 | 0.0006342 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-282_0_4_load_26 | 36 | 0.014447 | 0.0036207 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-282_0_4_load_27 | 37 | 0.01072 | 0.0026866 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-282_0_4_load_30 | 40 | 0.0053541 | 0.0013419 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-282_0_4_load_40 | 41 | 0.0058656 | 0.0014701 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-282_0_4_load_37 | 43 | 0.005777 | 0.0014479 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-282_0_4_load_32 | 44 | 0.024994 | 0.006264 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-282_0_4_load_56 | 45 | 0.02209 | 0.0055362 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-282_0_4_load_61 | 46 | 0.012523 | 0.0031386 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-282_0_4_load_33 | 47 | 0.0078083 | 0.0019569 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-282_0_4_load_41 | 48 | 0.0050693 | 0.0012705 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2701-282_0_4_load_42 | 49 | 0.002715 | 0.00068045 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2701-282_0_4_load_55 | 50 | 0.034721 | 0.0087019 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2701-282_0_4_load_59 | 51 | 0.0071414 | 0.0017898 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2701-282_0_4_load_46 | 52 | 0.0036265 | 0.00090888 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2701-282_0_4_load_44 | 53 | 0.0066894 | 0.0016765 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2701-282_0_4_load_45 | 54 | 0.013232 | 0.0033162 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2701-282_0_4_load_57 | 55 | 0.015985 | 0.0040062 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2701-282_0_4_load_58 | 56 | 0.006934 | 0.0017378 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-282_0_4_line_0 |  | 0 | 1 | 0.0011326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-282_0_4_line_1 |  | 0 | 2 | 0.0062651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-282_0_4_line_2 |  | 1 | 3 | 0.019924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-282_0_4_line_3 |  | 2 | 4 | 0.0074035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-282_0_4_line_4 |  | 4 | 5 | 0.0074006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-282_0_4_line_5 |  | 5 | 9 | 0.007401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-282_0_4_line_6 |  | 6 | 7 | 0.025764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-282_0_4_line_7 |  | 6 | 8 | 0.010884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-282_0_4_line_8 |  | 8 | 17 | 0.016381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-282_0_4_line_9 |  | 8 | 18 | 0.029625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-282_0_4_line_10 |  | 9 | 15 | 0.0073989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-282_0_4_line_11 |  | 10 | 11 | 0.048018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-282_0_4_line_12 |  | 11 | 12 | 0.011248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-282_0_4_line_13 |  | 11 | 13 | 0.022605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-282_0_4_line_14 |  | 12 | 14 | 0.023882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-282_0_4_line_15 |  | 13 | 15 | 0.0082183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-282_0_4_line_16 |  | 14 | 16 | 0.014503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-282_0_4_line_17 |  | 16 | 25 | 0.021962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-282_0_4_line_18 |  | 17 | 19 | 0.028154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-282_0_4_line_19 |  | 18 | 20 | 0.02331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-282_0_4_line_20 |  | 19 | 54 | 0.01571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-282_0_4_line_21 |  | 20 | 25 | 0.02035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-282_0_4_line_22 |  | 21 | 22 | 0.0093572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2701-282_0_4_line_23 |  | 21 | 23 | 0.0010765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2701-282_0_4_line_24 |  | 22 | 24 | 0.010855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_2701-282_0_4_line_25 |  | 23 | 25 | 0.02852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2701-282_0_4_line_26 |  | 24 | 26 | 0.010822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2701-282_0_4_line_27 |  | 26 | 27 | 0.0041201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2701-282_0_4_line_28 |  | 27 | 38 | 0.012357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2701-282_0_4_line_29 |  | 28 | 29 | 0.0078401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-282_0_4_line_30 |  | 28 | 30 | 0.006464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-282_0_4_line_31 |  | 29 | 31 | 0.008493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-282_0_4_line_32 |  | 30 | 32 | 0.0062205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-282_0_4_line_33 |  | 31 | 33 | 0.0075292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-282_0_4_line_34 |  | 32 | 34 | 0.0076144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-282_0_4_line_35 |  | 34 | 35 | 0.0073722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-282_0_4_line_36 |  | 35 | 41 | 0.010206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-282_0_4_line_37 |  | 36 | 37 | 0.020154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_2701-282_0_4_line_38 |  | 36 | 38 | 0.0011459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2701-282_0_4_line_39 |  | 37 | 39 | 0.047848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2701-282_0_4_line_40 |  | 38 | 40 | 0.020239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2701-282_0_4_line_41 |  | 39 | 41 | 0.014721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-282_0_4_line_42 |  | 39 | 42 | 0.004616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-282_0_4_line_43 |  | 39 | 43 | 0.018181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-282_0_4_line_44 |  | 40 | 44 | 0.0071988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2701-282_0_4_line_45 |  | 42 | 45 | 0.020654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2701-282_0_4_line_46 |  | 42 | 46 | 0.013696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2701-282_0_4_line_47 |  | 44 | 47 | 0.0036003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2701-282_0_4_line_48 |  | 45 | 50 | 0.050675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2701-282_0_4_line_49 |  | 46 | 51 | 0.011405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2701-282_0_4_line_50 |  | 47 | 48 | 0.010878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2701-282_0_4_line_51 |  | 48 | 49 | 0.0081482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2701-282_0_4_line_52 |  | 49 | 52 | 0.0091796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2701-282_0_4_line_53 |  | 51 | 55 | 0.0025817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2701-282_0_4_line_54 |  | 52 | 53 | 0.0056474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2701-282_0_4_line_55 |  | 55 | 56 | 0.0061749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-282_0_4_trafo_30 | 0.63 MVA 20/0.4 kV | 57 | 40 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2612029.165 | 1267824.8388 | 2612030.0093 | 1267825.5938
1 | 2612029.165 | 1267824.8388 | 2612024.4949 | 1267820.6625
2 | 2612030.0093 | 1267825.5938 | 2612038.284 | 1267832.9935 | 2612039.4782 | 1267837.9105 | 2612042.0188 | 1267840.6865
3 | 2612024.4949 | 1267820.6625 | 2612018.9761 | 1267815.7274
4 | 2612013.4596 | 1267810.7942 | 2612018.9761 | 1267815.7274
5 | 2612013.4596 | 1267810.7942 | 2612007.9427 | 1267805.8608
6 | 2612068.0247 | 1267871.2474 | 2612060.5788 | 1267876.2247 | 2612048.8107 | 1267882.3606 | 2612046.1117 | 1267884.6457
7 | 2612076.4904 | 1267864.4042 | 2612075.8269 | 1267864.9811 | 2612070.6398 | 1267869.4959 | 2612068.0247 | 1267871.2474
8 | 2612076.4904 | 1267864.4042 | 2612077.8932 | 1267862.9728 | 2612088.1196 | 1267852.8683
9 | 2612076.4904 | 1267864.4042 | 2612056.702 | 1267842.3579
10 | 2612007.9427 | 1267805.8608 | 2612002.4275 | 1267800.9287
11 | 2611978.4649 | 1267781.5921 | 2611964.4428 | 1267827.5175
12 | 2611978.4649 | 1267781.5921 | 2611981.5724 | 1267770.7797
13 | 2611978.4649 | 1267781.5921 | 2611992.2247 | 1267791.8048 | 2611996.3014 | 1267795.4504
14 | 2611981.5724 | 1267770.7797 | 2611991.564 | 1267779.7951 | 2611993.4573 | 1267781.4667 | 2611999.5252 | 1267786.5231
15 | 2611996.3014 | 1267795.4504 | 2612002.4275 | 1267800.9287
16 | 2611999.5252 | 1267786.5231 | 2612010.6665 | 1267795.8072
17 | 2612027.5384 | 1267809.8667 | 2612010.6665 | 1267795.8072
18 | 2612088.1196 | 1267852.8683 | 2612094.9515 | 1267846.1179 | 2612104.3287 | 1267830.1127
19 | 2612041.1316 | 1267825.0109 | 2612056.702 | 1267842.3579
20 | 2612112.2701 | 1267816.5581 | 2612104.3287 | 1267830.1127
21 | 2612027.5384 | 1267809.8667 | 2612041.1316 | 1267825.0109
22 | 2612044.1567 | 1267785.3774 | 2612049.3953 | 1267777.624
23 | 2612044.1567 | 1267785.3774 | 2612043.5541 | 1267786.2694
24 | 2612049.3953 | 1267777.624 | 2612055.4726 | 1267768.6291
25 | 2612027.5384 | 1267809.8667 | 2612028.3233 | 1267808.812 | 2612043.5541 | 1267786.2694
26 | 2612061.5312 | 1267759.6621 | 2612055.4726 | 1267768.6291
27 | 2612063.8378 | 1267756.2481 | 2612061.5312 | 1267759.6621
28 | 2612070.7554 | 1267746.0095 | 2612063.8378 | 1267756.2481
29 | 2612152.305 | 1267718.5426 | 2612158.7396 | 1267723.0219
30 | 2612152.305 | 1267718.5426 | 2612146.9998 | 1267714.8496
31 | 2612158.7396 | 1267723.0219 | 2612165.71 | 1267727.8742
32 | 2612141.8945 | 1267711.2956 | 2612146.9998 | 1267714.8496
33 | 2612171.8894 | 1267732.1758 | 2612165.71 | 1267727.8742
34 | 2612141.8945 | 1267711.2956 | 2612135.6452 | 1267706.9453
35 | 2612135.6452 | 1267706.9453 | 2612129.5946 | 1267702.7334
36 | 2612121.2182 | 1267696.9024 | 2612129.5946 | 1267702.7334
37 | 2612071.3915 | 1267745.0564 | 2612082.5779 | 1267728.2922
38 | 2612070.7554 | 1267746.0095 | 2612071.3915 | 1267745.0564
39 | 2612109.1361 | 1267688.4917 | 2612082.5779 | 1267728.2922
40 | 2612070.7554 | 1267746.0095 | 2612087.4637 | 1267757.4309
41 | 2612109.1361 | 1267688.4917 | 2612121.2182 | 1267696.9024
42 | 2612111.7028 | 1267684.6498 | 2612109.1361 | 1267688.4917
43 | 2612109.1361 | 1267688.4917 | 2612094.0541 | 1267678.3392
44 | 2612087.4637 | 1267757.4309 | 2612093.4067 | 1267761.4934
45 | 2612111.7028 | 1267684.6498 | 2612128.7775 | 1267696.2714
46 | 2612111.7028 | 1267684.6498 | 2612114.8357 | 1267680.0196 | 2612119.3767 | 1267673.3056
47 | 2612096.3789 | 1267763.5251 | 2612093.4067 | 1267761.4934
48 | 2612170.6701 | 1267724.7849 | 2612128.7775 | 1267696.2714
49 | 2612125.766 | 1267663.8586 | 2612119.3767 | 1267673.3056
50 | 2612096.3789 | 1267763.5251 | 2612105.3592 | 1267769.6638
51 | 2612105.3592 | 1267769.6638 | 2612112.086 | 1267774.2621
52 | 2612112.086 | 1267774.2621 | 2612119.6642 | 1267779.4424
53 | 2612127.2124 | 1267661.72 | 2612125.766 | 1267663.8586
54 | 2612124.3264 | 1267782.6293 | 2612119.6642 | 1267779.4424
55 | 2612127.2124 | 1267661.72 | 2612130.6718 | 1267656.6052

## bus_geodata
| x | y | coords
0 | 2612029.165 | 1267824.8388
1 | 2612030.0093 | 1267825.5938
2 | 2612024.4949 | 1267820.6625
3 | 2612042.0188 | 1267840.6865
4 | 2612018.9761 | 1267815.7274
5 | 2612013.4596 | 1267810.7942
6 | 2612068.0247 | 1267871.2474
7 | 2612046.1117 | 1267884.6457
8 | 2612076.4904 | 1267864.4042
9 | 2612007.9427 | 1267805.8608
10 | 2611964.4428 | 1267827.5175
11 | 2611978.4649 | 1267781.5921
12 | 2611981.5724 | 1267770.7797
13 | 2611996.3014 | 1267795.4504
14 | 2611999.5252 | 1267786.5231
15 | 2612002.4275 | 1267800.9287
16 | 2612010.6665 | 1267795.8072
17 | 2612088.1196 | 1267852.8683
18 | 2612056.702 | 1267842.3579
19 | 2612104.3287 | 1267830.1127
20 | 2612041.1316 | 1267825.0109
21 | 2612044.1567 | 1267785.3774
22 | 2612049.3953 | 1267777.624
23 | 2612043.5541 | 1267786.2694
24 | 2612055.4726 | 1267768.6291
25 | 2612027.5385 | 1267809.8667
26 | 2612061.5312 | 1267759.6621
27 | 2612063.8378 | 1267756.2481
28 | 2612152.305 | 1267718.5426
29 | 2612158.7396 | 1267723.0219
30 | 2612146.9998 | 1267714.8496
31 | 2612165.71 | 1267727.8742
32 | 2612141.8945 | 1267711.2956
33 | 2612171.8894 | 1267732.1758
34 | 2612135.6452 | 1267706.9453
35 | 2612129.5946 | 1267702.7334
36 | 2612071.3915 | 1267745.0564
37 | 2612082.5779 | 1267728.2922
38 | 2612070.7554 | 1267746.0095
39 | 2612109.1361 | 1267688.4917
40 | 2612087.4637 | 1267757.4309
41 | 2612121.2182 | 1267696.9024
42 | 2612111.7028 | 1267684.6498
43 | 2612094.0541 | 1267678.3392
44 | 2612093.4067 | 1267761.4934
45 | 2612128.7775 | 1267696.2714
46 | 2612119.3767 | 1267673.3056
47 | 2612096.3789 | 1267763.5251
48 | 2612105.3592 | 1267769.6638
49 | 2612112.086 | 1267774.2621
50 | 2612170.6701 | 1267724.7849
51 | 2612125.766 | 1267663.8586
52 | 2612119.6642 | 1267779.4424
53 | 2612124.3264 | 1267782.6293
54 | 2612112.2701 | 1267816.5581
55 | 2612127.2124 | 1267661.72
56 | 2612130.6718 | 1267656.6052
57 | 2612070.7554 | 1267746.0095

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98333 | -0.32115 | 0.025144 | 0.0063018
1 | 0.9833 | -0.3216 | 0.004596 | 0.0011519
2 | 0.9836 | -0.31581 | 0.0046006 | 0.001153
3 | 0.98298 | -0.3279 | 0.017532 | 0.0043941
4 | 0.98396 | -0.30889 | 0.0046014 | 0.0011532
5 | 0.98434 | -0.30137 | 0.0045984 | 0.0011525
6 | 0.98755 | -0.23923 | 0 | 0
7 | 0.98701 | -0.24985 | 0.023059 | 0.0057791
8 | 0.98778 | -0.23474 | 0 | 0
9 | 0.98476 | -0.29325 | 0.0016615 | 0.00041642
10 | 0.98688 | -0.25191 | 0.0040504 | 0.0010151
11 | 0.98706 | -0.24843 | 0 | 0
12 | 0.98779 | -0.23422 | 0 | 0
13 | 0.98567 | -0.27541 | 0.0022262 | 0.00055793
14 | 0.98935 | -0.20412 | 0.0052475 | 0.0013151
15 | 0.98519 | -0.28491 | 0.0016595 | 0.0004159
16 | 0.99037 | -0.18453 | 0.012419 | 0.0031125
17 | 0.98735 | -0.24313 | 0.0090305 | 0.0022632
18 | 0.98919 | -0.20741 | 0.0089724 | 0.0022487
19 | 0.98684 | -0.25301 | 0.0063893 | 0.0016013
20 | 0.99049 | -0.18225 | 0.028351 | 0.0071053
21 | 0.99454 | -0.10427 | 0.01169 | 0.0029299
22 | 0.9951 | -0.093585 | 0.0099356 | 0.0024901
23 | 0.99448 | -0.10543 | 0.0054894 | 0.0013758
24 | 0.99578 | -0.080569 | 0.0085254 | 0.0021367
25 | 0.99215 | -0.15011 | 0 | 0
26 | 0.99648 | -0.067071 | 0.0083322 | 0.0020882
27 | 0.99676 | -0.061736 | 0.0052829 | 0.001324
28 | 0.98939 | -0.20373 | 0.0025855 | 0.000648
29 | 0.98932 | -0.20515 | 0.0040539 | 0.001016
30 | 0.98947 | -0.20225 | 0.0019124 | 0.0004793
31 | 0.98927 | -0.20609 | 0.0034828 | 0.00087288
32 | 0.98955 | -0.20062 | 0.0024296 | 0.0006089
33 | 0.98925 | -0.20645 | 0.0026845 | 0.0006728
34 | 0.98967 | -0.1983 | 0.002423 | 0.00060726
35 | 0.9898 | -0.19573 | 0.0025305 | 0.0006342
36 | 0.99756 | -0.046433 | 0.014447 | 0.0036207
37 | 0.99623 | -0.071858 | 0.01072 | 0.0026866
38 | 0.99762 | -0.045374 | 0 | 0
39 | 0.99039 | -0.1844 | 0 | 0
40 | 1 | 0 | -0.44137 | -0.1117
41 | 0.99001 | -0.19172 | 0.0058656 | 0.0014701
42 | 0.98997 | -0.19255 | 0 | 0
43 | 0.99029 | -0.18626 | 0.005777 | 0.0014479
44 | 0.99967 | -0.0063891 | 0.024994 | 0.006264
45 | 0.98889 | -0.21345 | 0.02209 | 0.0055362
46 | 0.98943 | -0.20293 | 0.012523 | 0.0031386
47 | 0.99958 | -0.0080161 | 0.0078083 | 0.0019569
48 | 0.9994 | -0.011451 | 0.0050693 | 0.0012705
49 | 0.99931 | -0.013305 | 0.002715 | 0.00068045
50 | 0.98728 | -0.24486 | 0.034721 | 0.0087019
51 | 0.98912 | -0.20904 | 0.0071414 | 0.0017898
52 | 0.99922 | -0.014958 | 0.0036265 | 0.00090888
53 | 0.99919 | -0.015617 | 0.0066894 | 0.0016765
54 | 0.98665 | -0.25673 | 0.013232 | 0.0033162
55 | 0.98906 | -0.21009 | 0.015985 | 0.0040062
56 | 0.98903 | -0.21086 | 0.006934 | 0.0017378
57 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.022134 | 0.0055493 | -0.022134 | -0.005549 | 4.7652e-07 | 2.906e-07 | 0.033495 | 0.033495 | 0.033495 | 0.98333 | -0.32115 | 0.9833 | -0.3216 | 9.202
1 | -0.047279 | -0.011851 | 0.047291 | 0.011859 | 1.2026e-05 | 7.6171e-06 | 0.071545 | 0.071545 | 0.071545 | 0.98333 | -0.32115 | 0.9836 | -0.31581 | 19.6552
2 | 0.017538 | 0.0043972 | -0.017532 | -0.0043941 | 5.2628e-06 | 3.1155e-06 | 0.02654 | 0.02654 | 0.02654 | 0.9833 | -0.3216 | 0.98298 | -0.3279 | 7.2913
3 | -0.051891 | -0.013012 | 0.051908 | 0.013023 | 1.711e-05 | 1.0857e-05 | 0.078505 | 0.078505 | 0.078505 | 0.9836 | -0.31581 | 0.98396 | -0.30889 | 21.5672
4 | -0.05651 | -0.014176 | 0.05653 | 0.014189 | 2.027e-05 | 1.2879e-05 | 0.085463 | 0.085463 | 0.085463 | 0.98396 | -0.30889 | 0.98434 | -0.30137 | 23.4789
5 | -0.061128 | -0.015341 | 0.061152 | 0.015356 | 2.3703e-05 | 1.5076e-05 | 0.092414 | 0.092414 | 0.092414 | 0.98434 | -0.30137 | 0.98476 | -0.29325 | 25.3886
6 | 0.023071 | 0.0057862 | -0.023059 | -0.0057791 | 1.1676e-05 | 7.1433e-06 | 0.034764 | 0.034764 | 0.034764 | 0.98755 | -0.23923 | 0.98701 | -0.24985 | 9.5505
7 | -0.023071 | -0.0057862 | 0.023076 | 0.0057893 | 4.9325e-06 | 3.0175e-06 | 0.034764 | 0.034764 | 0.034764 | 0.98755 | -0.23923 | 0.98778 | -0.23474 | 9.5504
8 | 0.028675 | 0.0071947 | -0.028663 | -0.0071876 | 1.1463e-05 | 7.1269e-06 | 0.043199 | 0.043199 | 0.043199 | 0.98778 | -0.23474 | 0.98735 | -0.24313 | 11.8678
9 | -0.05175 | -0.012984 | 0.051818 | 0.013027 | 6.7523e-05 | 4.2835e-05 | 0.077962 | 0.077962 | 0.077962 | 0.98778 | -0.23474 | 0.98919 | -0.20741 | 21.4182
10 | -0.062814 | -0.015773 | 0.062839 | 0.015789 | 2.5001e-05 | 1.5907e-05 | 0.094925 | 0.094925 | 0.094925 | 0.98476 | -0.29325 | 0.98519 | -0.28491 | 26.0783
11 | -0.0040504 | -0.0010151 | 0.0040511 | 0.0010149 | 6.716e-07 | -1.8384e-07 | 0.0061072 | 0.006107 | 0.0061072 | 0.98688 | -0.25191 | 0.98706 | -0.24843 | 1.6778
12 | -0.070891 | -0.017851 | 0.070939 | 0.017881 | 4.8201e-05 | 3.0705e-05 | 0.1069 | 0.1069 | 0.1069 | 0.98706 | -0.24843 | 0.98779 | -0.23422 | 29.3679
13 | 0.06684 | 0.016836 | -0.066753 | -0.016781 | 8.6116e-05 | 5.4826e-05 | 0.10079 | 0.10079 | 0.10079 | 0.98706 | -0.24843 | 0.98567 | -0.27541 | 27.6902
14 | -0.070939 | -0.017881 | 0.071041 | 0.017947 | 0.00010234 | 6.5192e-05 | 0.1069 | 0.1069 | 0.1069 | 0.98779 | -0.23422 | 0.98935 | -0.20412 | 29.3679
15 | 0.064527 | 0.016223 | -0.064498 | -0.016204 | 2.9256e-05 | 1.8619e-05 | 0.097431 | 0.097432 | 0.097432 | 0.98567 | -0.27541 | 0.98519 | -0.28491 | 26.7669
16 | -0.076289 | -0.019262 | 0.07636 | 0.019307 | 7.1663e-05 | 4.5678e-05 | 0.11479 | 0.11479 | 0.11479 | 0.98935 | -0.20412 | 0.99037 | -0.18453 | 31.5361
17 | -0.08878 | -0.02242 | 0.088926 | 0.022514 | 0.00014667 | 9.3587e-05 | 0.13345 | 0.13345 | 0.13345 | 0.99037 | -0.18453 | 0.99215 | -0.15011 | 36.6624
18 | 0.019633 | 0.0049244 | -0.019623 | -0.0049188 | 9.2437e-06 | 5.5561e-06 | 0.029589 | 0.029589 | 0.029589 | 0.98735 | -0.24313 | 0.98684 | -0.25301 | 8.129
19 | -0.06079 | -0.015276 | 0.060863 | 0.015322 | 7.3119e-05 | 4.6496e-05 | 0.091459 | 0.091459 | 0.091459 | 0.98919 | -0.20741 | 0.99049 | -0.18225 | 25.1261
20 | 0.013234 | 0.0033175 | -0.013232 | -0.0033162 | 2.3459e-06 | 1.3007e-06 | 0.019955 | 0.019955 | 0.019955 | 0.98684 | -0.25301 | 0.98665 | -0.25673 | 5.4822
21 | -0.089214 | -0.022427 | 0.089351 | 0.022515 | 0.00013713 | 8.75e-05 | 0.13405 | 0.13405 | 0.13405 | 0.99049 | -0.18225 | 0.99215 | -0.15011 | 36.827
22 | -0.19585 | -0.049585 | 0.19595 | 0.049649 | 0.00010055 | 6.399e-05 | 0.29321 | 0.29321 | 0.29321 | 0.99454 | -0.10427 | 0.9951 | -0.093585 | 26.8503
23 | 0.18416 | 0.046655 | -0.18415 | -0.046648 | 1.0229e-05 | 6.5047e-06 | 0.27571 | 0.27571 | 0.27571 | 0.99454 | -0.10427 | 0.99448 | -0.10543 | 25.2486
24 | -0.20589 | -0.052139 | 0.20601 | 0.052221 | 0.00012878 | 8.1993e-05 | 0.30806 | 0.30806 | 0.30806 | 0.9951 | -0.093585 | 0.99578 | -0.080569 | 28.2108
25 | 0.17866 | 0.045273 | -0.17828 | -0.045028 | 0.00038265 | 0.00024416 | 0.2675 | 0.2675 | 0.2675 | 0.99448 | -0.10543 | 0.99215 | -0.15011 | 36.7446
26 | -0.21454 | -0.054358 | 0.21468 | 0.054446 | 0.00013922 | 8.8675e-05 | 0.3208 | 0.3208 | 0.3208 | 0.99578 | -0.080569 | 0.99648 | -0.067071 | 29.3774
27 | -0.22301 | -0.056534 | 0.22307 | 0.056571 | 5.7193e-05 | 3.6442e-05 | 0.33324 | 0.33324 | 0.33324 | 0.99648 | -0.067071 | 0.99676 | -0.061736 | 30.5168
28 | -0.22835 | -0.057895 | 0.22853 | 0.058009 | 0.00017974 | 0.00011455 | 0.34113 | 0.34113 | 0.34113 | 0.99676 | -0.061736 | 0.99762 | -0.045374 | 31.239
29 | 0.010222 | 0.002562 | -0.010222 | -0.0025617 | 6.9491e-07 | 3.4407e-07 | 0.015374 | 0.015374 | 0.015374 | 0.98939 | -0.20373 | 0.98932 | -0.20515 | 4.2236
30 | -0.012808 | -0.00321 | 0.012809 | 0.0032105 | 8.9943e-07 | 4.9261e-07 | 0.019263 | 0.019263 | 0.019263 | 0.98939 | -0.20373 | 0.98947 | -0.20225 | 5.2919
31 | 0.0061677 | 0.0015457 | -0.0061674 | -0.0015456 | 2.7408e-07 | 6.6361e-08 | 0.0092766 | 0.0092767 | 0.0092767 | 0.98932 | -0.20515 | 0.98927 | -0.20609 | 2.5485
32 | -0.014721 | -0.0036898 | 0.014722 | 0.0036905 | 1.1433e-06 | 6.518e-07 | 0.022139 | 0.022139 | 0.022139 | 0.98947 | -0.20225 | 0.98955 | -0.20062 | 6.082
33 | 0.0026845 | 0.00067273 | -0.0026845 | -0.0006728 | 4.6036e-08 | -6.7204e-08 | 0.0040379 | 0.004038 | 0.004038 | 0.98927 | -0.20609 | 0.98925 | -0.20645 | 1.1093
34 | -0.017152 | -0.0042994 | 0.017154 | 0.0043005 | 1.8995e-06 | 1.1178e-06 | 0.025792 | 0.025792 | 0.025792 | 0.98955 | -0.20062 | 0.98967 | -0.1983 | 7.0857
35 | -0.019577 | -0.0049078 | 0.019579 | 0.0049092 | 2.3953e-06 | 1.4382e-06 | 0.029435 | 0.029435 | 0.029435 | 0.98967 | -0.1983 | 0.9898 | -0.19573 | 8.0865
36 | -0.02211 | -0.0055434 | 0.022114 | 0.005546 | 4.2285e-06 | 2.5751e-06 | 0.033239 | 0.033239 | 0.033239 | 0.9898 | -0.19573 | 0.99001 | -0.19172 | 9.1316
37 | 0.14496 | 0.036753 | -0.14478 | -0.036641 | 0.00017692 | 0.0001127 | 0.21637 | 0.21637 | 0.21637 | 0.99756 | -0.046433 | 0.99623 | -0.071858 | 29.7218
38 | -0.1594 | -0.040374 | 0.15941 | 0.040379 | 8.1081e-06 | 5.1443e-06 | 0.23792 | 0.23792 | 0.23792 | 0.99756 | -0.046433 | 0.99762 | -0.045374 | 21.7879
39 | 0.13406 | 0.033954 | -0.13334 | -0.033493 | 0.00072033 | 0.00046039 | 0.20036 | 0.20036 | 0.20036 | 0.99623 | -0.071858 | 0.99039 | -0.1844 | 55.0449
40 | -0.38794 | -0.098389 | 0.38879 | 0.098931 | 0.00084828 | 0.0005421 | 0.57905 | 0.57905 | 0.57905 | 0.99762 | -0.045374 | 1 | 0 | 53.0269
41 | 0.027989 | 0.0070221 | -0.027979 | -0.007016 | 9.7638e-06 | 6.0595e-06 | 0.042055 | 0.042055 | 0.042055 | 0.99039 | -0.1844 | 0.99001 | -0.19172 | 11.5536
42 | 0.099573 | 0.025023 | -0.099534 | -0.024999 | 3.8754e-05 | 2.4743e-05 | 0.14963 | 0.14963 | 0.14963 | 0.99039 | -0.1844 | 0.98997 | -0.19255 | 41.1065
43 | 0.0057775 | 0.001448 | -0.005777 | -0.0014479 | 5.1373e-07 | 9.4853e-08 | 0.0086805 | 0.0086806 | 0.0086806 | 0.99039 | -0.1844 | 0.99029 | -0.18626 | 2.3848
44 | 0.050925 | 0.012771 | -0.050909 | -0.012761 | 1.5503e-05 | 9.8272e-06 | 0.07578 | 0.07578 | 0.07578 | 1 | 0 | 0.99967 | -0.0063891 | 20.8187
45 | 0.056919 | 0.014307 | -0.056863 | -0.014271 | 5.6714e-05 | 3.6032e-05 | 0.08557 | 0.08557 | 0.08557 | 0.98997 | -0.19255 | 0.98889 | -0.21345 | 23.5082
46 | 0.042615 | 0.010692 | -0.042593 | -0.010679 | 2.1075e-05 | 1.3312e-05 | 0.064058 | 0.064058 | 0.064058 | 0.98997 | -0.19255 | 0.98943 | -0.20293 | 17.5983
47 | 0.025916 | 0.0064974 | -0.025914 | -0.0064961 | 2.0091e-06 | 1.2386e-06 | 0.038576 | 0.038576 | 0.038576 | 0.99967 | -0.0063891 | 0.99958 | -0.0080161 | 10.5979
48 | 0.034773 | 0.0087345 | -0.034721 | -0.0087019 | 5.2041e-05 | 3.2657e-05 | 0.052331 | 0.052331 | 0.052331 | 0.98889 | -0.21345 | 0.98728 | -0.24486 | 14.3767
49 | 0.03007 | 0.00754 | -0.030062 | -0.0075346 | 8.7471e-06 | 5.4517e-06 | 0.045224 | 0.045224 | 0.045224 | 0.98943 | -0.20293 | 0.98912 | -0.20904 | 12.4243
50 | 0.018105 | 0.0045392 | -0.018102 | -0.0045374 | 2.9634e-06 | 1.754e-06 | 0.026953 | 0.026953 | 0.026953 | 0.99958 | -0.0080161 | 0.9994 | -0.011451 | 7.4046
51 | 0.013033 | 0.0032669 | -0.013032 | -0.0032663 | 1.1506e-06 | 6.2963e-07 | 0.019405 | 0.019405 | 0.019405 | 0.9994 | -0.011451 | 0.99931 | -0.013305 | 5.3311
52 | 0.010317 | 0.0025859 | -0.010316 | -0.0025855 | 8.1241e-07 | 3.9969e-07 | 0.015362 | 0.015362 | 0.015362 | 0.99931 | -0.013305 | 0.99922 | -0.014958 | 4.2205
53 | 0.02292 | 0.0057448 | -0.022919 | -0.0057441 | 1.1511e-06 | 7.0355e-07 | 0.034481 | 0.034481 | 0.034481 | 0.98912 | -0.20904 | 0.98906 | -0.21009 | 9.4728
54 | 0.0066896 | 0.0016766 | -0.0066894 | -0.0016765 | 2.1017e-07 | 6.0538e-08 | 0.009962 | 0.0099621 | 0.0099621 | 0.99922 | -0.014958 | 0.99919 | -0.015617 | 2.7368
55 | 0.0069343 | 0.0017379 | -0.006934 | -0.0017378 | 2.5202e-07 | 8.2047e-08 | 0.010432 | 0.010432 | 0.010432 | 0.98906 | -0.21009 | 0.98903 | -0.21086 | 2.8661

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44672 | 0.11304

## res_load
| p_mw | q_mvar
0 | 0.025144 | 0.0063018
1 | 0.004596 | 0.0011519
2 | 0.0046006 | 0.001153
3 | 0.017532 | 0.0043941
4 | 0.0046014 | 0.0011532
5 | 0.0045984 | 0.0011525
6 | 0.023059 | 0.0057791
7 | 0.0016615 | 0.00041642
8 | 0.0040504 | 0.0010151
9 | 0.0022262 | 0.00055793
10 | 0.0052475 | 0.0013151
11 | 0.0016595 | 0.0004159
12 | 0.012419 | 0.0031125
13 | 0.0090305 | 0.0022632
14 | 0.0089724 | 0.0022487
15 | 0.0063893 | 0.0016013
16 | 0.028351 | 0.0071053
17 | 0.01169 | 0.0029299
18 | 0.0099356 | 0.0024901
19 | 0.0054894 | 0.0013758
20 | 0.0085254 | 0.0021367
21 | 0.0083322 | 0.0020882
22 | 0.0052829 | 0.001324
23 | 0.0025855 | 0.000648
24 | 0.0040539 | 0.001016
25 | 0.0019124 | 0.0004793
26 | 0.0034828 | 0.00087288
27 | 0.0024296 | 0.0006089
28 | 0.0026845 | 0.0006728
29 | 0.002423 | 0.00060726
30 | 0.0025305 | 0.0006342
31 | 0.014447 | 0.0036207
32 | 0.01072 | 0.0026866
33 | 0.0053541 | 0.0013419
34 | 0.0058656 | 0.0014701
35 | 0.005777 | 0.0014479
36 | 0.024994 | 0.006264
37 | 0.02209 | 0.0055362
38 | 0.012523 | 0.0031386
39 | 0.0078083 | 0.0019569
40 | 0.0050693 | 0.0012705
41 | 0.002715 | 0.00068045
42 | 0.034721 | 0.0087019
43 | 0.0071414 | 0.0017898
44 | 0.0036265 | 0.00090888
45 | 0.0066894 | 0.0016765
46 | 0.013232 | 0.0033162
47 | 0.015985 | 0.0040062
48 | 0.006934 | 0.0017378

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1