## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-283_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-283_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-283_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-283_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2701-283_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_2701-283_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_2701-283_0_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_2701-283_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2701-283_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2701-283_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_2701-283_0_4_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_2701-283_0_4_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_2701-283_0_4_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_2701-283_0_4_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_2701-283_0_4_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_2701-283_0_4_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_2701-283_0_4_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_2701-283_0_4_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_2701-283_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2701-283_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2701-283_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2701-283_0_4_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_2701-283_0_4_node_31 | 0.4 | n |  | TRUE
23 | bus_LV_2701-283_0_4_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_2701-283_0_4_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_2701-283_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_2701-283_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_2701-283_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_2701-283_0_4_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_2701-283_0_4_node_32 | 0.4 | n |  | TRUE
30 | bus_MV_561_0_node_87 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-283_0_4_load_0 | 0 | 0.013516 | 0.0033873 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-283_0_4_load_1 | 1 | 0.048439 | 0.01214 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-283_0_4_load_2 | 2 | 0.023414 | 0.0058681 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-283_0_4_load_5 | 7 | 0.026243 | 0.006577 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-283_0_4_load_9 | 9 | 0.0073765 | 0.0018487 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-283_0_4_load_16 | 11 | 0.0090397 | 0.0022656 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-283_0_4_load_34 | 12 | 0.02133 | 0.0053459 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-283_0_4_load_24 | 14 | 0.015098 | 0.0037839 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-283_0_4_load_28 | 15 | 0.017699 | 0.0044357 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-283_0_4_load_27 | 16 | 0.024835 | 0.0062243 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-283_0_4_load_25 | 17 | 0.071985 | 0.018041 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-283_0_4_load_12 | 18 | 0.041444 | 0.010387 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-283_0_4_load_31 | 22 | 0.061502 | 0.015414 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-283_0_4_load_33 | 23 | 0.019064 | 0.004778 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-283_0_4_load_29 | 24 | 0.061047 | 0.0153 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-283_0_4_load_18 | 25 | 0.018323 | 0.0045922 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-283_0_4_load_19 | 26 | 0.024361 | 0.0061053 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-283_0_4_load_30 | 28 | 0.0081632 | 0.0020459 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-283_0_4_load_32 | 29 | 0.056129 | 0.014067 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-283_0_4_line_0 |  | 0 | 1 | 0.014846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-283_0_4_line_1 |  | 0 | 2 | 0.0095511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-283_0_4_line_2 |  | 2 | 3 | 0.013767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-283_0_4_line_3 |  | 3 | 4 | 0.028714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-283_0_4_line_4 |  | 4 | 8 | 0.004478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-283_0_4_line_5 |  | 4 | 9 | 0.004069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-283_0_4_line_6 |  | 4 | 7 | 0.020696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-283_0_4_line_7 |  | 5 | 6 | 0.031645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2701-283_0_4_line_8 |  | 5 | 7 | 0.026332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2701-283_0_4_line_9 |  | 6 | 13 | 0.017878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-283_0_4_line_10 |  | 6 | 14 | 0.018806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2701-283_0_4_line_11 |  | 8 | 12 | 0.000822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-283_0_4_line_12 |  | 8 | 10 | 0.026647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-283_0_4_line_13 |  | 10 | 11 | 0.0099238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-283_0_4_line_14 |  | 13 | 15 | 0.025204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-283_0_4_line_15 |  | 13 | 16 | 0.022619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-283_0_4_line_16 |  | 14 | 17 | 0.0096903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2701-283_0_4_line_17 |  | 17 | 27 | 0.010542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2701-283_0_4_line_18 |  | 18 | 19 | 0.057207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-283_0_4_line_19 |  | 19 | 20 | 0.03185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-283_0_4_line_20 |  | 20 | 21 | 0.028432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2701-283_0_4_line_21 |  | 20 | 22 | 0.042145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2701-283_0_4_line_22 |  | 21 | 23 | 0.067405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_2701-283_0_4_line_23 |  | 22 | 24 | 0.0067437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2701-283_0_4_line_24 |  | 23 | 27 | 0.015364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_2701-283_0_4_line_25 |  | 24 | 28 | 0.01813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2701-283_0_4_line_26 |  | 25 | 26 | 0.011622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-283_0_4_line_27 |  | 26 | 27 | 0.022018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-283_0_4_line_28 |  | 28 | 29 | 0.0046673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-283_0_4_trafo_32 | 0.63 MVA 20/0.4 kV | 30 | 29 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2611625.3158 | 1267876.8797 | 2611611.692 | 1267870.9822
1 | 2611625.3158 | 1267876.8797 | 2611625.3158 | 1267876.8797 | 2611631.5892 | 1267878.582 | 2611634.5331 | 1267879.3827
2 | 2611647.9356 | 1267882.528 | 2611635.6662 | 1267879.6908 | 2611634.5331 | 1267879.3827
3 | 2611647.9356 | 1267882.528 | 2611646.447 | 1267885.5939 | 2611645.2076 | 1267888.171 | 2611641.5124 | 1267895.8358 | 2611639.3663 | 1267900.2903 | 2611635.5872 | 1267908.4664
4 | 2611635.5872 | 1267908.4664 | 2611636.7072 | 1267909.1913 | 2611636.9853 | 1267909.3809 | 2611639.3228 | 1267910.9532
5 | 2611632.0838 | 1267906.5916 | 2611632.7461 | 1267906.5706 | 2611633.9938 | 1267907.407 | 2611634.1591 | 1267907.5185 | 2611635.5872 | 1267908.4664
6 | 2611635.5872 | 1267908.4664 | 2611632.5162 | 1267912.5188 | 2611622.5988 | 1267924.5755
7 | 2611584.6245 | 1267968.42 | 2611605.871 | 1267944.9116
8 | 2611605.871 | 1267944.9116 | 2611622.5988 | 1267924.5755
9 | 2611573.1433 | 1267982.1517 | 2611584.6245 | 1267968.42
10 | 2611584.6245 | 1267968.42 | 2611586.0522 | 1267969.5792 | 2611598.6964 | 1267980.8928
11 | 2611638.8248 | 1267911.6083 | 2611639.3228 | 1267910.9532
12 | 2611663.0354 | 1267904.2284 | 2611658.0195 | 1267902.2282 | 2611652.1859 | 1267902.6615 | 2611646.793 | 1267904.8747 | 2611639.3228 | 1267910.9532
13 | 2611663.0354 | 1267904.2284 | 2611672.4491 | 1267907.369
14 | 2611573.1433 | 1267982.1517 | 2611571.6776 | 1267981.1704 | 2611566.3697 | 1267978.4026 | 2611550.2547 | 1267971.6992
15 | 2611573.1433 | 1267982.1517 | 2611565.1352 | 1267994.0111 | 2611561.247 | 1268001.3545
16 | 2611605.9179 | 1267987.3543 | 2611598.6964 | 1267980.8928
17 | 2611613.7744 | 1267994.384 | 2611605.9179 | 1267987.3543
18 | 2611717.5232 | 1267973.1284 | 2611665.5682 | 1267949.1842
19 | 2611703.0927 | 1268001.5421 | 2611717.5232 | 1267973.1284
20 | 2611689.9404 | 1268026.7672 | 2611693.3621 | 1268020.4584 | 2611703.0927 | 1268001.5421
21 | 2611703.0927 | 1268001.5421 | 2611664.7656 | 1267984.0134
22 | 2611689.9404 | 1268026.7672 | 2611627.7862 | 1268000.6853
23 | 2611664.7656 | 1267984.0134 | 2611658.6329 | 1267981.2086
24 | 2611613.7744 | 1267994.384 | 2611627.0609 | 1268000.3809 | 2611627.7862 | 1268000.6853
25 | 2611658.6329 | 1267981.2086 | 2611651.2557 | 1267977.8347 | 2611642.146 | 1267973.6678
26 | 2611601.5524 | 1268012.6163 | 2611596.6691 | 1268023.1629
27 | 2611613.7744 | 1267994.384 | 2611606.3726 | 1268004.0097 | 2611602.6577 | 1268010.229 | 2611601.5524 | 1268012.6163
28 | 2611637.9017 | 1267971.7264 | 2611642.146 | 1267973.6678

## bus_geodata
| x | y | coords
0 | 2611625.3159 | 1267876.8797
1 | 2611611.692 | 1267870.9822
2 | 2611634.5331 | 1267879.3827
3 | 2611647.9356 | 1267882.528
4 | 2611635.5872 | 1267908.4664
5 | 2611605.871 | 1267944.9116
6 | 2611584.6245 | 1267968.42
7 | 2611622.5988 | 1267924.5755
8 | 2611639.3228 | 1267910.9532
9 | 2611632.0838 | 1267906.5916
10 | 2611663.0354 | 1267904.2284
11 | 2611672.4491 | 1267907.369
12 | 2611638.8248 | 1267911.6083
13 | 2611573.1433 | 1267982.1517
14 | 2611598.6964 | 1267980.8928
15 | 2611550.2547 | 1267971.6992
16 | 2611561.247 | 1268001.3545
17 | 2611605.9179 | 1267987.3543
18 | 2611665.5682 | 1267949.1842
19 | 2611717.5232 | 1267973.1284
20 | 2611703.0927 | 1268001.5421
21 | 2611689.9404 | 1268026.7672
22 | 2611664.7656 | 1267984.0134
23 | 2611627.7862 | 1268000.6853
24 | 2611658.6329 | 1267981.2086
25 | 2611596.6691 | 1268023.1629
26 | 2611601.5524 | 1268012.6163
27 | 2611613.7744 | 1267994.384
28 | 2611642.146 | 1267973.6678
29 | 2611637.9017 | 1267971.7264
30 | 2611703.0927 | 1268001.5421

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97299 | -0.52151 | 0.013516 | 0.0033873
1 | 0.97232 | -0.53476 | 0.048439 | 0.01214
2 | 0.97354 | -0.51062 | 0.023414 | 0.0058681
3 | 0.97464 | -0.48903 | 0 | 0
4 | 0.97692 | -0.44416 | 0 | 0
5 | 0.98112 | -0.36207 | 0 | 0
6 | 0.98222 | -0.3407 | 0 | 0
7 | 0.9793 | -0.39774 | 0.026243 | 0.006577
8 | 0.9768 | -0.44665 | 0 | 0
9 | 0.97689 | -0.44471 | 0.0073765 | 0.0018487
10 | 0.97657 | -0.45105 | 0 | 0
11 | 0.97649 | -0.45269 | 0.0090397 | 0.0022656
12 | 0.97678 | -0.44697 | 0.02133 | 0.0053459
13 | 0.98152 | -0.35444 | 0 | 0
14 | 0.98306 | -0.32441 | 0.015098 | 0.0037839
15 | 0.98111 | -0.36252 | 0.017699 | 0.0044357
16 | 0.981 | -0.36461 | 0.024835 | 0.0062243
17 | 0.98353 | -0.31537 | 0.071985 | 0.018041
18 | 0.98954 | -0.19996 | 0.041444 | 0.010387
19 | 0.99171 | -0.15785 | 0 | 0
20 | 0.99292 | -0.13448 | 0 | 0
21 | 0.99067 | -0.1774 | 0 | 0
22 | 0.99665 | -0.063557 | 0.061502 | 0.015414
23 | 0.98535 | -0.27992 | 0.019064 | 0.004778
24 | 0.99734 | -0.05044 | 0.061047 | 0.0153
25 | 0.98315 | -0.32289 | 0.018323 | 0.0045922
26 | 0.98334 | -0.31905 | 0.024361 | 0.0061053
27 | 0.98421 | -0.30213 | 0 | 0
28 | 0.99945 | -0.010437 | 0.0081632 | 0.0020459
29 | 1 | 0 | -0.52181 | -0.13318
30 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.04847 | 0.012159 | -0.048439 | -0.01214 | 3.0593e-05 | 1.9395e-05 | 0.074131 | 0.074131 | 0.074131 | 0.97299 | -0.52151 | 0.97232 | -0.53476 | 20.3656
1 | -0.061986 | -0.015547 | 0.062018 | 0.015567 | 3.2189e-05 | 2.0482e-05 | 0.0948 | 0.0948 | 0.0948 | 0.97299 | -0.52151 | 0.97354 | -0.51062 | 26.044
2 | -0.085432 | -0.021435 | 0.08552 | 0.021492 | 8.8041e-05 | 5.6175e-05 | 0.13059 | 0.13059 | 0.13059 | 0.97354 | -0.51062 | 0.97464 | -0.48903 | 35.8757
3 | -0.08552 | -0.021492 | 0.085703 | 0.021609 | 0.00018362 | 0.00011716 | 0.13059 | 0.13059 | 0.13059 | 0.97464 | -0.48903 | 0.97692 | -0.44416 | 35.8756
4 | 0.030376 | 0.0076151 | -0.030373 | -0.0076128 | 3.595e-06 | 2.2447e-06 | 0.046269 | 0.046269 | 0.046269 | 0.97692 | -0.44416 | 0.9768 | -0.44665 | 12.7113
5 | 0.0073767 | 0.0018488 | -0.0073765 | -0.0018487 | 1.9264e-07 | 7.2342e-08 | 0.011236 | 0.011236 | 0.011236 | 0.97692 | -0.44416 | 0.97689 | -0.44471 | 3.0868
6 | -0.12346 | -0.031073 | 0.12373 | 0.031248 | 0.00027457 | 0.00017547 | 0.18809 | 0.18809 | 0.18809 | 0.97692 | -0.44416 | 0.9793 | -0.39774 | 51.6737
7 | -0.15023 | -0.037989 | 0.15038 | 0.038086 | 0.00015418 | 9.7073e-05 | 0.22797 | 0.22797 | 0.22797 | 0.98112 | -0.36207 | 0.98222 | -0.3407 | 15.6571
8 | 0.15023 | 0.037989 | -0.14997 | -0.037825 | 0.00025658 | 0.00016355 | 0.22797 | 0.22797 | 0.22797 | 0.98112 | -0.36207 | 0.9793 | -0.39774 | 31.3142
9 | 0.042581 | 0.010689 | -0.042553 | -0.010671 | 2.7903e-05 | 1.7632e-05 | 0.064514 | 0.064514 | 0.064514 | 0.98222 | -0.3407 | 0.98152 | -0.35444 | 17.7236
10 | -0.19297 | -0.048775 | 0.19312 | 0.04887 | 0.00015082 | 9.5571e-05 | 0.29248 | 0.29248 | 0.29248 | 0.98222 | -0.3407 | 0.98306 | -0.32441 | 20.0879
11 | 0.021331 | 0.0053461 | -0.02133 | -0.0053459 | 3.2547e-07 | 1.9801e-07 | 0.032494 | 0.032494 | 0.032494 | 0.9768 | -0.44665 | 0.97678 | -0.44697 | 8.927
12 | 0.0090423 | 0.0022668 | -0.0090404 | -0.0022659 | 1.8961e-06 | 8.8002e-07 | 0.013775 | 0.013775 | 0.013775 | 0.9768 | -0.44665 | 0.97657 | -0.45105 | 3.7843
13 | 0.0090404 | 0.0022659 | -0.0090397 | -0.0022656 | 7.0615e-07 | 3.2778e-07 | 0.013775 | 0.013775 | 0.013775 | 0.97657 | -0.45105 | 0.97649 | -0.45269 | 3.7844
14 | 0.017706 | 0.0044398 | -0.017699 | -0.0044357 | 6.8101e-06 | 4.0401e-06 | 0.026843 | 0.026843 | 0.026843 | 0.98152 | -0.35444 | 0.98111 | -0.36252 | 7.3745
15 | 0.024847 | 0.0062317 | -0.024835 | -0.0062243 | 1.2037e-05 | 7.418e-06 | 0.037671 | 0.037671 | 0.037671 | 0.98152 | -0.35444 | 0.981 | -0.36461 | 10.3492
16 | -0.20821 | -0.052654 | 0.2083 | 0.052712 | 9.0333e-05 | 5.7321e-05 | 0.31533 | 0.31533 | 0.31533 | 0.98306 | -0.32441 | 0.98353 | -0.31537 | 21.6575
17 | -0.28029 | -0.070753 | 0.28047 | 0.070866 | 0.00017788 | 0.00011331 | 0.42424 | 0.42424 | 0.42424 | 0.98353 | -0.31537 | 0.98421 | -0.30213 | 29.1374
18 | -0.041444 | -0.010387 | 0.041528 | 0.01044 | 8.3323e-05 | 5.259e-05 | 0.062322 | 0.062322 | 0.062322 | 0.98954 | -0.19996 | 0.99171 | -0.15785 | 17.1214
19 | -0.041528 | -0.01044 | 0.041574 | 0.010469 | 4.639e-05 | 2.9278e-05 | 0.062322 | 0.062322 | 0.062322 | 0.99171 | -0.15785 | 0.99292 | -0.13448 | 17.1214
20 | 0.345 | 0.08812 | -0.34429 | -0.087665 | 0.00071418 | 0.00045561 | 0.51762 | 0.51762 | 0.51762 | 0.99292 | -0.13448 | 0.99067 | -0.1774 | 35.551
21 | -0.38658 | -0.098589 | 0.38791 | 0.099438 | 0.0013289 | 0.0008483 | 0.57994 | 0.57994 | 0.57994 | 0.99292 | -0.13448 | 0.99665 | -0.063557 | 39.8313
22 | 0.34429 | 0.087665 | -0.3426 | -0.086585 | 0.0016931 | 0.0010802 | 0.51762 | 0.51762 | 0.51762 | 0.99067 | -0.1774 | 0.98535 | -0.27992 | 35.5511
23 | -0.44941 | -0.11485 | 0.44969 | 0.11503 | 0.0002853 | 0.00018224 | 0.67177 | 0.67177 | 0.67177 | 0.99665 | -0.063557 | 0.99734 | -0.05044 | 46.1377
24 | 0.32353 | 0.081807 | -0.32319 | -0.081587 | 0.00034419 | 0.0002195 | 0.48883 | 0.48883 | 0.48883 | 0.98535 | -0.27992 | 0.98421 | -0.30213 | 33.5738
25 | -0.51074 | -0.13033 | 0.51173 | 0.13097 | 0.00098908 | 0.00063207 | 0.76285 | 0.76285 | 0.76285 | 0.99734 | -0.05044 | 0.99945 | -0.010437 | 52.3933
26 | -0.018323 | -0.0045922 | 0.018326 | 0.0045942 | 3.3519e-06 | 1.9978e-06 | 0.027732 | 0.027732 | 0.027732 | 0.98315 | -0.32289 | 0.98334 | -0.31905 | 7.6187
27 | -0.042687 | -0.010699 | 0.042721 | 0.010721 | 3.4451e-05 | 2.1769e-05 | 0.064595 | 0.064595 | 0.064595 | 0.98334 | -0.31905 | 0.98421 | -0.30213 | 17.7459
28 | -0.51989 | -0.13301 | 0.52016 | 0.13318 | 0.00026281 | 0.00016795 | 0.775 | 0.775 | 0.775 | 0.99945 | -0.010437 | 1 | 0 | 53.228

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57794 | 0.14725

## res_load
| p_mw | q_mvar
0 | 0.013516 | 0.0033873
1 | 0.048439 | 0.01214
2 | 0.023414 | 0.0058681
3 | 0.026243 | 0.006577
4 | 0.0073765 | 0.0018487
5 | 0.0090397 | 0.0022656
6 | 0.02133 | 0.0053459
7 | 0.015098 | 0.0037839
8 | 0.017699 | 0.0044357
9 | 0.024835 | 0.0062243
10 | 0.071985 | 0.018041
11 | 0.041444 | 0.010387
12 | 0.061502 | 0.015414
13 | 0.019064 | 0.004778
14 | 0.061047 | 0.0153
15 | 0.018323 | 0.0045922
16 | 0.024361 | 0.0061053
17 | 0.0081632 | 0.0020459
18 | 0.056129 | 0.014067

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1