## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-286_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-286_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-286_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-286_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-286_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-286_0_6_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_2701-286_0_6_node_24 | 0.4 | n |  | TRUE
7 | bus_LV_2701-286_0_6_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_2701-286_0_6_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_2701-286_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2701-286_0_6_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2701-286_0_6_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2701-286_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2701-286_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2701-286_0_6_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_2701-286_0_6_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_2701-286_0_6_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_2701-286_0_6_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_2701-286_0_6_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2701-286_0_6_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2701-286_0_6_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2701-286_0_6_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2701-286_0_6_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_2701-286_0_6_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_2701-286_0_6_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2701-286_0_6_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2701-286_0_6_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_2701-286_0_6_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2701-286_0_6_node_30 | 0.4 | n |  | TRUE
29 | bus_MV_559_0_node_37 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-286_0_6_load_0 | 0 | 0.0067201 | 0.0016842 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-286_0_6_load_1 | 1 | 0.010422 | 0.002612 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-286_0_6_load_2 | 2 | 0.0025515 | 0.00063946 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-286_0_6_load_3 | 3 | 0.010428 | 0.0026135 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-286_0_6_load_4 | 4 | 0.005338 | 0.0013378 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-286_0_6_load_15 | 5 | 0.0051811 | 0.0012985 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-286_0_6_load_24 | 6 | 0.0066108 | 0.0016568 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-286_0_6_load_22 | 8 | 0.0040207 | 0.0010077 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-286_0_6_load_5 | 9 | 0.0063371 | 0.0015882 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-286_0_6_load_6 | 10 | 0.0684 | 0.017143 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-286_0_6_load_7 | 11 | 0.0025339 | 0.00063506 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-286_0_6_load_8 | 12 | 0.051181 | 0.012827 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-286_0_6_load_9 | 13 | 0.0043652 | 0.001094 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-286_0_6_load_26 | 14 | 0.0049501 | 0.0012406 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-286_0_6_load_20 | 15 | 0.019937 | 0.0049966 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-286_0_6_load_27 | 16 | 0.078469 | 0.019666 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-286_0_6_load_18 | 17 | 0.0066488 | 0.0016663 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-286_0_6_load_10 | 18 | 0.0052008 | 0.0013035 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-286_0_6_load_11 | 19 | 0.041048 | 0.010288 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-286_0_6_load_12 | 20 | 0.017723 | 0.0044418 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-286_0_6_load_13 | 21 | 0.026129 | 0.0065486 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-286_0_6_load_29 | 22 | 0.085269 | 0.02137 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-286_0_6_load_28 | 23 | 0.057483 | 0.014407 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-286_0_6_load_16 | 24 | 0.0069858 | 0.0017508 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-286_0_6_load_17 | 25 | 0.0040163 | 0.0010066 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-286_0_6_load_21 | 26 | 0.0038361 | 0.00096141 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-286_0_6_load_23 | 27 | 0.0081978 | 0.0020546 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-286_0_6_line_0 |  | 0 | 1 | 0.0019167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-286_0_6_line_1 |  | 0 | 2 | 0.0027387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-286_0_6_line_2 |  | 1 | 3 | 0.015799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-286_0_6_line_3 |  | 2 | 4 | 0.010723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-286_0_6_line_4 |  | 3 | 5 | 0.016655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-286_0_6_line_5 |  | 4 | 6 | 0.011894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-286_0_6_line_6 |  | 5 | 7 | 0.025191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-286_0_6_line_7 |  | 6 | 8 | 0.00023726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-286_0_6_line_8 |  | 7 | 20 | 0.016689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-286_0_6_line_9 |  | 8 | 26 | 0.013407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-286_0_6_line_10 |  | 9 | 10 | 0.0011029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-286_0_6_line_11 |  | 9 | 11 | 0.0035149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-286_0_6_line_12 |  | 10 | 12 | 0.016277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-286_0_6_line_13 |  | 11 | 13 | 0.0035066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-286_0_6_line_14 |  | 12 | 14 | 0.0010583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2701-286_0_6_line_15 |  | 13 | 15 | 0.0041696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-286_0_6_line_16 |  | 14 | 16 | 0.024171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2701-286_0_6_line_17 |  | 15 | 17 | 0.0011598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-286_0_6_line_18 |  | 16 | 28 | 0.034438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2701-286_0_6_line_19 |  | 17 | 24 | 0.01067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-286_0_6_line_20 |  | 18 | 19 | 0.001052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-286_0_6_line_21 |  | 18 | 20 | 0.013149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-286_0_6_line_22 |  | 19 | 21 | 0.0085167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-286_0_6_line_23 |  | 21 | 22 | 0.0075309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2701-286_0_6_line_24 |  | 22 | 23 | 0.018285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_2701-286_0_6_line_25 |  | 23 | 28 | 0.029818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2701-286_0_6_line_26 |  | 24 | 25 | 0.0043781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-286_0_6_line_27 |  | 26 | 27 | 1.3491e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-286_0_6_trafo_27 | 0.63 MVA 20/0.4 kV | 29 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2611850.0975 | 1267772.6368 | 2611848.972 | 1267774.1882
1 | 2611850.0975 | 1267772.6368 | 2611851.7057 | 1267770.42
2 | 2611848.972 | 1267774.1882 | 2611839.6943 | 1267786.9766
3 | 2611858.0024 | 1267761.7405 | 2611851.7057 | 1267770.42
4 | 2611839.6943 | 1267786.9766 | 2611829.914 | 1267800.4579
5 | 2611858.0024 | 1267761.7405 | 2611864.9871 | 1267752.1128
6 | 2611815.1215 | 1267820.8481 | 2611829.914 | 1267800.4579
7 | 2611864.9871 | 1267752.1128 | 2611865.1264 | 1267751.9208
8 | 2611815.1215 | 1267820.8481 | 2611811.732 | 1267818.4397 | 2611801.5188 | 1267811.1794
9 | 2611865.1264 | 1267751.9208 | 2611872.9992 | 1267741.0688
10 | 2611789.011 | 1267708.0048 | 2611788.2846 | 1267708.8347
11 | 2611789.011 | 1267708.0048 | 2611791.3261 | 1267705.3601
12 | 2611777.4993 | 1267721.0258 | 2611784.0255 | 1267713.7001 | 2611788.2846 | 1267708.8347
13 | 2611793.6359 | 1267702.7216 | 2611791.3261 | 1267705.3601
14 | 2611777.4993 | 1267721.0258 | 2611776.7954 | 1267721.816
15 | 2611793.6359 | 1267702.7216 | 2611796.3822 | 1267699.5843
16 | 2611760.7174 | 1267739.8638 | 2611776.7954 | 1267721.816
17 | 2611797.1462 | 1267698.7116 | 2611796.3822 | 1267699.5843
18 | 2611737.8095 | 1267765.5783 | 2611760.7174 | 1267739.8638
19 | 2611797.1462 | 1267698.7116 | 2611804.1744 | 1267690.6829
20 | 2611790.8021 | 1267803.5612 | 2611789.9447 | 1267802.9516
21 | 2611790.8021 | 1267803.5612 | 2611801.5188 | 1267811.1794
22 | 2611783.0031 | 1267798.0171 | 2611789.9447 | 1267802.9516
23 | 2611776.8651 | 1267793.6537 | 2611783.0031 | 1267798.0171
24 | 2611761.962 | 1267783.0595 | 2611776.8651 | 1267793.6537
25 | 2611737.8095 | 1267765.5783 | 2611743.5809 | 1267769.9928 | 2611761.962 | 1267783.0595
26 | 2611807.0581 | 1267687.3887 | 2611804.1744 | 1267690.6829
27 | 2611872.9992 | 1267741.0688 | 2611873.0071 | 1267741.0579

## bus_geodata
| x | y | coords
0 | 2611850.0975 | 1267772.6368
1 | 2611848.972 | 1267774.1882
2 | 2611851.7057 | 1267770.42
3 | 2611839.6943 | 1267786.9766
4 | 2611858.0024 | 1267761.7405
5 | 2611829.914 | 1267800.4579
6 | 2611864.9871 | 1267752.1128
7 | 2611815.1215 | 1267820.8481
8 | 2611865.1264 | 1267751.9208
9 | 2611789.011 | 1267708.0048
10 | 2611788.2846 | 1267708.8347
11 | 2611791.3261 | 1267705.3601
12 | 2611777.4993 | 1267721.0258
13 | 2611793.6359 | 1267702.7216
14 | 2611776.7954 | 1267721.816
15 | 2611796.3822 | 1267699.5843
16 | 2611760.7174 | 1267739.8638
17 | 2611797.1462 | 1267698.7116
18 | 2611790.8021 | 1267803.5612
19 | 2611789.9447 | 1267802.9516
20 | 2611801.5188 | 1267811.1794
21 | 2611783.0031 | 1267798.0171
22 | 2611776.8651 | 1267793.6537
23 | 2611761.962 | 1267783.0595
24 | 2611804.1744 | 1267690.6829
25 | 2611807.0581 | 1267687.3887
26 | 2611872.9992 | 1267741.0688
27 | 2611873.0071 | 1267741.0579
28 | 2611737.8095 | 1267765.5783
29 | 2611756.9679 | 1267744.0727

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98619 | -0.26617 | 0.0067201 | 0.0016842
1 | 0.98626 | -0.26489 | 0.010422 | 0.002612
2 | 0.98611 | -0.26767 | 0.0025515 | 0.00063946
3 | 0.98695 | -0.2514 | 0.010428 | 0.0026135
4 | 0.98584 | -0.27306 | 0.005338 | 0.0013378
5 | 0.98784 | -0.23409 | 0.0051811 | 0.0012985
6 | 0.98559 | -0.27789 | 0.0066108 | 0.0016568
7 | 0.98931 | -0.20565 | 0 | 0
8 | 0.98559 | -0.27796 | 0.0040207 | 0.0010077
9 | 0.99682 | -0.061193 | 0.0063371 | 0.0015882
10 | 0.99687 | -0.06021 | 0.0684 | 0.017143
11 | 0.99667 | -0.063936 | 0.0025339 | 0.00063506
12 | 0.99863 | -0.026232 | 0.051181 | 0.012827
13 | 0.99654 | -0.066518 | 0.0043652 | 0.001094
14 | 0.99872 | -0.024657 | 0.0049501 | 0.0012406
15 | 0.9964 | -0.069269 | 0.019937 | 0.0049966
16 | 1 | 0 | -0.47599 | -0.11998
17 | 0.99638 | -0.069628 | 0.0066488 | 0.0016663
18 | 0.99126 | -0.16793 | 0.0052008 | 0.0013035
19 | 0.99134 | -0.16632 | 0.041048 | 0.010288
20 | 0.99028 | -0.18685 | 0.017723 | 0.0044418
21 | 0.99233 | -0.14712 | 0.026129 | 0.0065486
22 | 0.99286 | -0.1369 | 0.085269 | 0.02137
23 | 0.99419 | -0.11121 | 0.057483 | 0.014407
24 | 0.99627 | -0.07169 | 0.0069858 | 0.0017508
25 | 0.99626 | -0.071998 | 0.0040163 | 0.0010066
26 | 0.98544 | -0.28086 | 0.0038361 | 0.00096141
27 | 0.98544 | -0.28086 | 0.0081978 | 0.0020546
28 | 0.99689 | -0.059443 | 0 | 0
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.037291 | -0.0093519 | 0.037294 | 0.0093534 | 2.2757e-06 | 1.432e-06 | 0.056269 | 0.056269 | 0.056269 | 0.98619 | -0.26617 | 0.98626 | -0.26489 | 15.4586
1 | 0.030571 | 0.0076677 | -0.030569 | -0.0076663 | 2.1854e-06 | 1.3637e-06 | 0.04613 | 0.04613 | 0.04613 | 0.98619 | -0.26617 | 0.98611 | -0.26767 | 12.6729
2 | -0.047715 | -0.011965 | 0.047746 | 0.011985 | 3.0708e-05 | 1.9451e-05 | 0.071993 | 0.071993 | 0.071993 | 0.98626 | -0.26489 | 0.98695 | -0.2514 | 19.7783
3 | 0.028018 | 0.0070269 | -0.02801 | -0.0070224 | 7.188e-06 | 4.4635e-06 | 0.042279 | 0.042279 | 0.042279 | 0.98611 | -0.26767 | 0.98584 | -0.27306 | 11.6152
4 | -0.058174 | -0.014598 | 0.058222 | 0.014629 | 4.8055e-05 | 3.0542e-05 | 0.087716 | 0.087716 | 0.087716 | 0.98695 | -0.2514 | 0.98784 | -0.23409 | 24.0977
5 | 0.022672 | 0.0056846 | -0.022667 | -0.0056814 | 5.2239e-06 | 3.1917e-06 | 0.034222 | 0.034222 | 0.034222 | 0.98584 | -0.27306 | 0.98559 | -0.27789 | 9.4018
6 | -0.063403 | -0.015927 | 0.06349 | 0.015982 | 8.6191e-05 | 5.4839e-05 | 0.09552 | 0.09552 | 0.09552 | 0.98784 | -0.23409 | 0.98931 | -0.20565 | 26.2418
7 | 0.016056 | 0.0040246 | -0.016056 | -0.0040246 | 5.2285e-08 | 3.0439e-08 | 0.024242 | 0.024242 | 0.024242 | 0.98559 | -0.27789 | 0.98559 | -0.27796 | 6.6598
8 | -0.06349 | -0.015982 | 0.063547 | 0.016019 | 5.7101e-05 | 3.633e-05 | 0.09552 | 0.09552 | 0.09552 | 0.98931 | -0.20565 | 0.99028 | -0.18685 | 26.2417
9 | 0.012036 | 0.0030169 | -0.012034 | -0.003016 | 1.6601e-06 | 8.9162e-07 | 0.018171 | 0.018171 | 0.018171 | 0.98559 | -0.27796 | 0.98544 | -0.28086 | 4.9921
10 | -0.050841 | -0.012748 | 0.050843 | 0.01275 | 2.3824e-06 | 1.5103e-06 | 0.075896 | 0.075896 | 0.075896 | 0.99682 | -0.061193 | 0.99687 | -0.06021 | 20.8506
11 | 0.044504 | 0.01116 | -0.044498 | -0.011156 | 5.8177e-06 | 3.6775e-06 | 0.066436 | 0.066436 | 0.066436 | 0.99682 | -0.061193 | 0.99667 | -0.063936 | 18.2517
12 | -0.11924 | -0.029893 | 0.11944 | 0.030016 | 0.00019339 | 0.00012356 | 0.178 | 0.178 | 0.178 | 0.99687 | -0.06021 | 0.99863 | -0.026232 | 48.9002
13 | 0.041964 | 0.010521 | -0.041959 | -0.010518 | 5.1619e-06 | 3.2579e-06 | 0.062653 | 0.062653 | 0.062653 | 0.99667 | -0.063936 | 0.99654 | -0.066518 | 17.2124
14 | -0.17062 | -0.042843 | 0.17063 | 0.042852 | 1.2828e-05 | 8.1821e-06 | 0.25426 | 0.25426 | 0.25426 | 0.99863 | -0.026232 | 0.99872 | -0.024657 | 34.9257
15 | 0.037594 | 0.0094241 | -0.037589 | -0.009421 | 4.9271e-06 | 3.099e-06 | 0.056135 | 0.056135 | 0.056135 | 0.99654 | -0.066518 | 0.9964 | -0.069269 | 15.4218
16 | -0.17558 | -0.044092 | 0.17579 | 0.044224 | 0.00020682 | 0.00013141 | 0.26163 | 0.26163 | 0.26163 | 0.99872 | -0.024657 | 1 | 0 | 23.9592
17 | 0.017652 | 0.0044244 | -0.017652 | -0.0044243 | 3.0226e-07 | 1.7834e-07 | 0.026362 | 0.026362 | 0.026362 | 0.9964 | -0.069269 | 0.99638 | -0.069628 | 7.2423
18 | 0.29855 | 0.075752 | -0.2977 | -0.075209 | 0.00085085 | 0.00054319 | 0.44458 | 0.44458 | 0.44458 | 1 | 0 | 0.99689 | -0.059443 | 40.7125
19 | 0.011003 | 0.0027579 | -0.011002 | -0.0027574 | 1.0805e-06 | 5.5255e-07 | 0.016432 | 0.016433 | 0.016433 | 0.99638 | -0.069628 | 0.99627 | -0.07169 | 4.5144
20 | -0.086544 | -0.021811 | 0.086551 | 0.021815 | 6.6628e-06 | 4.2506e-06 | 0.12996 | 0.12996 | 0.12996 | 0.99126 | -0.16793 | 0.99134 | -0.16632 | 35.7028
21 | 0.081343 | 0.020507 | -0.08127 | -0.02046 | 7.357e-05 | 4.6916e-05 | 0.12215 | 0.12215 | 0.12215 | 0.99126 | -0.16793 | 0.99028 | -0.18685 | 33.558
22 | -0.1276 | -0.032103 | 0.12772 | 0.032177 | 0.00011721 | 7.4905e-05 | 0.19157 | 0.19157 | 0.19157 | 0.99134 | -0.16632 | 0.99233 | -0.14712 | 52.6296
23 | -0.15385 | -0.038726 | 0.15392 | 0.038774 | 7.5186e-05 | 4.7925e-05 | 0.23075 | 0.23075 | 0.23075 | 0.99233 | -0.14712 | 0.99286 | -0.1369 | 31.6968
24 | -0.23919 | -0.060144 | 0.23948 | 0.060332 | 0.00029383 | 0.00018734 | 0.35855 | 0.35855 | 0.35855 | 0.99286 | -0.1369 | 0.99419 | -0.11121 | 32.8339
25 | -0.29697 | -0.074738 | 0.2977 | 0.075209 | 0.00073671 | 0.00047033 | 0.44458 | 0.44458 | 0.44458 | 0.99419 | -0.11121 | 0.99689 | -0.059443 | 40.7125
26 | 0.0040163 | 0.0010066 | -0.0040163 | -0.0010066 | 5.908e-08 | -1.9199e-08 | 0.0059987 | 0.0059987 | 0.0059987 | 0.99627 | -0.07169 | 0.99626 | -0.071998 | 1.648
27 | 0.0081978 | 0.0020546 | -0.0081978 | -0.0020546 | 7.744e-10 | 3.2408e-10 | 0.012379 | 0.012379 | 0.012379 | 0.98544 | -0.28086 | 0.98544 | -0.28086 | 3.4007

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.55446 | 0.13964

## res_load
| p_mw | q_mvar
0 | 0.0067201 | 0.0016842
1 | 0.010422 | 0.002612
2 | 0.0025515 | 0.00063946
3 | 0.010428 | 0.0026135
4 | 0.005338 | 0.0013378
5 | 0.0051811 | 0.0012985
6 | 0.0066108 | 0.0016568
7 | 0.0040207 | 0.0010077
8 | 0.0063371 | 0.0015882
9 | 0.0684 | 0.017143
10 | 0.0025339 | 0.00063506
11 | 0.051181 | 0.012827
12 | 0.0043652 | 0.001094
13 | 0.0049501 | 0.0012406
14 | 0.019937 | 0.0049966
15 | 0.078469 | 0.019666
16 | 0.0066488 | 0.0016663
17 | 0.0052008 | 0.0013035
18 | 0.041048 | 0.010288
19 | 0.017723 | 0.0044418
20 | 0.026129 | 0.0065486
21 | 0.085269 | 0.02137
22 | 0.057483 | 0.014407
23 | 0.0069858 | 0.0017508
24 | 0.0040163 | 0.0010066
25 | 0.0038361 | 0.00096141
26 | 0.0081978 | 0.0020546

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1