## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-288_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-288_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-288_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-288_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-288_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-288_0_4_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_2701-288_0_4_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_2701-288_0_4_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_2701-288_0_4_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_2701-288_0_4_node_45 | 0.4 | n |  | TRUE
10 | bus_LV_2701-288_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2701-288_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_2701-288_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2701-288_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2701-288_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2701-288_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2701-288_0_4_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_2701-288_0_4_node_27 | 0.4 | n |  | TRUE
18 | bus_LV_2701-288_0_4_node_43 | 0.4 | n |  | TRUE
19 | bus_LV_2701-288_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2701-288_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2701-288_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_2701-288_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_2701-288_0_4_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_2701-288_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2701-288_0_4_node_50 | 0.4 | n |  | TRUE
26 | bus_LV_2701-288_0_4_node_54 | 0.4 | n |  | TRUE
27 | bus_LV_2701-288_0_4_node_55 | 0.4 | n |  | TRUE
28 | bus_LV_2701-288_0_4_node_51 | 0.4 | n |  | TRUE
29 | bus_LV_2701-288_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_2701-288_0_4_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_2701-288_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_2701-288_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_2701-288_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_2701-288_0_4_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_2701-288_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_2701-288_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_2701-288_0_4_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_2701-288_0_4_node_41 | 0.4 | n |  | TRUE
39 | bus_LV_2701-288_0_4_node_46 | 0.4 | n |  | TRUE
40 | bus_LV_2701-288_0_4_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_2701-288_0_4_node_47 | 0.4 | n |  | TRUE
42 | bus_LV_2701-288_0_4_node_57 | 0.4 | n |  | TRUE
43 | bus_LV_2701-288_0_4_node_56 | 0.4 | n |  | TRUE
44 | bus_LV_2701-288_0_4_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_2701-288_0_4_node_61 | 0.4 | n |  | TRUE
46 | bus_LV_2701-288_0_4_node_59 | 0.4 | n |  | TRUE
47 | bus_LV_2701-288_0_4_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_2701-288_0_4_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_2701-288_0_4_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_2701-288_0_4_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_2701-288_0_4_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_2701-288_0_4_node_44 | 0.4 | n |  | TRUE
53 | bus_LV_2701-288_0_4_node_58 | 0.4 | n |  | TRUE
54 | bus_LV_2701-288_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_2701-288_0_4_node_60 | 0.4 | n |  | TRUE
56 | bus_LV_2701-288_0_4_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_2701-288_0_4_node_53 | 0.4 | n |  | TRUE
58 | bus_MV_560_0_node_106 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-288_0_4_load_0 | 0 | 0.010599 | 0.0026564 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-288_0_4_load_1 | 1 | 0.0043446 | 0.0010889 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-288_0_4_load_2 | 2 | 0.0045456 | 0.0011392 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-288_0_4_load_3 | 3 | 0.0022521 | 0.00056443 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-288_0_4_load_4 | 4 | 0.027641 | 0.0069275 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-288_0_4_load_16 | 5 | 0.0027959 | 0.00070073 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-288_0_4_load_12 | 6 | 0.012396 | 0.0031066 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-288_0_4_load_11 | 7 | 0.017943 | 0.004497 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-288_0_4_load_14 | 8 | 0.003818 | 0.00095689 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-288_0_4_load_45 | 9 | 0.021264 | 0.0053292 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-288_0_4_load_8 | 10 | 0.0097197 | 0.002436 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-288_0_4_load_5 | 11 | 0.0072391 | 0.0018143 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-288_0_4_load_6 | 12 | 0.0075654 | 0.0018961 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-288_0_4_load_9 | 14 | 0.018053 | 0.0045244 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-288_0_4_load_10 | 15 | 0.022644 | 0.0056751 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-288_0_4_load_27 | 17 | 0.015328 | 0.0038416 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-288_0_4_load_43 | 18 | 0.0069146 | 0.001733 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-288_0_4_load_13 | 19 | 0.0056855 | 0.0014249 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-288_0_4_load_15 | 20 | 0.0022175 | 0.00055577 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-288_0_4_load_17 | 21 | 0.0015368 | 0.00038517 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-288_0_4_load_20 | 22 | 0.0018555 | 0.00046504 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-288_0_4_load_18 | 23 | 0.0042777 | 0.0010721 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-288_0_4_load_19 | 24 | 0.0014827 | 0.0003716 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-288_0_4_load_54 | 26 | 0.0033931 | 0.00085038 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-288_0_4_load_55 | 27 | 0.005923 | 0.0014844 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-288_0_4_load_51 | 28 | 0.0046745 | 0.0011715 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-288_0_4_load_32 | 30 | 0.0024002 | 0.00060155 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-288_0_4_load_24 | 31 | 0.0079577 | 0.0019944 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-288_0_4_load_23 | 32 | 0.0030148 | 0.00075558 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-288_0_4_load_25 | 33 | 0.0212 | 0.0053131 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-288_0_4_load_33 | 34 | 0.0070266 | 0.001761 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-288_0_4_load_28 | 35 | 0.0084207 | 0.0021104 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-288_0_4_load_48 | 37 | 0.0056651 | 0.0014198 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-288_0_4_load_41 | 38 | 0.0044896 | 0.0011252 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-288_0_4_load_46 | 39 | 0.0032872 | 0.00082384 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-288_0_4_load_40 | 40 | 0.030386 | 0.0076154 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-288_0_4_load_47 | 41 | 0.0035267 | 0.00088386 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-288_0_4_load_57 | 42 | 0.0088382 | 0.0022151 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-288_0_4_load_56 | 43 | 0.0077329 | 0.001938 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-288_0_4_load_34 | 44 | 0.0035274 | 0.00088405 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-288_0_4_load_61 | 45 | 0.0025907 | 0.00064929 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2701-288_0_4_load_59 | 46 | 0.004652 | 0.0011659 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2701-288_0_4_load_35 | 47 | 0.011817 | 0.0029616 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2701-288_0_4_load_36 | 48 | 0.007755 | 0.0019436 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2701-288_0_4_load_37 | 49 | 0.0062464 | 0.0015655 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2701-288_0_4_load_38 | 50 | 0.0060118 | 0.0015067 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2701-288_0_4_load_39 | 51 | 0.005057 | 0.0012674 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2701-288_0_4_load_44 | 52 | 0.0064079 | 0.001606 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2701-288_0_4_load_58 | 53 | 0.0059601 | 0.0014937 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2701-288_0_4_load_42 | 54 | 0.0062023 | 0.0015544 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2701-288_0_4_load_60 | 55 | 0.0046392 | 0.0011627 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2701-288_0_4_load_52 | 56 | 0.005194 | 0.0013017 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2701-288_0_4_load_53 | 57 | 0.0039421 | 0.00098798 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 54 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-288_0_4_line_0 |  | 0 | 1 | 0.0020454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-288_0_4_line_1 |  | 0 | 2 | 0.003281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-288_0_4_line_2 |  | 1 | 3 | 0.0055675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-288_0_4_line_3 |  | 2 | 4 | 0.017436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-288_0_4_line_4 |  | 3 | 5 | 0.0064787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-288_0_4_line_5 |  | 4 | 6 | 0.011464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-288_0_4_line_6 |  | 4 | 7 | 0.0035405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-288_0_4_line_7 |  | 5 | 8 | 0.0013578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-288_0_4_line_8 |  | 6 | 9 | 0.0036889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2701-288_0_4_line_9 |  | 7 | 10 | 0.016435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-288_0_4_line_10 |  | 8 | 19 | 0.0030819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-288_0_4_line_11 |  | 9 | 18 | 0.013479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_2701-288_0_4_line_12 |  | 10 | 12 | 0.0084743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-288_0_4_line_13 |  | 11 | 12 | 0.0097997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-288_0_4_line_14 |  | 11 | 13 | 0.0012968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-288_0_4_line_15 |  | 13 | 14 | 0.0028906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-288_0_4_line_16 |  | 15 | 16 | 0.017764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-288_0_4_line_17 |  | 16 | 17 | 0.029026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-288_0_4_line_18 |  | 17 | 35 | 0.0052312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-288_0_4_line_19 |  | 18 | 54 | 0.010152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2701-288_0_4_line_20 |  | 19 | 20 | 0.0028865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-288_0_4_line_21 |  | 20 | 21 | 0.0093945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-288_0_4_line_22 |  | 21 | 22 | 0.0045929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-288_0_4_line_23 |  | 22 | 23 | 0.0017975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-288_0_4_line_24 |  | 23 | 24 | 0.0016999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-288_0_4_line_25 |  | 25 | 26 | 0.0117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-288_0_4_line_26 |  | 25 | 27 | 0.05493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-288_0_4_line_27 |  | 25 | 28 | 0.021708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-288_0_4_line_28 |  | 26 | 37 | 0.00037897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-288_0_4_line_29 |  | 27 | 55 | 0.017502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-288_0_4_line_30 |  | 28 | 56 | 0.0049028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-288_0_4_line_31 |  | 29 | 30 | 0.0035886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-288_0_4_line_32 |  | 29 | 31 | 0.014752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-288_0_4_line_33 |  | 30 | 34 | 0.0079535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-288_0_4_line_34 |  | 31 | 32 | 0.0070049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-288_0_4_line_35 |  | 32 | 33 | 0.0020374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-288_0_4_line_36 |  | 34 | 44 | 0.0060709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-288_0_4_line_37 |  | 35 | 36 | 0.013423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-288_0_4_line_38 |  | 36 | 37 | 0.0087898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2701-288_0_4_line_39 |  | 36 | 38 | 0.0126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_2701-288_0_4_line_40 |  | 36 | 39 | 0.010317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2701-288_0_4_line_41 |  | 38 | 40 | 0.0068925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_2701-288_0_4_line_42 |  | 39 | 41 | 0.0057194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-288_0_4_line_43 |  | 40 | 54 | 0.0044653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_2701-288_0_4_line_44 |  | 41 | 51 | 0.0050611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2701-288_0_4_line_45 |  | 42 | 43 | 0.0079089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2701-288_0_4_line_46 |  | 43 | 57 | 0.0055419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2701-288_0_4_line_47 |  | 44 | 45 | 0.0050114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2701-288_0_4_line_48 |  | 45 | 46 | 0.0016978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2701-288_0_4_line_49 |  | 46 | 53 | 0.0045295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2701-288_0_4_line_50 |  | 47 | 48 | 0.0043081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2701-288_0_4_line_51 |  | 47 | 49 | 0.0025544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2701-288_0_4_line_52 |  | 48 | 50 | 0.0049458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2701-288_0_4_line_53 |  | 49 | 51 | 0.0081095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2701-288_0_4_line_54 |  | 50 | 52 | 0.00010667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2701-288_0_4_line_55 |  | 52 | 53 | 0.0059512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2701-288_0_4_line_56 |  | 56 | 57 | 0.0043634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-288_0_4_trafo_42 | 0.63 MVA 20/0.4 kV | 58 | 54 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2611703.5577 | 1267641.0208 | 2611704.9371 | 1267639.5105
1 | 2611703.5577 | 1267641.0208 | 2611701.345 | 1267643.4434
2 | 2611704.9371 | 1267639.5105 | 2611708.6918 | 1267635.3997
3 | 2611689.586 | 1267656.3178 | 2611701.345 | 1267643.4434
4 | 2611713.061 | 1267630.616 | 2611708.6918 | 1267635.3997
5 | 2611689.586 | 1267656.3178 | 2611681.6305 | 1267648.0636
6 | 2611689.586 | 1267656.3178 | 2611687.2084 | 1267658.9411
7 | 2611713.061 | 1267630.616 | 2611713.9767 | 1267629.6135
8 | 2611679.0706 | 1267645.4075 | 2611681.6305 | 1267648.0636
9 | 2611687.2084 | 1267658.9411 | 2611676.1712 | 1267671.1186
10 | 2611716.0552 | 1267627.3379 | 2611713.9767 | 1267629.6135
11 | 2611679.0706 | 1267645.4075 | 2611669.7165 | 1267635.7023
12 | 2611670.4802 | 1267677.3976 | 2611676.1712 | 1267671.1186
13 | 2611663.8991 | 1267684.6586 | 2611670.4802 | 1267677.3976
14 | 2611663.0283 | 1267685.6194 | 2611663.8991 | 1267684.6586
15 | 2611663.0283 | 1267685.6194 | 2611661.0746 | 1267687.7498
16 | 2611611.1198 | 1267643.088 | 2611624.8608 | 1267654.3468
17 | 2611611.1198 | 1267643.088 | 2611632.5459 | 1267623.5072
18 | 2611632.5459 | 1267623.5072 | 2611636.4075 | 1267619.9782
19 | 2611669.7165 | 1267635.7023 | 2611662.6717 | 1267628.393
20 | 2611718.0019 | 1267625.2065 | 2611716.0552 | 1267627.3379
21 | 2611718.0019 | 1267625.2065 | 2611718.0821 | 1267625.1187 | 2611724.6025 | 1267618.5217
22 | 2611727.8788 | 1267615.3063 | 2611727.2299 | 1267615.8636 | 2611724.6025 | 1267618.5217
23 | 2611727.8788 | 1267615.3063 | 2611729.2424 | 1267614.1352
24 | 2611730.532 | 1267613.0277 | 2611729.2424 | 1267614.1352
25 | 2611633.4327 | 1267594.5198 | 2611640.8136 | 1267603.5975
26 | 2611633.4327 | 1267594.5198 | 2611660.1114 | 1267572.7902 | 2611676.4095 | 1267560.3191
27 | 2611633.4327 | 1267594.5198 | 2611617.2309 | 1267608.9674
28 | 2611640.8136 | 1267603.5975 | 2611641.0526 | 1267603.8915
29 | 2611690.3089 | 1267549.6834 | 2611676.4095 | 1267560.3191
30 | 2611617.2309 | 1267608.9674 | 2611613.5717 | 1267612.2304
31 | 2611717.6231 | 1267586.9021 | 2611714.0421 | 1267587.1343
32 | 2611717.6231 | 1267586.9021 | 2611716.1279 | 1267581.8289 | 2611711.0439 | 1267573.8472
33 | 2611714.0421 | 1267587.1343 | 2611708.801 | 1267587.474 | 2611706.1566 | 1267588.0258
34 | 2611707.2807 | 1267567.9391 | 2611711.0439 | 1267573.8472
35 | 2611706.1861 | 1267566.2206 | 2611707.2807 | 1267567.9391
36 | 2611700.2137 | 1267589.2659 | 2611706.1566 | 1267588.0258
37 | 2611646.3159 | 1267610.9232 | 2611636.4075 | 1267619.9782
38 | 2611646.3159 | 1267610.9232 | 2611643.7191 | 1267607.171 | 2611641.0526 | 1267603.8915
39 | 2611646.3159 | 1267610.9232 | 2611647.4866 | 1267612.6378 | 2611654.7898 | 1267620.2152
40 | 2611646.3159 | 1267610.9232 | 2611655.3995 | 1267606.0323
41 | 2611659.573 | 1267625.1779 | 2611654.7898 | 1267620.2152
42 | 2611655.3995 | 1267606.0323 | 2611660.4354 | 1267603.3209
43 | 2611659.573 | 1267625.1779 | 2611662.6717 | 1267628.393
44 | 2611660.4354 | 1267603.3209 | 2611661.151 | 1267602.9356 | 2611665.0963 | 1267601.3599
45 | 2611606.1789 | 1267618.8228 | 2611600.276 | 1267624.0865
46 | 2611606.1789 | 1267618.8228 | 2611610.3151 | 1267615.1344
47 | 2611695.308 | 1267590.2896 | 2611700.2137 | 1267589.2659
48 | 2611695.308 | 1267590.2896 | 2611693.9679 | 1267590.5692 | 2611693.6561 | 1267590.6736
49 | 2611693.6561 | 1267590.6736 | 2611689.3611 | 1267592.1121
50 | 2611674.9996 | 1267597.4046 | 2611679.0004 | 1267595.8067
51 | 2611674.9996 | 1267597.4046 | 2611672.6274 | 1267598.352
52 | 2611679.0004 | 1267595.8067 | 2611682.4825 | 1267594.416 | 2611683.6169 | 1267594.036
53 | 2611665.0963 | 1267601.3599 | 2611672.6274 | 1267598.352
54 | 2611683.6169 | 1267594.036 | 2611683.718 | 1267594.0022
55 | 2611683.718 | 1267594.0022 | 2611689.3611 | 1267592.1121
56 | 2611613.5717 | 1267612.2304 | 2611610.3151 | 1267615.1344

## bus_geodata
| x | y | coords
0 | 2611703.5577 | 1267641.0208
1 | 2611704.9371 | 1267639.5105
2 | 2611701.345 | 1267643.4434
3 | 2611708.6918 | 1267635.3997
4 | 2611689.586 | 1267656.3178
5 | 2611713.061 | 1267630.616
6 | 2611681.6305 | 1267648.0636
7 | 2611687.2084 | 1267658.9411
8 | 2611713.9767 | 1267629.6135
9 | 2611679.0706 | 1267645.4075
10 | 2611676.1712 | 1267671.1186
11 | 2611663.8991 | 1267684.6586
12 | 2611670.4802 | 1267677.3976
13 | 2611663.0283 | 1267685.6194
14 | 2611661.0746 | 1267687.7498
15 | 2611624.8608 | 1267654.3468
16 | 2611611.1198 | 1267643.088
17 | 2611632.5459 | 1267623.5072
18 | 2611669.7165 | 1267635.7023
19 | 2611716.0552 | 1267627.3379
20 | 2611718.0018 | 1267625.2065
21 | 2611724.6025 | 1267618.5217
22 | 2611727.8788 | 1267615.3063
23 | 2611729.2424 | 1267614.1352
24 | 2611730.532 | 1267613.0277
25 | 2611633.4327 | 1267594.5198
26 | 2611640.8136 | 1267603.5975
27 | 2611676.4095 | 1267560.319
28 | 2611617.2309 | 1267608.9674
29 | 2611717.6231 | 1267586.9021
30 | 2611714.0421 | 1267587.1343
31 | 2611711.0439 | 1267573.8472
32 | 2611707.2807 | 1267567.9391
33 | 2611706.1861 | 1267566.2206
34 | 2611706.1566 | 1267588.0258
35 | 2611636.4075 | 1267619.9782
36 | 2611646.3159 | 1267610.9232
37 | 2611641.0526 | 1267603.8915
38 | 2611654.7898 | 1267620.2152
39 | 2611655.3995 | 1267606.0323
40 | 2611659.573 | 1267625.1779
41 | 2611660.4354 | 1267603.3209
42 | 2611600.276 | 1267624.0865
43 | 2611606.1789 | 1267618.8228
44 | 2611700.2137 | 1267589.2659
45 | 2611695.308 | 1267590.2896
46 | 2611693.6561 | 1267590.6736
47 | 2611674.9996 | 1267597.4046
48 | 2611679.0004 | 1267595.8067
49 | 2611672.6274 | 1267598.352
50 | 2611683.6169 | 1267594.036
51 | 2611665.0963 | 1267601.3599
52 | 2611683.718 | 1267594.0022
53 | 2611689.3611 | 1267592.1121
54 | 2611662.6717 | 1267628.393
55 | 2611690.3089 | 1267549.6834
56 | 2611613.5717 | 1267612.2304
57 | 2611610.3151 | 1267615.1344
58 | 2611646.3159 | 1267610.9232

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99569 | -0.08293 | 0.010599 | 0.0026564
1 | 0.99563 | -0.084019 | 0.0043446 | 0.0010889
2 | 0.99581 | -0.080573 | 0.0045456 | 0.0011392
3 | 0.9955 | -0.086557 | 0.0022521 | 0.00056443
4 | 0.99653 | -0.066666 | 0.027641 | 0.0069275
5 | 0.99536 | -0.089254 | 0.0027959 | 0.00070073
6 | 0.99792 | -0.039827 | 0.012396 | 0.0031066
7 | 0.99633 | -0.070427 | 0.017943 | 0.004497
8 | 0.99533 | -0.089753 | 0.003818 | 0.00095689
9 | 0.99817 | -0.035116 | 0.021264 | 0.0053292
10 | 0.9957 | -0.082721 | 0.0097197 | 0.002436
11 | 0.99522 | -0.091978 | 0.0072391 | 0.0018143
12 | 0.99544 | -0.087618 | 0.0075654 | 0.0018961
13 | 0.9952 | -0.09239 | 0 | 0
14 | 0.99515 | -0.093309 | 0.018053 | 0.0045244
15 | 0.99597 | -0.077492 | 0.022644 | 0.0056751
16 | 0.99633 | -0.070426 | 0 | 0
17 | 0.99693 | -0.058893 | 0.015328 | 0.0038416
18 | 0.9992 | -0.015419 | 0.0069146 | 0.001733
19 | 0.99529 | -0.090678 | 0.0056855 | 0.0014249
20 | 0.99526 | -0.091255 | 0.0022175 | 0.00055577
21 | 0.99518 | -0.092768 | 0.0015368 | 0.00038517
22 | 0.99515 | -0.093384 | 0.0018555 | 0.00046504
23 | 0.99514 | -0.093566 | 0.0042777 | 0.0010721
24 | 0.99513 | -0.09361 | 0.0014827 | 0.0003716
25 | 0.99683 | -0.060893 | 0 | 0
26 | 0.99726 | -0.052493 | 0.0033931 | 0.00085038
27 | 0.9963 | -0.071076 | 0.005923 | 0.0014844
28 | 0.99623 | -0.072468 | 0.0046745 | 0.0011715
29 | 0.99268 | -0.1409 | 0 | 0
30 | 0.99278 | -0.13886 | 0.0024002 | 0.00060155
31 | 0.99224 | -0.1493 | 0.0079577 | 0.0019944
32 | 0.99209 | -0.1523 | 0.0030148 | 0.00075558
33 | 0.99205 | -0.15307 | 0.0212 | 0.0053131
34 | 0.99303 | -0.134 | 0.0070266 | 0.001761
35 | 0.99711 | -0.05541 | 0.0084207 | 0.0021104
36 | 0.99768 | -0.044499 | 0 | 0
37 | 0.99728 | -0.052199 | 0.0056651 | 0.0014198
38 | 0.99885 | -0.021927 | 0.0044896 | 0.0011252
39 | 0.99666 | -0.064109 | 0.0032872 | 0.00082384
40 | 0.99951 | -0.009333 | 0.030386 | 0.0076154
41 | 0.99611 | -0.074667 | 0.0035267 | 0.00088386
42 | 0.99588 | -0.079096 | 0.0088382 | 0.0022151
43 | 0.99595 | -0.077868 | 0.0077329 | 0.001938
44 | 0.99326 | -0.12954 | 0.0035274 | 0.00088405
45 | 0.99347 | -0.12554 | 0.0025907 | 0.00064929
46 | 0.99355 | -0.12411 | 0.004652 | 0.0011659
47 | 0.99471 | -0.10155 | 0.011817 | 0.0029616
48 | 0.99441 | -0.10751 | 0.007755 | 0.0019436
49 | 0.99492 | -0.097486 | 0.0062464 | 0.0015655
50 | 0.99409 | -0.11368 | 0.0060118 | 0.0015067
51 | 0.99564 | -0.083706 | 0.005057 | 0.0012674
52 | 0.99408 | -0.1138 | 0.0064079 | 0.001606
53 | 0.99376 | -0.11992 | 0.0059601 | 0.0014937
54 | 1 | 0 | -0.41706 | -0.10471
55 | 0.99623 | -0.072502 | 0.0046392 | 0.0011627
56 | 0.99611 | -0.074682 | 0.005194 | 0.0013017
57 | 0.99603 | -0.076255 | 0.0039421 | 0.00098798
58 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.030277 | 0.0075916 | -0.030275 | -0.0075906 | 1.5704e-06 | 9.7847e-07 | 0.045249 | 0.045249 | 0.045249 | 0.99569 | -0.08293 | 0.99563 | -0.084019 | 12.431
1 | -0.040876 | -0.010248 | 0.04088 | 0.010251 | 4.5916e-06 | 2.8959e-06 | 0.061089 | 0.061089 | 0.061089 | 0.99569 | -0.08293 | 0.99581 | -0.080573 | 16.7826
2 | 0.025931 | 0.0065017 | -0.025927 | -0.0064998 | 3.1359e-06 | 1.9346e-06 | 0.038756 | 0.038756 | 0.038756 | 0.99563 | -0.084019 | 0.9955 | -0.086557 | 10.6471
3 | -0.045426 | -0.01139 | 0.045456 | 0.011409 | 3.0129e-05 | 1.9055e-05 | 0.067881 | 0.067881 | 0.067881 | 0.99581 | -0.080573 | 0.99653 | -0.066666 | 18.6486
4 | 0.023675 | 0.0059354 | -0.023672 | -0.0059335 | 3.0427e-06 | 1.8631e-06 | 0.035389 | 0.035389 | 0.035389 | 0.9955 | -0.086557 | 0.99536 | -0.089254 | 9.7223
5 | -0.13367 | -0.033536 | 0.13384 | 0.033645 | 0.00017128 | 0.00010947 | 0.1996 | 0.1996 | 0.1996 | 0.99653 | -0.066666 | 0.99792 | -0.039827 | 54.8365
6 | 0.06057 | 0.015199 | -0.060559 | -0.015192 | 1.0862e-05 | 6.9057e-06 | 0.09045 | 0.09045 | 0.09045 | 0.99653 | -0.066666 | 0.99633 | -0.070427 | 24.8489
7 | 0.020876 | 0.0052328 | -0.020876 | -0.0052325 | 4.9595e-07 | 2.9976e-07 | 0.031209 | 0.031209 | 0.031209 | 0.99536 | -0.089254 | 0.99533 | -0.089753 | 8.574
8 | -0.14623 | -0.036752 | 0.14627 | 0.036773 | 3.2897e-05 | 2.0958e-05 | 0.21809 | 0.21809 | 0.21809 | 0.99792 | -0.039827 | 0.99817 | -0.035116 | 29.9571
9 | 0.042616 | 0.010695 | -0.042591 | -0.01068 | 2.497e-05 | 1.5767e-05 | 0.063652 | 0.063652 | 0.063652 | 0.99633 | -0.070427 | 0.9957 | -0.082721 | 17.4868
10 | 0.017058 | 0.0042756 | -0.017057 | -0.0042751 | 7.516e-07 | 4.4097e-07 | 0.025502 | 0.025502 | 0.025502 | 0.99533 | -0.089753 | 0.99529 | -0.090678 | 7.0059
11 | -0.16753 | -0.042102 | 0.16769 | 0.042203 | 0.00015769 | 0.00010057 | 0.24979 | 0.24979 | 0.24979 | 0.99817 | -0.035116 | 0.9992 | -0.015419 | 34.3114
12 | 0.032871 | 0.0082435 | -0.032864 | -0.0082387 | 7.6694e-06 | 4.7982e-06 | 0.049126 | 0.049126 | 0.049126 | 0.9957 | -0.082721 | 0.99544 | -0.087618 | 13.4962
13 | -0.025293 | -0.0063394 | 0.025298 | 0.0063426 | 5.2556e-06 | 3.2362e-06 | 0.037817 | 0.037817 | 0.037817 | 0.99522 | -0.091978 | 0.99544 | -0.087618 | 10.3894
14 | 0.018054 | 0.0045251 | -0.018054 | -0.0045249 | 3.5434e-07 | 2.0993e-07 | 0.026994 | 0.026994 | 0.026994 | 0.99522 | -0.091978 | 0.9952 | -0.09239 | 7.4158
15 | 0.018054 | 0.0045249 | -0.018053 | -0.0045244 | 7.8984e-07 | 4.6794e-07 | 0.026994 | 0.026994 | 0.026994 | 0.9952 | -0.09239 | 0.99515 | -0.093309 | 7.4159
16 | -0.022644 | -0.0056751 | 0.022652 | 0.0056797 | 7.6245e-06 | 4.6484e-06 | 0.033831 | 0.033831 | 0.033831 | 0.99597 | -0.077492 | 0.99633 | -0.070426 | 9.2942
17 | -0.022652 | -0.0056797 | 0.022664 | 0.0056873 | 1.2458e-05 | 7.5947e-06 | 0.033831 | 0.033831 | 0.033831 | 0.99633 | -0.070426 | 0.99693 | -0.058893 | 9.2942
18 | -0.037992 | -0.009529 | 0.037999 | 0.0095329 | 6.3088e-06 | 3.9694e-06 | 0.05671 | 0.05671 | 0.05671 | 0.99693 | -0.058893 | 0.99711 | -0.05541 | 15.5796
19 | -0.1746 | -0.043936 | 0.17473 | 0.044018 | 0.00012875 | 8.2137e-05 | 0.26008 | 0.26008 | 0.26008 | 0.9992 | -0.015419 | 1 | 0 | 35.7259
20 | 0.011372 | 0.0028502 | -0.011371 | -0.00285 | 3.1288e-07 | 1.6273e-07 | 0.017001 | 0.017001 | 0.017001 | 0.99529 | -0.090678 | 0.99526 | -0.091255 | 4.6707
21 | 0.0091537 | 0.0022943 | -0.009153 | -0.002294 | 6.5986e-07 | 3.0024e-07 | 0.013686 | 0.013686 | 0.013686 | 0.99526 | -0.091255 | 0.99518 | -0.092768 | 3.7599
22 | 0.0076162 | 0.0019088 | -0.007616 | -0.0019087 | 2.2336e-07 | 8.3278e-08 | 0.011388 | 0.011388 | 0.011388 | 0.99518 | -0.092768 | 0.99515 | -0.093384 | 3.1286
23 | 0.0057605 | 0.0014437 | -0.0057604 | -0.0014437 | 5.0009e-08 | 8.6528e-09 | 0.0086135 | 0.0086135 | 0.0086135 | 0.99515 | -0.093384 | 0.99514 | -0.093566 | 2.3663
24 | 0.0014827 | 0.00037158 | -0.0014827 | -0.0003716 | 3.1334e-09 | -2.0079e-08 | 0.0022171 | 0.0022171 | 0.0022171 | 0.99514 | -0.093566 | 0.99513 | -0.09361 | 0.60909
25 | -0.040972 | -0.010278 | 0.040989 | 0.010288 | 1.6414e-05 | 1.0352e-05 | 0.061165 | 0.061165 | 0.061165 | 0.99683 | -0.060893 | 0.99726 | -0.052493 | 16.8035
26 | 0.010568 | 0.0026497 | -0.010562 | -0.0026471 | 5.1263e-06 | 2.5651e-06 | 0.015775 | 0.015776 | 0.015776 | 0.99683 | -0.060893 | 0.9963 | -0.071076 | 4.3339
27 | 0.030405 | 0.0076284 | -0.030388 | -0.0076179 | 1.6771e-05 | 1.0451e-05 | 0.045389 | 0.045389 | 0.045389 | 0.99683 | -0.060893 | 0.99623 | -0.072468 | 12.4696
28 | -0.044382 | -0.011139 | 0.044382 | 0.011139 | 6.2332e-07 | 3.9398e-07 | 0.066227 | 0.066227 | 0.066227 | 0.99726 | -0.052493 | 0.99728 | -0.052199 | 18.1943
29 | 0.0046395 | 0.0011627 | -0.0046392 | -0.0011627 | 3.1513e-07 | -2.6214e-08 | 0.0069292 | 0.0069293 | 0.0069293 | 0.9963 | -0.071076 | 0.99623 | -0.072502 | 1.9037
30 | 0.025713 | 0.0064464 | -0.025711 | -0.0064447 | 2.7121e-06 | 1.6719e-06 | 0.038407 | 0.038407 | 0.038407 | 0.99623 | -0.072468 | 0.99611 | -0.074682 | 10.5515
31 | -0.032189 | -0.0080737 | 0.032192 | 0.0080757 | 3.1333e-06 | 1.9589e-06 | 0.048253 | 0.048253 | 0.048253 | 0.99268 | -0.1409 | 0.99278 | -0.13886 | 13.2564
32 | 0.032189 | 0.0080737 | -0.032176 | -0.0080656 | 1.2881e-05 | 8.0532e-06 | 0.048253 | 0.048254 | 0.048254 | 0.99268 | -0.1409 | 0.99224 | -0.1493 | 13.2565
33 | -0.034592 | -0.0086772 | 0.0346 | 0.0086822 | 8.0187e-06 | 5.0291e-06 | 0.051851 | 0.051851 | 0.051851 | 0.99278 | -0.13886 | 0.99303 | -0.134 | 14.2448
34 | 0.024219 | 0.0060713 | -0.024215 | -0.0060691 | 3.4651e-06 | 2.1272e-06 | 0.03632 | 0.03632 | 0.03632 | 0.99224 | -0.1493 | 0.99209 | -0.1523 | 9.978
35 | 0.0212 | 0.0053136 | -0.0212 | -0.0053131 | 7.7253e-07 | 4.6811e-07 | 0.031798 | 0.031798 | 0.031798 | 0.99209 | -0.1523 | 0.99205 | -0.15307 | 8.7357
36 | -0.041627 | -0.010443 | 0.041636 | 0.010449 | 8.8587e-06 | 5.591e-06 | 0.06238 | 0.06238 | 0.06238 | 0.99303 | -0.134 | 0.99326 | -0.12954 | 17.1373
37 | -0.046419 | -0.011643 | 0.046443 | 0.011659 | 2.4157e-05 | 1.5285e-05 | 0.069276 | 0.069276 | 0.069276 | 0.99711 | -0.05541 | 0.99768 | -0.044499 | 19.0319
38 | 0.050066 | 0.012571 | -0.050047 | -0.012559 | 1.8383e-05 | 1.1651e-05 | 0.07468 | 0.07468 | 0.07468 | 0.99768 | -0.044499 | 0.99728 | -0.052199 | 20.5165
39 | -0.20535 | -0.051661 | 0.20557 | 0.051803 | 0.00022171 | 0.00014156 | 0.30634 | 0.30634 | 0.30634 | 0.99768 | -0.044499 | 0.99885 | -0.021927 | 42.0797
40 | 0.10884 | 0.027432 | -0.10874 | -0.027367 | 0.00010201 | 6.5154e-05 | 0.16238 | 0.16238 | 0.16238 | 0.99768 | -0.044499 | 0.99666 | -0.064109 | 44.6111
41 | -0.21006 | -0.052928 | 0.21019 | 0.053009 | 0.00012663 | 8.0865e-05 | 0.31303 | 0.31303 | 0.31303 | 0.99885 | -0.021927 | 0.99951 | -0.009333 | 42.9984
42 | 0.10545 | 0.026543 | -0.1054 | -0.026509 | 5.3188e-05 | 3.3966e-05 | 0.15748 | 0.15748 | 0.15748 | 0.99666 | -0.064109 | 0.99611 | -0.074667 | 43.2629
43 | -0.24057 | -0.060624 | 0.24068 | 0.060693 | 0.00010746 | 6.866e-05 | 0.35827 | 0.35827 | 0.35827 | 0.99951 | -0.009333 | 1 | 0 | 49.2123
44 | 0.10187 | 0.025625 | -0.10183 | -0.025597 | 4.397e-05 | 2.8075e-05 | 0.15221 | 0.15221 | 0.15221 | 0.99611 | -0.074667 | 0.99564 | -0.083706 | 41.8155
45 | -0.0088382 | -0.0022151 | 0.0088388 | 0.0022153 | 5.1722e-07 | 2.2811e-07 | 0.013206 | 0.013206 | 0.013206 | 0.99588 | -0.079096 | 0.99595 | -0.077868 | 3.628
46 | -0.016572 | -0.0041533 | 0.016573 | 0.0041541 | 1.274e-06 | 7.4322e-07 | 0.024759 | 0.024759 | 0.024759 | 0.99595 | -0.077868 | 0.99603 | -0.076255 | 6.802
47 | -0.045163 | -0.011333 | 0.045172 | 0.011338 | 8.6042e-06 | 5.4418e-06 | 0.067664 | 0.067664 | 0.067664 | 0.99326 | -0.12954 | 0.99347 | -0.12554 | 18.5891
48 | -0.047763 | -0.011988 | 0.047766 | 0.01199 | 3.2588e-06 | 2.0637e-06 | 0.071545 | 0.071545 | 0.071545 | 0.99347 | -0.12554 | 0.99355 | -0.12411 | 19.6551
49 | -0.052418 | -0.013156 | 0.052428 | 0.013162 | 1.047e-05 | 6.6422e-06 | 0.078512 | 0.078512 | 0.078512 | 0.99355 | -0.12411 | 0.99376 | -0.11992 | 21.5692
50 | 0.078624 | 0.019751 | -0.078601 | -0.019737 | 2.2354e-05 | 1.4251e-05 | 0.11763 | 0.11763 | 0.11763 | 0.99471 | -0.10155 | 0.99441 | -0.10751 | 32.3163
51 | -0.090441 | -0.022712 | 0.090458 | 0.022724 | 1.7537e-05 | 1.1191e-05 | 0.13531 | 0.13531 | 0.13531 | 0.99471 | -0.10155 | 0.99492 | -0.097486 | 37.1727
52 | 0.070846 | 0.017793 | -0.070825 | -0.01778 | 2.085e-05 | 1.328e-05 | 0.10603 | 0.10603 | 0.10603 | 0.99441 | -0.10751 | 0.99409 | -0.11368 | 29.1282
53 | -0.096705 | -0.024289 | 0.096768 | 0.02433 | 6.3631e-05 | 4.0618e-05 | 0.14465 | 0.14465 | 0.14465 | 0.99492 | -0.097486 | 0.99564 | -0.083706 | 39.7392
54 | 0.064814 | 0.016273 | -0.064813 | -0.016273 | 3.7659e-07 | 2.3963e-07 | 0.097028 | 0.097028 | 0.097028 | 0.99409 | -0.11368 | 0.99408 | -0.1138 | 26.656
55 | 0.058405 | 0.014667 | -0.058388 | -0.014656 | 1.7061e-05 | 1.0842e-05 | 0.087436 | 0.087436 | 0.087436 | 0.99408 | -0.1138 | 0.99376 | -0.11992 | 24.0209
56 | 0.020517 | 0.005143 | -0.020515 | -0.0051421 | 1.537e-06 | 9.2688e-07 | 0.030648 | 0.030648 | 0.030648 | 0.99611 | -0.074682 | 0.99603 | -0.076255 | 8.4199

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42326 | 0.10627

## res_load
| p_mw | q_mvar
0 | 0.010599 | 0.0026564
1 | 0.0043446 | 0.0010889
2 | 0.0045456 | 0.0011392
3 | 0.0022521 | 0.00056443
4 | 0.027641 | 0.0069275
5 | 0.0027959 | 0.00070073
6 | 0.012396 | 0.0031066
7 | 0.017943 | 0.004497
8 | 0.003818 | 0.00095689
9 | 0.021264 | 0.0053292
10 | 0.0097197 | 0.002436
11 | 0.0072391 | 0.0018143
12 | 0.0075654 | 0.0018961
13 | 0.018053 | 0.0045244
14 | 0.022644 | 0.0056751
15 | 0.015328 | 0.0038416
16 | 0.0069146 | 0.001733
17 | 0.0056855 | 0.0014249
18 | 0.0022175 | 0.00055577
19 | 0.0015368 | 0.00038517
20 | 0.0018555 | 0.00046504
21 | 0.0042777 | 0.0010721
22 | 0.0014827 | 0.0003716
23 | 0.0033931 | 0.00085038
24 | 0.005923 | 0.0014844
25 | 0.0046745 | 0.0011715
26 | 0.0024002 | 0.00060155
27 | 0.0079577 | 0.0019944
28 | 0.0030148 | 0.00075558
29 | 0.0212 | 0.0053131
30 | 0.0070266 | 0.001761
31 | 0.0084207 | 0.0021104
32 | 0.0056651 | 0.0014198
33 | 0.0044896 | 0.0011252
34 | 0.0032872 | 0.00082384
35 | 0.030386 | 0.0076154
36 | 0.0035267 | 0.00088386
37 | 0.0088382 | 0.0022151
38 | 0.0077329 | 0.001938
39 | 0.0035274 | 0.00088405
40 | 0.0025907 | 0.00064929
41 | 0.004652 | 0.0011659
42 | 0.011817 | 0.0029616
43 | 0.007755 | 0.0019436
44 | 0.0062464 | 0.0015655
45 | 0.0060118 | 0.0015067
46 | 0.005057 | 0.0012674
47 | 0.0064079 | 0.001606
48 | 0.0059601 | 0.0014937
49 | 0.0062023 | 0.0015544
50 | 0.0046392 | 0.0011627
51 | 0.005194 | 0.0013017
52 | 0.0039421 | 0.00098798

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1