## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-296_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-296_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-296_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-296_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-296_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-296_0_5_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_2701-296_0_5_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_2701-296_0_5_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_2701-296_0_5_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_2701-296_0_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2701-296_0_5_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2701-296_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2701-296_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2701-296_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2701-296_0_5_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_2701-296_0_5_node_74 | 0.4 | n |  | TRUE
16 | bus_LV_2701-296_0_5_node_107 | 0.4 | n |  | TRUE
17 | bus_LV_2701-296_0_5_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_2701-296_0_5_node_72 | 0.4 | n |  | TRUE
19 | bus_LV_2701-296_0_5_node_108 | 0.4 | n |  | TRUE
20 | bus_LV_2701-296_0_5_node_131 | 0.4 | n |  | TRUE
21 | bus_LV_2701-296_0_5_node_135 | 0.4 | n |  | TRUE
22 | bus_LV_2701-296_0_5_node_71 | 0.4 | n |  | TRUE
23 | bus_LV_2701-296_0_5_node_130 | 0.4 | n |  | TRUE
24 | bus_LV_2701-296_0_5_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2701-296_0_5_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2701-296_0_5_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2701-296_0_5_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2701-296_0_5_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_2701-296_0_5_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2701-296_0_5_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_2701-296_0_5_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_2701-296_0_5_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_2701-296_0_5_node_126 | 0.4 | n |  | TRUE
34 | bus_LV_2701-296_0_5_node_123 | 0.4 | n |  | TRUE
35 | bus_LV_2701-296_0_5_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_2701-296_0_5_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_2701-296_0_5_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_2701-296_0_5_node_44 | 0.4 | n |  | TRUE
39 | bus_LV_2701-296_0_5_node_41 | 0.4 | n |  | TRUE
40 | bus_LV_2701-296_0_5_node_43 | 0.4 | n |  | TRUE
41 | bus_LV_2701-296_0_5_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_2701-296_0_5_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_2701-296_0_5_node_141 | 0.4 | n |  | TRUE
44 | bus_LV_2701-296_0_5_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_2701-296_0_5_node_96 | 0.4 | n |  | TRUE
46 | bus_LV_2701-296_0_5_node_97 | 0.4 | n |  | TRUE
47 | bus_LV_2701-296_0_5_node_93 | 0.4 | n |  | TRUE
48 | bus_LV_2701-296_0_5_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_2701-296_0_5_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_2701-296_0_5_node_119 | 0.4 | n |  | TRUE
51 | bus_LV_2701-296_0_5_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_2701-296_0_5_node_106 | 0.4 | n |  | TRUE
53 | bus_LV_2701-296_0_5_node_143 | 0.4 | n |  | TRUE
54 | bus_LV_2701-296_0_5_node_103 | 0.4 | n |  | TRUE
55 | bus_LV_2701-296_0_5_node_21 | 0.4 | n |  | TRUE
56 | bus_LV_2701-296_0_5_node_121 | 0.4 | n |  | TRUE
57 | bus_LV_2701-296_0_5_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_2701-296_0_5_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_2701-296_0_5_node_139 | 0.4 | n |  | TRUE
60 | bus_LV_2701-296_0_5_node_137 | 0.4 | n |  | TRUE
61 | bus_LV_2701-296_0_5_node_102 | 0.4 | n |  | TRUE
62 | bus_LV_2701-296_0_5_node_101 | 0.4 | n |  | TRUE
63 | bus_LV_2701-296_0_5_node_94 | 0.4 | n |  | TRUE
64 | bus_LV_2701-296_0_5_node_142 | 0.4 | n |  | TRUE
65 | bus_LV_2701-296_0_5_node_140 | 0.4 | n |  | TRUE
66 | bus_LV_2701-296_0_5_node_117 | 0.4 | n |  | TRUE
67 | bus_LV_2701-296_0_5_node_104 | 0.4 | n |  | TRUE
68 | bus_LV_2701-296_0_5_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_2701-296_0_5_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_2701-296_0_5_node_48 | 0.4 | n |  | TRUE
71 | bus_LV_2701-296_0_5_node_49 | 0.4 | n |  | TRUE
72 | bus_LV_2701-296_0_5_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_2701-296_0_5_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_2701-296_0_5_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_2701-296_0_5_node_118 | 0.4 | n |  | TRUE
76 | bus_LV_2701-296_0_5_node_125 | 0.4 | n |  | TRUE
77 | bus_LV_2701-296_0_5_node_116 | 0.4 | n |  | TRUE
78 | bus_LV_2701-296_0_5_node_112 | 0.4 | n |  | TRUE
79 | bus_LV_2701-296_0_5_node_53 | 0.4 | n |  | TRUE
80 | bus_LV_2701-296_0_5_node_54 | 0.4 | n |  | TRUE
81 | bus_LV_2701-296_0_5_node_55 | 0.4 | n |  | TRUE
82 | bus_LV_2701-296_0_5_node_61 | 0.4 | n |  | TRUE
83 | bus_LV_2701-296_0_5_node_90 | 0.4 | n |  | TRUE
84 | bus_LV_2701-296_0_5_node_56 | 0.4 | n |  | TRUE
85 | bus_LV_2701-296_0_5_node_57 | 0.4 | n |  | TRUE
86 | bus_LV_2701-296_0_5_node_58 | 0.4 | n |  | TRUE
87 | bus_LV_2701-296_0_5_node_59 | 0.4 | n |  | TRUE
88 | bus_LV_2701-296_0_5_node_60 | 0.4 | n |  | TRUE
89 | bus_LV_2701-296_0_5_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_2701-296_0_5_node_83 | 0.4 | n |  | TRUE
91 | bus_LV_2701-296_0_5_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_2701-296_0_5_node_81 | 0.4 | n |  | TRUE
93 | bus_LV_2701-296_0_5_node_92 | 0.4 | n |  | TRUE
94 | bus_LV_2701-296_0_5_node_62 | 0.4 | n |  | TRUE
95 | bus_LV_2701-296_0_5_node_63 | 0.4 | n |  | TRUE
96 | bus_LV_2701-296_0_5_node_64 | 0.4 | n |  | TRUE
97 | bus_LV_2701-296_0_5_node_65 | 0.4 | n |  | TRUE
98 | bus_LV_2701-296_0_5_node_66 | 0.4 | n |  | TRUE
99 | bus_LV_2701-296_0_5_node_67 | 0.4 | n |  | TRUE
100 | bus_LV_2701-296_0_5_node_68 | 0.4 | n |  | TRUE
101 | bus_LV_2701-296_0_5_node_98 | 0.4 | n |  | TRUE
102 | bus_LV_2701-296_0_5_node_127 | 0.4 | n |  | TRUE
103 | bus_LV_2701-296_0_5_node_114 | 0.4 | n |  | TRUE
104 | bus_LV_2701-296_0_5_node_69 | 0.4 | n |  | TRUE
105 | bus_LV_2701-296_0_5_node_99 | 0.4 | n |  | TRUE
106 | bus_LV_2701-296_0_5_node_89 | 0.4 | n |  | TRUE
107 | bus_LV_2701-296_0_5_node_113 | 0.4 | n |  | TRUE
108 | bus_LV_2701-296_0_5_node_70 | 0.4 | n |  | TRUE
109 | bus_LV_2701-296_0_5_node_73 | 0.4 | n |  | TRUE
110 | bus_LV_2701-296_0_5_node_75 | 0.4 | n |  | TRUE
111 | bus_LV_2701-296_0_5_node_78 | 0.4 | n |  | TRUE
112 | bus_LV_2701-296_0_5_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_2701-296_0_5_node_79 | 0.4 | n |  | TRUE
114 | bus_LV_2701-296_0_5_node_136 | 0.4 | n |  | TRUE
115 | bus_LV_2701-296_0_5_node_134 | 0.4 | n |  | TRUE
116 | bus_LV_2701-296_0_5_node_138 | 0.4 | n |  | TRUE
117 | bus_LV_2701-296_0_5_node_80 | 0.4 | n |  | TRUE
118 | bus_LV_2701-296_0_5_node_82 | 0.4 | n |  | TRUE
119 | bus_LV_2701-296_0_5_node_84 | 0.4 | n |  | TRUE
120 | bus_LV_2701-296_0_5_node_95 | 0.4 | n |  | TRUE
121 | bus_LV_2701-296_0_5_node_111 | 0.4 | n |  | TRUE
122 | bus_LV_2701-296_0_5_node_109 | 0.4 | n |  | TRUE
123 | bus_LV_2701-296_0_5_node_85 | 0.4 | n |  | TRUE
124 | bus_LV_2701-296_0_5_node_86 | 0.4 | n |  | TRUE
125 | bus_LV_2701-296_0_5_node_87 | 0.4 | n |  | TRUE
126 | bus_LV_2701-296_0_5_node_88 | 0.4 | n |  | TRUE
127 | bus_LV_2701-296_0_5_node_91 | 0.4 | n |  | TRUE
128 | bus_LV_2701-296_0_5_node_129 | 0.4 | n |  | TRUE
129 | bus_LV_2701-296_0_5_node_105 | 0.4 | n |  | TRUE
130 | bus_LV_2701-296_0_5_node_110 | 0.4 | n |  | TRUE
131 | bus_LV_2701-296_0_5_node_115 | 0.4 | n |  | TRUE
132 | bus_LV_2701-296_0_5_node_120 | 0.4 | n |  | TRUE
133 | bus_LV_2701-296_0_5_node_122 | 0.4 | n |  | TRUE
134 | bus_LV_2701-296_0_5_node_124 | 0.4 | n |  | TRUE
135 | bus_LV_2701-296_0_5_node_128 | 0.4 | n |  | TRUE
136 | bus_MV_558_0_node_50 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-296_0_5_load_0 | 0 | 0.0025541 | 0.00064011 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-296_0_5_load_1 | 1 | 0.0024738 | 0.00061999 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-296_0_5_load_2 | 2 | 0.0024646 | 0.00061768 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-296_0_5_load_3 | 3 | 0.0034748 | 0.00087087 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-296_0_5_load_4 | 4 | 0.0030636 | 0.00076781 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-296_0_5_load_11 | 6 | 0.0055579 | 0.0013929 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-296_0_5_load_12 | 7 | 0.0040073 | 0.0010043 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-296_0_5_load_5 | 9 | 0.0027017 | 0.0006771 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-296_0_5_load_6 | 10 | 0.0040186 | 0.0010072 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-296_0_5_load_7 | 11 | 0.0026823 | 0.00067225 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-296_0_5_load_8 | 12 | 0.0042549 | 0.0010664 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-296_0_5_load_9 | 13 | 0.003325 | 0.00083333 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-296_0_5_load_24 | 14 | 0.0040946 | 0.0010262 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-296_0_5_load_74 | 15 | 0.0070256 | 0.0017608 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-296_0_5_load_107 | 16 | 0.0086987 | 0.0021801 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-296_0_5_load_22 | 17 | 0.0092162 | 0.0023098 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-296_0_5_load_72 | 18 | 0.0036484 | 0.00091437 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-296_0_5_load_108 | 19 | 0.0031106 | 0.0007796 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-296_0_5_load_135 | 21 | 0.038099 | 0.0095484 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-296_0_5_load_130 | 23 | 0.0176 | 0.004411 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-296_0_5_load_16 | 24 | 0.0037626 | 0.00094299 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-296_0_5_load_17 | 25 | 0.0034321 | 0.00086016 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-296_0_5_load_18 | 26 | 0.0038904 | 0.00097503 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-296_0_5_load_20 | 28 | 0.0035987 | 0.00090193 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-296_0_5_load_25 | 29 | 0.0051772 | 0.0012975 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-296_0_5_load_23 | 30 | 0.0035952 | 0.00090104 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-296_0_5_load_40 | 31 | 0.0075232 | 0.0018855 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-296_0_5_load_126 | 33 | 0.0016986 | 0.00042572 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-296_0_5_load_123 | 34 | 0.0018218 | 0.00045659 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-296_0_5_load_44 | 38 | 0.0074392 | 0.0018644 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-296_0_5_load_41 | 39 | 0.0053486 | 0.0013405 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-296_0_5_load_43 | 40 | 0.0098192 | 0.0024609 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-296_0_5_load_141 | 43 | 0.0015175 | 0.00038032 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-296_0_5_load_93 | 47 | 0.0058686 | 0.0014708 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-296_0_5_load_119 | 50 | 0.0025736 | 0.00064501 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-296_0_5_load_106 | 52 | 0.0054439 | 0.0013644 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-296_0_5_load_143 | 53 | 0.0013524 | 0.00033895 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-296_0_5_load_103 | 54 | 0.0094769 | 0.0023751 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-296_0_5_load_21 | 55 | 0.0054931 | 0.0013767 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-296_0_5_load_121 | 56 | 0.0018244 | 0.00045724 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-296_0_5_load_45 | 57 | 0.0074718 | 0.0018726 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2701-296_0_5_load_42 | 58 | 0.0053056 | 0.0013297 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2701-296_0_5_load_139 | 59 | 0.0015352 | 0.00038476 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2701-296_0_5_load_137 | 60 | 0.0082148 | 0.0020588 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2701-296_0_5_load_102 | 61 | 0.0052214 | 0.0013086 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2701-296_0_5_load_101 | 62 | 0.015474 | 0.0038782 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2701-296_0_5_load_94 | 63 | 0.0045521 | 0.0011409 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2701-296_0_5_load_142 | 64 | 0.0013938 | 0.00034932 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2701-296_0_5_load_140 | 65 | 0.0013766 | 0.00034501 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2701-296_0_5_load_117 | 66 | 0.00077445 | 0.0001941 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2701-296_0_5_load_104 | 67 | 0.0014931 | 0.00037421 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2701-296_0_5_load_47 | 68 | 0.0052646 | 0.0013194 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2701-296_0_5_load_46 | 69 | 0.0052518 | 0.0013162 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2701-296_0_5_load_48 | 70 | 0.017945 | 0.0044974 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2701-296_0_5_load_49 | 71 | 0.0032418 | 0.00081248 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2701-296_0_5_load_50 | 72 | 0.0010795 | 0.00027055 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2701-296_0_5_load_51 | 73 | 0.0007713 | 0.00019331 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2701-296_0_5_load_52 | 74 | 0.0008387 | 0.0002102 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2701-296_0_5_load_118 | 75 | 0.0025012 | 0.00062685 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2701-296_0_5_load_125 | 76 | 0.0032299 | 0.0008095 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2701-296_0_5_load_116 | 77 | 0.00077227 | 0.00019355 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2701-296_0_5_load_112 | 78 | 0.0013135 | 0.00032919 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2701-296_0_5_load_53 | 79 | 0.0039919 | 0.0010005 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2701-296_0_5_load_54 | 80 | 0.0039938 | 0.0010009 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2701-296_0_5_load_55 | 81 | 0.0039523 | 0.00099053 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2701-296_0_5_load_61 | 82 | 0.0039484 | 0.00098956 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2701-296_0_5_load_90 | 83 | 0.0063786 | 0.0015986 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2701-296_0_5_load_56 | 84 | 0.0061359 | 0.0015378 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2701-296_0_5_load_57 | 85 | 0.0056829 | 0.0014243 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2701-296_0_5_load_58 | 86 | 0.0058158 | 0.0014576 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2701-296_0_5_load_59 | 87 | 0.007412 | 0.0018576 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2701-296_0_5_load_60 | 88 | 0.0061718 | 0.0015468 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2701-296_0_5_load_76 | 89 | 0.0066892 | 0.0016765 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2701-296_0_5_load_83 | 90 | 0.0059213 | 0.001484 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2701-296_0_5_load_77 | 91 | 0.0069258 | 0.0017358 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2701-296_0_5_load_81 | 92 | 0.0047003 | 0.001178 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2701-296_0_5_load_92 | 93 | 0.0039499 | 0.00098993 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2701-296_0_5_load_62 | 94 | 0.0026306 | 0.0006593 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2701-296_0_5_load_63 | 95 | 0.0023116 | 0.00057934 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2701-296_0_5_load_64 | 96 | 0.0016514 | 0.00041389 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2701-296_0_5_load_66 | 98 | 0.0015783 | 0.00039556 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2701-296_0_5_load_68 | 100 | 0.01421 | 0.0035614 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2701-296_0_5_load_98 | 101 | 0.0024801 | 0.00062158 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2701-296_0_5_load_127 | 102 | 0.0014919 | 0.00037391 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2701-296_0_5_load_114 | 103 | 0.0014929 | 0.00037416 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2701-296_0_5_load_69 | 104 | 0.0038361 | 0.00096142 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2701-296_0_5_load_99 | 105 | 0.001545 | 0.00038721 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2701-296_0_5_load_89 | 106 | 0.0015393 | 0.00038577 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2701-296_0_5_load_113 | 107 | 0.0014931 | 0.0003742 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2701-296_0_5_load_70 | 108 | 0.0032618 | 0.00081749 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2701-296_0_5_load_73 | 109 | 0.0036319 | 0.00091025 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2701-296_0_5_load_75 | 110 | 0.0072478 | 0.0018165 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2701-296_0_5_load_78 | 111 | 0.003991 | 0.0010002 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2701-296_0_5_load_100 | 112 | 0.0039964 | 0.0010016 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2701-296_0_5_load_136 | 114 | 0.0044562 | 0.0011168 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2701-296_0_5_load_134 | 115 | 0.0040089 | 0.0010047 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2701-296_0_5_load_138 | 116 | 0.0049036 | 0.001229 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2701-296_0_5_load_80 | 117 | 0.0076792 | 0.0019246 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2701-296_0_5_load_82 | 118 | 0.0065183 | 0.0016336 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2701-296_0_5_load_95 | 120 | 0.0077891 | 0.0019521 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2701-296_0_5_load_109 | 122 | 0.0021554 | 0.0005402 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2701-296_0_5_load_85 | 123 | 0.0040144 | 0.0010061 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2701-296_0_5_load_86 | 124 | 0.0039461 | 0.00098899 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2701-296_0_5_load_87 | 125 | 0.0029893 | 0.0007492 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2701-296_0_5_load_88 | 126 | 0.0039441 | 0.00098848 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2701-296_0_5_load_91 | 127 | 0.0039539 | 0.00099093 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2701-296_0_5_load_129 | 128 | 0.0021033 | 0.00052714 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2701-296_0_5_load_105 | 129 | 0.0014934 | 0.00037427 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2701-296_0_5_load_110 | 130 | 0.0033272 | 0.00083388 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2701-296_0_5_load_115 | 131 | 0.0024907 | 0.00062423 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2701-296_0_5_load_120 | 132 | 0.0018259 | 0.00045762 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2701-296_0_5_load_122 | 133 | 0.0018214 | 0.00045648 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2701-296_0_5_load_124 | 134 | 0.0018826 | 0.00047182 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2701-296_0_5_load_128 | 135 | 0.0034741 | 0.00087068 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 125 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-296_0_5_line_0 |  | 0 | 1 | 0.0079105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-296_0_5_line_1 |  | 0 | 2 | 0.0075903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-296_0_5_line_2 |  | 1 | 3 | 0.008266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-296_0_5_line_3 |  | 2 | 4 | 0.0081888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-296_0_5_line_4 |  | 4 | 5 | 0.010573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-296_0_5_line_5 |  | 5 | 6 | 0.014892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2701-296_0_5_line_6 |  | 5 | 7 | 0.016268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-296_0_5_line_7 |  | 5 | 8 | 0.005962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2701-296_0_5_line_8 |  | 6 | 14 | 0.013008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2701-296_0_5_line_9 |  | 7 | 12 | 0.0078196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-296_0_5_line_10 |  | 8 | 15 | 0.0044696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2701-296_0_5_line_11 |  | 8 | 16 | 0.019494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-296_0_5_line_12 |  | 9 | 10 | 5.3321e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-296_0_5_line_13 |  | 9 | 11 | 0.0024953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-296_0_5_line_14 |  | 10 | 12 | 0.0081849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-296_0_5_line_15 |  | 11 | 13 | 0.0051227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-296_0_5_line_16 |  | 14 | 17 | 0.013897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2701-296_0_5_line_17 |  | 15 | 18 | 0.025964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2701-296_0_5_line_18 |  | 16 | 19 | 0.0041519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-296_0_5_line_19 |  | 17 | 55 | 0.014136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_2701-296_0_5_line_20 |  | 18 | 109 | 0.00799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2701-296_0_5_line_21 |  | 20 | 21 | 0.068776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-296_0_5_line_22 |  | 20 | 22 | 0.047802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-296_0_5_line_23 |  | 21 | 113 | 0.02516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-296_0_5_line_24 |  | 22 | 23 | 0.061683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-296_0_5_line_25 |  | 24 | 25 | 0.0081122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-296_0_5_line_26 |  | 24 | 26 | 0.0076281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-296_0_5_line_27 |  | 25 | 27 | 0.017731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-296_0_5_line_28 |  | 26 | 28 | 0.0086192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2701-296_0_5_line_29 |  | 27 | 29 | 0.0088823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-296_0_5_line_30 |  | 28 | 30 | 0.0082464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2701-296_0_5_line_31 |  | 29 | 31 | 0.015587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-296_0_5_line_32 |  | 30 | 55 | 0.010358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2701-296_0_5_line_33 |  | 31 | 36 | 0.011322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-296_0_5_line_34 |  | 32 | 33 | 0.0069626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2701-296_0_5_line_35 |  | 32 | 34 | 0.011347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2701-296_0_5_line_36 |  | 33 | 51 | 0.017337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2701-296_0_5_line_37 |  | 34 | 56 | 0.004553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_2701-296_0_5_line_38 |  | 35 | 36 | 0.044741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2701-296_0_5_line_39 |  | 35 | 37 | 0.014278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2701-296_0_5_line_40 |  | 35 | 38 | 0.013276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2701-296_0_5_line_41 |  | 36 | 39 | 0.029661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-296_0_5_line_42 |  | 37 | 40 | 0.0081459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-296_0_5_line_43 |  | 38 | 57 | 0.016709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-296_0_5_line_44 |  | 39 | 58 | 0.012617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2701-296_0_5_line_45 |  | 41 | 42 | 0.015375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2701-296_0_5_line_46 |  | 41 | 43 | 0.0038781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2701-296_0_5_line_47 |  | 42 | 45 | 0.026436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2701-296_0_5_line_48 |  | 42 | 53 | 0.02293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2701-296_0_5_line_49 |  | 43 | 59 | 0.017364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2701-296_0_5_line_50 |  | 44 | 45 | 0.006783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2701-296_0_5_line_51 |  | 44 | 46 | 0.0052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2701-296_0_5_line_52 |  | 44 | 47 | 0.049301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2701-296_0_5_line_53 |  | 45 | 60 | 0.0036998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2701-296_0_5_line_54 |  | 46 | 61 | 0.0031237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2701-296_0_5_line_55 |  | 46 | 62 | 0.024156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2701-296_0_5_line_56 |  | 47 | 63 | 0.0035846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2701-296_0_5_line_57 |  | 48 | 49 | 0.020069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2701-296_0_5_line_58 |  | 48 | 50 | 0.023887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_2701-296_0_5_line_59 |  | 49 | 52 | 0.11027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_2701-296_0_5_line_60 |  | 49 | 54 | 0.0082292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_2701-296_0_5_line_61 |  | 50 | 66 | 0.0061665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_2701-296_0_5_line_62 |  | 51 | 52 | 0.015062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_2701-296_0_5_line_63 |  | 54 | 67 | 0.030449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_2701-296_0_5_line_64 |  | 56 | 132 | 0.0061381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_2701-296_0_5_line_65 |  | 57 | 69 | 0.015232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2701-296_0_5_line_66 |  | 59 | 65 | 0.0072192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2701-296_0_5_line_67 |  | 63 | 120 | 0.011662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2701-296_0_5_line_68 |  | 64 | 65 | 0.0067385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2701-296_0_5_line_69 |  | 66 | 131 | 0.0020753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2701-296_0_5_line_70 |  | 67 | 129 | 0.0051481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_2701-296_0_5_line_71 |  | 68 | 69 | 0.012492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2701-296_0_5_line_72 |  | 70 | 71 | 0.0037568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_2701-296_0_5_line_73 |  | 70 | 72 | 7.9825e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_2701-296_0_5_line_74 |  | 71 | 73 | 0.0064083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_2701-296_0_5_line_75 |  | 72 | 74 | 0.0064962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_2701-296_0_5_line_76 |  | 73 | 75 | 0.0030012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_2701-296_0_5_line_77 |  | 74 | 76 | 0.00019959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_2701-296_0_5_line_78 |  | 75 | 77 | 0.0036144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_2701-296_0_5_line_79 |  | 76 | 78 | 0.0073881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_2701-296_0_5_line_80 |  | 77 | 131 | 0.0046368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_2701-296_0_5_line_81 |  | 78 | 130 | 0.0032803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_2701-296_0_5_line_82 |  | 79 | 80 | 0.00011393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2701-296_0_5_line_83 |  | 80 | 81 | 0.0085706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2701-296_0_5_line_84 |  | 81 | 82 | 0.00011003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2701-296_0_5_line_85 |  | 82 | 83 | 0.0026318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2701-296_0_5_line_86 |  | 83 | 93 | 0.0058981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2701-296_0_5_line_87 |  | 84 | 85 | 0.0068926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2701-296_0_5_line_88 |  | 84 | 86 | 0.0019286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2701-296_0_5_line_89 |  | 85 | 87 | 0.0018579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2701-296_0_5_line_90 |  | 86 | 88 | 0.0083239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2701-296_0_5_line_91 |  | 87 | 89 | 0.011143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2701-296_0_5_line_92 |  | 88 | 90 | 0.00057582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2701-296_0_5_line_93 |  | 89 | 91 | 0.00044408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2701-296_0_5_line_94 |  | 90 | 92 | 0.008511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2701-296_0_5_line_95 |  | 91 | 113 | 0.013892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2701-296_0_5_line_96 |  | 92 | 117 | 0.0025423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2701-296_0_5_line_97 |  | 93 | 127 | 0.00011643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2701-296_0_5_line_98 |  | 94 | 95 | 0.0085224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2701-296_0_5_line_99 |  | 94 | 96 | 0.0076265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2701-296_0_5_line_100 |  | 95 | 97 | 0.015824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2701-296_0_5_line_101 |  | 96 | 98 | 0.0063754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2701-296_0_5_line_102 |  | 97 | 99 | 0.025194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2701-296_0_5_line_103 |  | 97 | 100 | 0.0062196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2701-296_0_5_line_104 |  | 98 | 101 | 0.0075433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2701-296_0_5_line_105 |  | 99 | 102 | 0.014882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_2701-296_0_5_line_106 |  | 99 | 103 | 0.015506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_2701-296_0_5_line_107 |  | 100 | 104 | 0.0083582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2701-296_0_5_line_108 |  | 101 | 105 | 0.0090931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2701-296_0_5_line_109 |  | 102 | 106 | 0.0004839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_2701-296_0_5_line_110 |  | 103 | 107 | 0.0051222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_2701-296_0_5_line_111 |  | 104 | 108 | 0.022551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2701-296_0_5_line_112 |  | 106 | 125 | 0.0012825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_2701-296_0_5_line_113 |  | 107 | 129 | 0.0038552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_2701-296_0_5_line_114 |  | 109 | 110 | 0.016837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_2701-296_0_5_line_115 |  | 110 | 111 | 0.011377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_2701-296_0_5_line_116 |  | 111 | 112 | 0.0079527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_2701-296_0_5_line_117 |  | 112 | 115 | 0.0070518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_2701-296_0_5_line_118 |  | 113 | 114 | 0.022272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2701-296_0_5_line_119 |  | 114 | 116 | 0.0076975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2701-296_0_5_line_120 |  | 115 | 128 | 0.0077095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2701-296_0_5_line_121 |  | 117 | 118 | 0.0066786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2701-296_0_5_line_122 |  | 118 | 119 | 0.010668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2701-296_0_5_line_123 |  | 119 | 120 | 0.0015352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2701-296_0_5_line_124 |  | 119 | 121 | 0.005709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
125 | LV_2701-296_0_5_line_125 |  | 121 | 122 | 0.021429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_2701-296_0_5_line_126 |  | 122 | 130 | 0.0091222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_2701-296_0_5_line_127 |  | 123 | 124 | 0.0090256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2701-296_0_5_line_128 |  | 123 | 125 | 0.022464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2701-296_0_5_line_129 |  | 124 | 126 | 0.00012195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2701-296_0_5_line_130 |  | 126 | 127 | 0.0085175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2701-296_0_5_line_131 |  | 128 | 135 | 0.0092904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_2701-296_0_5_line_132 |  | 132 | 133 | 0.006176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_2701-296_0_5_line_133 |  | 133 | 134 | 0.0062758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_2701-296_0_5_line_134 |  | 134 | 135 | 0.0073393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-296_0_5_trafo_87 | 0.63 MVA 20/0.4 kV | 136 | 125 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2612192.598 | 1267746.5915 | 2612186.1057 | 1267742.0721
1 | 2612192.598 | 1267746.5915 | 2612198.8276 | 1267750.9281
2 | 2612179.3216 | 1267737.3495 | 2612186.1057 | 1267742.0721
3 | 2612205.5483 | 1267755.6065 | 2612198.8276 | 1267750.9281
4 | 2612214.2257 | 1267761.6471 | 2612205.5483 | 1267755.6065
5 | 2612214.2257 | 1267761.6471 | 2612226.9355 | 1267769.408
6 | 2612214.2257 | 1267761.6471 | 2612205.3324 | 1267775.2687
7 | 2612214.2257 | 1267761.6471 | 2612215.1921 | 1267760.1703 | 2612217.4873 | 1267756.6503
8 | 2612238.0375 | 1267776.1873 | 2612226.9355 | 1267769.408
9 | 2612201.0576 | 1267781.8163 | 2612205.3324 | 1267775.2687
10 | 2612217.4873 | 1267756.6503 | 2612221.2617 | 1267759.0444
11 | 2612217.4873 | 1267756.6503 | 2612201.3719 | 1267745.6816
12 | 2612196.5539 | 1267788.7145 | 2612196.583 | 1267788.6699
13 | 2612196.5539 | 1267788.7145 | 2612195.1897 | 1267790.8039
14 | 2612201.0576 | 1267781.8163 | 2612196.583 | 1267788.6699
15 | 2612192.3892 | 1267795.0934 | 2612195.1897 | 1267790.8039
16 | 2612238.0375 | 1267776.1873 | 2612249.8983 | 1267783.4297
17 | 2612243.3888 | 1267772.6111 | 2612237.5711 | 1267769.3895 | 2612221.2617 | 1267759.0444
18 | 2612201.3719 | 1267745.6816 | 2612197.9397 | 1267743.3455
19 | 2612249.8983 | 1267783.4297 | 2612252.8316 | 1267785.2209 | 2612262.4351 | 1267789.9379
20 | 2612243.3888 | 1267772.6111 | 2612250.3786 | 1267776.4818
21 | 2612229.3705 | 1267581.6076 | 2612297.7968 | 1267574.6831
22 | 2612195.9733 | 1267597.45 | 2612194.6601 | 1267584.5494 | 2612229.3705 | 1267581.6076
23 | 2612322.8745 | 1267572.8391 | 2612312.8185 | 1267573.1629 | 2612297.7968 | 1267574.6831
24 | 2612195.9733 | 1267597.45 | 2612257.4483 | 1267590.505
25 | 2612293.9549 | 1267804.7623 | 2612301.5124 | 1267807.7103
26 | 2612286.8705 | 1267801.9398 | 2612287.4544 | 1267802.2266 | 2612293.9549 | 1267804.7623
27 | 2612318.031 | 1267814.1538 | 2612301.5124 | 1267807.7103
28 | 2612279.1342 | 1267798.1399 | 2612286.8705 | 1267801.9398
29 | 2612318.031 | 1267814.1538 | 2612317.2469 | 1267823.0014
30 | 2612279.1342 | 1267798.1399 | 2612271.7324 | 1267794.5044
31 | 2612317.2469 | 1267823.0014 | 2612315.8708 | 1267838.5275
32 | 2612271.7324 | 1267794.5044 | 2612262.4351 | 1267789.9379
33 | 2612314.8713 | 1267849.8056 | 2612315.8708 | 1267838.5275
34 | 2612344.021 | 1267816.6985 | 2612348.1709 | 1267811.6258 | 2612348.5711 | 1267811.5431
35 | 2612344.021 | 1267816.6985 | 2612333.8125 | 1267811.7438
36 | 2612365.7583 | 1267812.1961 | 2612352.2217 | 1267810.7892 | 2612348.5711 | 1267811.5431
37 | 2612329.5882 | 1267810.0595 | 2612332.5401 | 1267811.1263 | 2612333.8125 | 1267811.7438
38 | 2612314.8713 | 1267849.8056 | 2612338.6061 | 1267840.1481 | 2612342.3954 | 1267845.6265 | 2612351.3711 | 1267854.2623
39 | 2612351.3711 | 1267854.2623 | 2612359.8965 | 1267851.4336 | 2612365.0846 | 1267850.188
40 | 2612351.3711 | 1267854.2623 | 2612339.2237 | 1267859.6177
41 | 2612314.8713 | 1267849.8056 | 2612310.8689 | 1267849.0857 | 2612287.2398 | 1267858.9224
42 | 2612365.0846 | 1267850.188 | 2612365.4697 | 1267853.1576 | 2612365.4485 | 1267856.1151 | 2612365.2931 | 1267858.3034
43 | 2612339.2237 | 1267859.6177 | 2612323.9345 | 1267866.3582
44 | 2612275.5921 | 1267863.7721 | 2612275.6014 | 1267863.7675 | 2612287.2398 | 1267858.9224
45 | 2612504.1131 | 1267575.5309 | 2612488.7 | 1267575.0425
46 | 2612504.1131 | 1267575.5309 | 2612507.9744 | 1267575.8913
47 | 2612462.2094 | 1267573.8861 | 2612488.7 | 1267575.0425
48 | 2612488.7 | 1267575.0425 | 2612492.1302 | 1267552.3702
49 | 2612525.263 | 1267577.5053 | 2612507.9744 | 1267575.8913
50 | 2612462.1349 | 1267580.6685 | 2612462.2094 | 1267573.8861
51 | 2612462.1349 | 1267580.6685 | 2612461.5671 | 1267585.8376
52 | 2612462.1349 | 1267580.6685 | 2612436.7381 | 1267578.3247 | 2612413.0419 | 1267576.1422
53 | 2612462.2094 | 1267573.8861 | 2612458.5245 | 1267573.554
54 | 2612461.5671 | 1267585.8376 | 2612464.6644 | 1267586.243
55 | 2612461.5671 | 1267585.8376 | 2612437.4205 | 1267585.1624
56 | 2612409.4725 | 1267575.8135 | 2612413.0419 | 1267576.1422
57 | 2612377.7743 | 1267687.4447 | 2612391.5151 | 1267688.5074 | 2612391.7841 | 1267682.2258
58 | 2612391.7841 | 1267682.2258 | 2612392.79 | 1267658.3602
59 | 2612377.7743 | 1267687.4447 | 2612367.2024 | 1267797.203
60 | 2612377.7743 | 1267687.4447 | 2612369.7014 | 1267685.8483
61 | 2612392.79 | 1267658.3602 | 2612393.0497 | 1267652.1992
62 | 2612365.7583 | 1267812.1961 | 2612367.2024 | 1267797.203
63 | 2612369.7014 | 1267685.8483 | 2612358.6804 | 1267683.669 | 2612345.0135 | 1267679.6266 | 2612340.3196 | 1267678.0151
64 | 2612323.8143 | 1267807.9766 | 2612324.9896 | 1267808.3976 | 2612329.5882 | 1267810.0595
65 | 2612323.9345 | 1267866.3582 | 2612309.9966 | 1267872.503
66 | 2612525.263 | 1267577.5053 | 2612532.4509 | 1267578.1763
67 | 2612409.4725 | 1267575.8135 | 2612407.338 | 1267575.6169 | 2612397.8311 | 1267575.147
68 | 2612532.4509 | 1267578.1763 | 2612539.1603 | 1267578.8026
69 | 2612393.1371 | 1267650.1258 | 2612393.0497 | 1267652.1992
70 | 2612340.3196 | 1267678.0151 | 2612335.4505 | 1267676.3435
71 | 2612309.9966 | 1267872.503 | 2612298.5666 | 1267877.5421
72 | 2612394.039 | 1267628.7274 | 2612393.8808 | 1267632.4808
73 | 2612394.0423 | 1267628.6476 | 2612394.039 | 1267628.7274
74 | 2612393.6109 | 1267638.8834 | 2612393.8808 | 1267632.4808
75 | 2612394.3159 | 1267622.1572 | 2612394.0423 | 1267628.6476
76 | 2612393.4845 | 1267641.8819 | 2612393.6109 | 1267638.8834
77 | 2612394.3243 | 1267621.9578 | 2612394.3159 | 1267622.1572
78 | 2612393.4845 | 1267641.8819 | 2612393.3323 | 1267645.4931
79 | 2612394.3243 | 1267621.9578 | 2612394.6354 | 1267614.5762
80 | 2612393.1371 | 1267650.1258 | 2612393.3323 | 1267645.4931
81 | 2612394.7736 | 1267611.2988 | 2612394.6354 | 1267614.5762
82 | 2612286.6787 | 1267735.8364 | 2612286.7151 | 1267735.7284
83 | 2612286.7151 | 1267735.7284 | 2612289.4514 | 1267727.6064
84 | 2612289.4514 | 1267727.6064 | 2612289.4865 | 1267727.5021
85 | 2612289.4865 | 1267727.5021 | 2612290.3268 | 1267725.008
86 | 2612292.2098 | 1267719.4185 | 2612290.3268 | 1267725.008
87 | 2612350.2005 | 1267573.6179 | 2612357.0903 | 1267573.8143
88 | 2612359.0181 | 1267573.8692 | 2612357.0903 | 1267573.8143
89 | 2612350.2005 | 1267573.6179 | 2612348.3434 | 1267573.565
90 | 2612359.0181 | 1267573.8692 | 2612367.3387 | 1267574.1064
91 | 2612348.3434 | 1267573.565 | 2612337.2051 | 1267573.2475
92 | 2612367.3387 | 1267574.1064 | 2612367.9142 | 1267574.1228
93 | 2612336.7612 | 1267573.2349 | 2612337.2051 | 1267573.2475
94 | 2612376.4217 | 1267574.3652 | 2612367.9142 | 1267574.1228
95 | 2612322.8745 | 1267572.8391 | 2612336.7612 | 1267573.2349
96 | 2612376.4217 | 1267574.3652 | 2612378.963 | 1267574.4377
97 | 2612292.2098 | 1267719.4185 | 2612292.247 | 1267719.3082
98 | 2612278.3787 | 1267676.1498 | 2612281.8752 | 1267668.3776
99 | 2612278.3787 | 1267676.1498 | 2612275.2498 | 1267683.1048
100 | 2612290.3698 | 1267655.5186 | 2612286.1934 | 1267658.7789 | 2612281.8752 | 1267668.3776
101 | 2612272.6342 | 1267688.919 | 2612275.2498 | 1267683.1048
102 | 2612313.0388 | 1267666.5177 | 2612306.1741 | 1267663.2456 | 2612293.5439 | 1267656.448 | 2612290.3698 | 1267655.5186
103 | 2612290.3698 | 1267655.5186 | 2612288.7188 | 1267649.5221
104 | 2612269.5394 | 1267695.7982 | 2612272.6342 | 1267688.919
105 | 2612313.0388 | 1267666.5177 | 2612307.0664 | 1267680.1483
106 | 2612313.0388 | 1267666.5177 | 2612327.1604 | 1267672.9229
107 | 2612281.3859 | 1267645.5112 | 2612288.7188 | 1267649.5221 | 2612288.7188 | 1267649.5221
108 | 2612265.8088 | 1267704.0908 | 2612269.5394 | 1267695.7982
109 | 2612306.8722 | 1267680.5915 | 2612307.0664 | 1267680.1483
110 | 2612331.8252 | 1267675.0387 | 2612327.1604 | 1267672.9229
111 | 2612281.3859 | 1267645.5112 | 2612261.6014 | 1267634.6898
112 | 2612306.8722 | 1267680.5915 | 2612306.3575 | 1267681.7662
113 | 2612331.8252 | 1267675.0387 | 2612332.3708 | 1267675.2862 | 2612335.4505 | 1267676.3435
114 | 2612250.3786 | 1267776.4818 | 2612259.2969 | 1267781.4205 | 2612265.3644 | 1267784.125
115 | 2612265.3644 | 1267784.125 | 2612275.7563 | 1267788.7571
116 | 2612283.02 | 1267791.9949 | 2612275.7563 | 1267788.7571
117 | 2612289.4609 | 1267794.8659 | 2612283.02 | 1267791.9949
118 | 2612322.8745 | 1267572.8391 | 2612322.3492 | 1267550.5737
119 | 2612322.3492 | 1267550.5737 | 2612322.1676 | 1267542.8784
120 | 2612296.5025 | 1267798.0047 | 2612289.4609 | 1267794.8659
121 | 2612385.6374 | 1267574.6731 | 2612380.5312 | 1267574.4824 | 2612378.963 | 1267574.4377
122 | 2612396.2978 | 1267575.0712 | 2612385.6374 | 1267574.6731
123 | 2612396.2978 | 1267575.0712 | 2612397.8311 | 1267575.147
124 | 2612396.2978 | 1267575.0712 | 2612396.0601 | 1267580.7747
125 | 2612396.0601 | 1267580.7747 | 2612395.1577 | 1267602.1848
126 | 2612395.1577 | 1267602.1848 | 2612394.7736 | 1267611.2988
127 | 2612298.0156 | 1267702.6131 | 2612296.4047 | 1267706.9672 | 2612295.0053 | 1267711.1209
128 | 2612298.0156 | 1267702.6131 | 2612302.3158 | 1267690.9904 | 2612306.3575 | 1267681.7662
129 | 2612294.9664 | 1267711.2364 | 2612295.0053 | 1267711.1209
130 | 2612292.247 | 1267719.3082 | 2612294.9664 | 1267711.2364
131 | 2612296.5025 | 1267798.0047 | 2612298.6676 | 1267798.9697 | 2612305.1823 | 1267801.3031
132 | 2612323.8143 | 1267807.9766 | 2612318 | 1267805.8941
133 | 2612318 | 1267805.8941 | 2612312.0918 | 1267803.7779
134 | 2612312.0918 | 1267803.7779 | 2612305.1823 | 1267801.3031

## bus_geodata
| x | y | coords
0 | 2612192.598 | 1267746.5915
1 | 2612186.1057 | 1267742.0721
2 | 2612198.8276 | 1267750.9281
3 | 2612179.3216 | 1267737.3495
4 | 2612205.5483 | 1267755.6065
5 | 2612214.2257 | 1267761.6471
6 | 2612226.9354 | 1267769.408
7 | 2612205.3324 | 1267775.2687
8 | 2612217.4873 | 1267756.6503
9 | 2612196.5539 | 1267788.7145
10 | 2612196.583 | 1267788.6699
11 | 2612195.1897 | 1267790.8039
12 | 2612201.0576 | 1267781.8163
13 | 2612192.3892 | 1267795.0934
14 | 2612238.0375 | 1267776.1873
15 | 2612221.2617 | 1267759.0444
16 | 2612201.3719 | 1267745.6816
17 | 2612249.8983 | 1267783.4297
18 | 2612243.3888 | 1267772.6111
19 | 2612197.9397 | 1267743.3455
20 | 2612229.3705 | 1267581.6076
21 | 2612297.7968 | 1267574.6831
22 | 2612195.9733 | 1267597.45
23 | 2612257.4483 | 1267590.505
24 | 2612293.9549 | 1267804.7623
25 | 2612301.5124 | 1267807.7103
26 | 2612286.8705 | 1267801.9398
27 | 2612318.031 | 1267814.1538
28 | 2612279.1342 | 1267798.1399
29 | 2612317.2469 | 1267823.0014
30 | 2612271.7324 | 1267794.5044
31 | 2612315.8708 | 1267838.5275
32 | 2612344.021 | 1267816.6985
33 | 2612348.5711 | 1267811.5431
34 | 2612333.8125 | 1267811.7438
35 | 2612351.3711 | 1267854.2623
36 | 2612314.8713 | 1267849.8056
37 | 2612365.0846 | 1267850.188
38 | 2612339.2237 | 1267859.6177
39 | 2612287.2398 | 1267858.9224
40 | 2612365.2931 | 1267858.3034
41 | 2612504.1131 | 1267575.5309
42 | 2612488.7 | 1267575.0425
43 | 2612507.9744 | 1267575.8913
44 | 2612462.1349 | 1267580.6685
45 | 2612462.2094 | 1267573.8861
46 | 2612461.5671 | 1267585.8376
47 | 2612413.0419 | 1267576.1422
48 | 2612391.7841 | 1267682.2258
49 | 2612377.7743 | 1267687.4447
50 | 2612392.79 | 1267658.3602
51 | 2612365.7583 | 1267812.1961
52 | 2612367.2024 | 1267797.203
53 | 2612492.1302 | 1267552.3703
54 | 2612369.7014 | 1267685.8483
55 | 2612262.4351 | 1267789.9379
56 | 2612329.5882 | 1267810.0595
57 | 2612323.9345 | 1267866.3582
58 | 2612275.5921 | 1267863.7721
59 | 2612525.263 | 1267577.5053
60 | 2612458.5245 | 1267573.554
61 | 2612464.6644 | 1267586.243
62 | 2612437.4205 | 1267585.1624
63 | 2612409.4725 | 1267575.8135
64 | 2612539.1603 | 1267578.8026
65 | 2612532.4509 | 1267578.1763
66 | 2612393.0497 | 1267652.1992
67 | 2612340.3196 | 1267678.0151
68 | 2612298.5666 | 1267877.5421
69 | 2612309.9966 | 1267872.503
70 | 2612394.039 | 1267628.7274
71 | 2612393.8808 | 1267632.4808
72 | 2612394.0423 | 1267628.6476
73 | 2612393.6109 | 1267638.8834
74 | 2612394.3159 | 1267622.1572
75 | 2612393.4845 | 1267641.8819
76 | 2612394.3243 | 1267621.9578
77 | 2612393.3323 | 1267645.4931
78 | 2612394.6354 | 1267614.5762
79 | 2612286.6787 | 1267735.8364
80 | 2612286.7151 | 1267735.7284
81 | 2612289.4514 | 1267727.6064
82 | 2612289.4865 | 1267727.5021
83 | 2612290.3268 | 1267725.008
84 | 2612357.0903 | 1267573.8143
85 | 2612350.2005 | 1267573.6179
86 | 2612359.0181 | 1267573.8692
87 | 2612348.3434 | 1267573.565
88 | 2612367.3387 | 1267574.1064
89 | 2612337.2051 | 1267573.2475
90 | 2612367.9142 | 1267574.1228
91 | 2612336.7612 | 1267573.2349
92 | 2612376.4217 | 1267574.3652
93 | 2612292.2098 | 1267719.4185
94 | 2612278.3787 | 1267676.1498
95 | 2612281.8752 | 1267668.3776
96 | 2612275.2498 | 1267683.1048
97 | 2612290.3698 | 1267655.5186
98 | 2612272.6342 | 1267688.919
99 | 2612313.0388 | 1267666.5177
100 | 2612288.7188 | 1267649.5221
101 | 2612269.5394 | 1267695.7982
102 | 2612307.0664 | 1267680.1483
103 | 2612327.1604 | 1267672.9229
104 | 2612281.3859 | 1267645.5112
105 | 2612265.8088 | 1267704.0908
106 | 2612306.8722 | 1267680.5915
107 | 2612331.8252 | 1267675.0387
108 | 2612261.6014 | 1267634.6898
109 | 2612250.3786 | 1267776.4818
110 | 2612265.3644 | 1267784.125
111 | 2612275.7563 | 1267788.7571
112 | 2612283.02 | 1267791.9949
113 | 2612322.8745 | 1267572.8391
114 | 2612322.3492 | 1267550.5737
115 | 2612289.4609 | 1267794.8659
116 | 2612322.1676 | 1267542.8784
117 | 2612378.963 | 1267574.4377
118 | 2612385.6374 | 1267574.6731
119 | 2612396.2978 | 1267575.0712
120 | 2612397.8311 | 1267575.147
121 | 2612396.0601 | 1267580.7747
122 | 2612395.1577 | 1267602.1848
123 | 2612298.0156 | 1267702.6131
124 | 2612295.0053 | 1267711.1209
125 | 2612306.3575 | 1267681.7662
126 | 2612294.9664 | 1267711.2364
127 | 2612292.247 | 1267719.3082
128 | 2612296.5025 | 1267798.0046
129 | 2612335.4505 | 1267676.3435
130 | 2612394.7736 | 1267611.2988
131 | 2612393.1371 | 1267650.1258
132 | 2612323.8143 | 1267807.9766
133 | 2612318 | 1267805.8941
134 | 2612312.0918 | 1267803.7779
135 | 2612305.1823 | 1267801.3031
136 | 2612313.0388 | 1267666.5177

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97791 | -0.42416 | 0.0025541 | 0.00064011
1 | 0.97787 | -0.42502 | 0.0024738 | 0.00061999
2 | 0.97797 | -0.42298 | 0.0024646 | 0.00061768
3 | 0.97784 | -0.42554 | 0.0034748 | 0.00087087
4 | 0.97805 | -0.42135 | 0.0030636 | 0.00076781
5 | 0.97819 | -0.41864 | 0 | 0
6 | 0.97784 | -0.42551 | 0.0055579 | 0.0013929
7 | 0.97788 | -0.42486 | 0.0040073 | 0.0010043
8 | 0.97838 | -0.41494 | 0 | 0
9 | 0.97766 | -0.42919 | 0.0027017 | 0.0006771
10 | 0.97766 | -0.42918 | 0.0040186 | 0.0010072
11 | 0.97764 | -0.42947 | 0.0026823 | 0.00067225
12 | 0.97775 | -0.42729 | 0.0042549 | 0.0010664
13 | 0.97763 | -0.42978 | 0.003325 | 0.00083333
14 | 0.97755 | -0.43119 | 0.0040946 | 0.0010262
15 | 0.97854 | -0.41193 | 0.0070256 | 0.0017608
16 | 0.97817 | -0.41914 | 0.0086987 | 0.0021801
17 | 0.97726 | -0.43699 | 0.0092162 | 0.0023098
18 | 0.97947 | -0.39362 | 0.0036484 | 0.00091437
19 | 0.97816 | -0.41937 | 0.0031106 | 0.0007796
20 | 0.97532 | -0.47566 | 0 | 0
21 | 0.97645 | -0.4535 | 0.038099 | 0.0095484
22 | 0.97454 | -0.49109 | 0 | 0
23 | 0.97353 | -0.51103 | 0.0176 | 0.004411
24 | 0.97605 | -0.46063 | 0.0037626 | 0.00094299
25 | 0.97558 | -0.46984 | 0.0034321 | 0.00086016
26 | 0.97652 | -0.45145 | 0.0038904 | 0.00097503
27 | 0.97461 | -0.48889 | 0 | 0
28 | 0.97666 | -0.44871 | 0.0035987 | 0.00090193
29 | 0.97412 | -0.49845 | 0.0051772 | 0.0012975
30 | 0.9768 | -0.44594 | 0.0035952 | 0.00090104
31 | 0.97335 | -0.51376 | 0.0075232 | 0.0018855
32 | 0.98405 | -0.3045 | 0 | 0
33 | 0.98437 | -0.29835 | 0.0016986 | 0.00042572
34 | 0.98353 | -0.31454 | 0.0018218 | 0.00045659
35 | 0.97139 | -0.55241 | 0 | 0
36 | 0.97286 | -0.52332 | 0 | 0
37 | 0.97126 | -0.555 | 0 | 0
38 | 0.97107 | -0.55865 | 0.0074392 | 0.0018644
39 | 0.97257 | -0.52914 | 0.0053486 | 0.0013405
40 | 0.97118 | -0.55648 | 0.0098192 | 0.0024609
41 | 0.98182 | -0.34862 | 0 | 0
42 | 0.9819 | -0.347 | 0 | 0
43 | 0.9818 | -0.34903 | 0.0015175 | 0.00038032
44 | 0.98217 | -0.34169 | 0 | 0
45 | 0.98208 | -0.34357 | 0 | 0
46 | 0.98208 | -0.34363 | 0 | 0
47 | 0.98382 | -0.30959 | 0.0058686 | 0.0014708
48 | 0.98999 | -0.1901 | 0 | 0
49 | 0.99107 | -0.16942 | 0 | 0
50 | 0.98871 | -0.21478 | 0.0025736 | 0.00064501
51 | 0.98517 | -0.28292 | 0 | 0
52 | 0.98586 | -0.26953 | 0.0054439 | 0.0013644
53 | 0.98187 | -0.34756 | 0.0013524 | 0.00033895
54 | 0.9919 | -0.15353 | 0.0094769 | 0.0023751
55 | 0.97698 | -0.44231 | 0.0054931 | 0.0013767
56 | 0.98333 | -0.31853 | 0.0018244 | 0.00045724
57 | 0.97079 | -0.5642 | 0.0074718 | 0.0018726
58 | 0.9725 | -0.53038 | 0.0053056 | 0.0013297
59 | 0.98173 | -0.35038 | 0.0015352 | 0.00038476
60 | 0.98205 | -0.34412 | 0.0082148 | 0.0020588
61 | 0.98206 | -0.34393 | 0.0052214 | 0.0013086
62 | 0.98173 | -0.35039 | 0.015474 | 0.0038782
63 | 0.98396 | -0.30688 | 0.0045521 | 0.0011409
64 | 0.9817 | -0.35092 | 0.0013938 | 0.00034932
65 | 0.98171 | -0.35075 | 0.0013766 | 0.00034501
66 | 0.98839 | -0.22109 | 0.00077445 | 0.0001941
67 | 0.99504 | -0.093697 | 0.0014931 | 0.00037421
68 | 0.97058 | -0.56838 | 0.0052646 | 0.0013194
69 | 0.97064 | -0.56717 | 0.0052518 | 0.0013162
70 | 0.98717 | -0.24455 | 0.017945 | 0.0044974
71 | 0.98736 | -0.24087 | 0.0032418 | 0.00081248
72 | 0.98717 | -0.24462 | 0.0010795 | 0.00027055
73 | 0.98769 | -0.23451 | 0.0007713 | 0.00019331
74 | 0.98687 | -0.25043 | 0.0008387 | 0.0002102
75 | 0.98784 | -0.23152 | 0.0025012 | 0.00062685
76 | 0.98686 | -0.25061 | 0.0032299 | 0.0008095
77 | 0.98803 | -0.22789 | 0.00077227 | 0.00019355
78 | 0.98652 | -0.25708 | 0.0013135 | 0.00032919
79 | 0.99837 | -0.031358 | 0.0039919 | 0.0010005
80 | 0.99837 | -0.03135 | 0.0039938 | 0.0010009
81 | 0.99843 | -0.030153 | 0.0039523 | 0.00099053
82 | 0.99843 | -0.03013 | 0.0039484 | 0.00098956
83 | 0.99847 | -0.029399 | 0.0063786 | 0.0015986
84 | 0.98017 | -0.38053 | 0.0061359 | 0.0015378
85 | 0.97959 | -0.39202 | 0.0056829 | 0.0014243
86 | 0.98035 | -0.37711 | 0.0058158 | 0.0014576
87 | 0.97944 | -0.39492 | 0.007412 | 0.0018576
88 | 0.98115 | -0.36146 | 0.0061718 | 0.0015468
89 | 0.97862 | -0.41086 | 0.0066892 | 0.0016765
90 | 0.98121 | -0.36032 | 0.0059213 | 0.001484
91 | 0.97859 | -0.41145 | 0.0069258 | 0.0017358
92 | 0.98212 | -0.34249 | 0.0047003 | 0.001178
93 | 0.99859 | -0.027103 | 0.0039499 | 0.00098993
94 | 0.99711 | -0.05488 | 0.0026306 | 0.0006593
95 | 0.99719 | -0.053403 | 0.0023116 | 0.00057934
96 | 0.99706 | -0.05585 | 0.0016514 | 0.00041389
97 | 0.99736 | -0.05002 | 0 | 0
98 | 0.99703 | -0.056476 | 0.0015783 | 0.00039556
99 | 0.99813 | -0.035239 | 0 | 0
100 | 0.99724 | -0.052343 | 0.01421 | 0.0035614
101 | 0.997 | -0.057009 | 0.0024801 | 0.00062158
102 | 0.9998 | -0.0037508 | 0.0014919 | 0.00037391
103 | 0.99651 | -0.065882 | 0.0014929 | 0.00037416
104 | 0.99719 | -0.053383 | 0.0038361 | 0.00096142
105 | 0.99699 | -0.057255 | 0.001545 | 0.00038721
106 | 0.99986 | -0.0027255 | 0.0015393 | 0.00038577
107 | 0.99598 | -0.075992 | 0.0014931 | 0.0003742
108 | 0.99712 | -0.054672 | 0.0032618 | 0.00081749
109 | 0.97977 | -0.38786 | 0.0036319 | 0.00091025
110 | 0.9804 | -0.37546 | 0.0072478 | 0.0018165
111 | 0.98085 | -0.36671 | 0.003991 | 0.0010002
112 | 0.98117 | -0.36046 | 0.0039964 | 0.0010016
113 | 0.97775 | -0.42791 | 0 | 0
114 | 0.97756 | -0.43171 | 0.0044562 | 0.0011168
115 | 0.98146 | -0.35479 | 0.0040089 | 0.0010047
116 | 0.97753 | -0.4324 | 0.0049036 | 0.001229
117 | 0.98241 | -0.33695 | 0.0076792 | 0.0019246
118 | 0.9832 | -0.3215 | 0.0065183 | 0.0016336
119 | 0.98453 | -0.29562 | 0 | 0
120 | 0.98446 | -0.29712 | 0.0077891 | 0.0019521
121 | 0.98503 | -0.28593 | 0 | 0
122 | 0.98597 | -0.26775 | 0.0021554 | 0.0005402
123 | 0.99914 | -0.016487 | 0.0040144 | 0.0010061
124 | 0.99883 | -0.022487 | 0.0039461 | 0.00098899
125 | 1 | 0 | -0.54001 | -0.13829
126 | 0.99883 | -0.02256 | 0.0039441 | 0.00098848
127 | 0.99859 | -0.02705 | 0.0039539 | 0.00099093
128 | 0.98179 | -0.34846 | 0.0021033 | 0.00052714
129 | 0.99558 | -0.083584 | 0.0014934 | 0.00037427
130 | 0.98637 | -0.25994 | 0.0033272 | 0.00083388
131 | 0.98828 | -0.22321 | 0.0024907 | 0.00062423
132 | 0.98305 | -0.32386 | 0.0018259 | 0.00045762
133 | 0.98278 | -0.32918 | 0.0018214 | 0.00045648
134 | 0.9825 | -0.33454 | 0.0018826 | 0.00047182
135 | 0.98218 | -0.34074 | 0.0034741 | 0.00087068
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0059489 | 0.0014909 | -0.0059487 | -0.0014908 | 2.4307e-07 | 5.6321e-08 | 0.009052 | 0.009052 | 0.009052 | 0.97791 | -0.42416 | 0.97787 | -0.42502 | 2.4868
1 | -0.008503 | -0.002131 | 0.0085034 | 0.0021312 | 4.7648e-07 | 2.0971e-07 | 0.012938 | 0.012938 | 0.012938 | 0.97791 | -0.42416 | 0.97797 | -0.42298 | 3.5545
2 | 0.0034749 | 0.00087082 | -0.0034748 | -0.00087087 | 8.6668e-08 | -4.8226e-08 | 0.0052877 | 0.0052877 | 0.0052877 | 0.97787 | -0.42502 | 0.97784 | -0.42554 | 1.4527
3 | -0.010968 | -0.0027489 | 0.010969 | 0.0027493 | 8.552e-07 | 4.4457e-07 | 0.016688 | 0.016688 | 0.016688 | 0.97797 | -0.42298 | 0.97805 | -0.42135 | 4.5847
4 | -0.014032 | -0.0035171 | 0.014034 | 0.0035181 | 1.8071e-06 | 1.0238e-06 | 0.021349 | 0.021349 | 0.021349 | 0.97805 | -0.42135 | 0.97819 | -0.41864 | 5.8651
5 | 0.10165 | 0.025625 | -0.10161 | -0.025604 | 3.3402e-05 | 2.063e-05 | 0.15468 | 0.15468 | 0.15468 | 0.97819 | -0.41864 | 0.97784 | -0.42551 | 10.6234
6 | 0.020999 | 0.0052661 | -0.020993 | -0.0052623 | 6.2254e-06 | 3.7801e-06 | 0.031945 | 0.031945 | 0.031945 | 0.97819 | -0.41864 | 0.97788 | -0.42486 | 8.7761
7 | -0.13668 | -0.034409 | 0.1367 | 0.034424 | 2.4175e-05 | 1.5173e-05 | 0.20797 | 0.20797 | 0.20797 | 0.97819 | -0.41864 | 0.97838 | -0.41494 | 14.2837
8 | 0.096054 | 0.024211 | -0.096028 | -0.024195 | 2.6073e-05 | 1.6034e-05 | 0.14622 | 0.14622 | 0.14622 | 0.97784 | -0.42551 | 0.97755 | -0.43119 | 10.0425
9 | 0.016986 | 0.004258 | -0.016984 | -0.0042568 | 1.959e-06 | 1.1557e-06 | 0.025847 | 0.025847 | 0.025847 | 0.97788 | -0.42486 | 0.97775 | -0.42729 | 7.1009
10 | -0.14851 | -0.037385 | 0.14854 | 0.037399 | 2.139e-05 | 1.3465e-05 | 0.22593 | 0.22593 | 0.22593 | 0.97838 | -0.41494 | 0.97854 | -0.41193 | 15.5175
11 | 0.011812 | 0.0029609 | -0.011809 | -0.0029597 | 2.3592e-06 | 1.2652e-06 | 0.017965 | 0.017965 | 0.017965 | 0.97838 | -0.41494 | 0.97817 | -0.41914 | 4.9354
12 | -0.0087091 | -0.0021827 | 0.0087091 | 0.0021827 | 3.5119e-09 | 1.5799e-09 | 0.013255 | 0.013255 | 0.013255 | 0.97766 | -0.42919 | 0.97766 | -0.42918 | 3.6416
13 | 0.0060074 | 0.0015056 | -0.0060074 | -0.0015055 | 7.8231e-08 | 1.8778e-08 | 0.0091435 | 0.0091435 | 0.0091435 | 0.97766 | -0.42919 | 0.97764 | -0.42947 | 2.5119
14 | -0.012728 | -0.0031898 | 0.012729 | 0.0031905 | 1.1518e-06 | 6.3452e-07 | 0.019372 | 0.019372 | 0.019372 | 0.97766 | -0.42918 | 0.97775 | -0.42729 | 5.3219
15 | 0.0033251 | 0.00083329 | -0.003325 | -0.00083333 | 4.9202e-08 | -3.2744e-08 | 0.0050609 | 0.0050609 | 0.0050609 | 0.97764 | -0.42947 | 0.97763 | -0.42978 | 1.3904
16 | 0.091934 | 0.023169 | -0.091908 | -0.023153 | 2.5531e-05 | 1.5643e-05 | 0.13999 | 0.13999 | 0.13999 | 0.97755 | -0.43119 | 0.97726 | -0.43699 | 9.6145
17 | -0.15556 | -0.039159 | 0.1557 | 0.039245 | 0.00013628 | 8.5914e-05 | 0.23662 | 0.23662 | 0.23662 | 0.97854 | -0.41193 | 0.97947 | -0.39362 | 16.2512
18 | 0.0031107 | 0.00077957 | -0.0031106 | -0.0007796 | 3.4863e-08 | -2.9804e-08 | 0.004732 | 0.004732 | 0.004732 | 0.97817 | -0.41914 | 0.97816 | -0.41937 | 1.3
19 | 0.082692 | 0.020844 | -0.082671 | -0.020831 | 2.1025e-05 | 1.2748e-05 | 0.12595 | 0.12595 | 0.12595 | 0.97726 | -0.43699 | 0.97698 | -0.44231 | 8.6507
20 | -0.15935 | -0.04016 | 0.15939 | 0.040187 | 4.3926e-05 | 2.771e-05 | 0.24216 | 0.24216 | 0.24216 | 0.97947 | -0.39362 | 0.97977 | -0.38786 | 16.6319
21 | -0.01763 | -0.0044286 | 0.017648 | 0.0044397 | 1.8663e-05 | 1.1085e-05 | 0.026901 | 0.0269 | 0.026901 | 0.97532 | -0.47566 | 0.97645 | -0.4535 | 7.3903
22 | 0.01763 | 0.0044286 | -0.017617 | -0.0044209 | 1.2972e-05 | 7.706e-06 | 0.026901 | 0.026901 | 0.026901 | 0.97532 | -0.47566 | 0.97454 | -0.49109 | 7.3903
23 | -0.055747 | -0.013988 | 0.055815 | 0.014031 | 6.8101e-05 | 4.3269e-05 | 0.084959 | 0.084959 | 0.084959 | 0.97645 | -0.4535 | 0.97775 | -0.42791 | 23.3403
24 | 0.017617 | 0.0044209 | -0.0176 | -0.004411 | 1.6739e-05 | 9.9452e-06 | 0.026901 | 0.026901 | 0.026901 | 0.97454 | -0.49109 | 0.97353 | -0.51103 | 7.3904
25 | 0.062269 | 0.015695 | -0.062242 | -0.015678 | 2.7434e-05 | 1.7456e-05 | 0.094964 | 0.094964 | 0.094964 | 0.97605 | -0.46063 | 0.97558 | -0.46984 | 26.089
26 | -0.066032 | -0.016638 | 0.066061 | 0.016657 | 2.9007e-05 | 1.8469e-05 | 0.1007 | 0.1007 | 0.1007 | 0.97605 | -0.46063 | 0.97652 | -0.45145 | 27.6648
27 | 0.05881 | 0.014818 | -0.058756 | -0.014784 | 5.3534e-05 | 3.404e-05 | 0.089729 | 0.089729 | 0.089729 | 0.97558 | -0.46984 | 0.97461 | -0.48889 | 24.6509
28 | -0.069951 | -0.017632 | 0.069961 | 0.017637 | 9.1871e-06 | 5.4484e-06 | 0.10663 | 0.10663 | 0.10663 | 0.97652 | -0.45145 | 0.97666 | -0.44871 | 7.3234
29 | 0.058756 | 0.014784 | -0.05873 | -0.014767 | 2.6818e-05 | 1.7053e-05 | 0.089729 | 0.089729 | 0.089729 | 0.97461 | -0.48889 | 0.97412 | -0.49845 | 24.6509
30 | -0.073559 | -0.018539 | 0.073569 | 0.018545 | 9.7169e-06 | 5.806e-06 | 0.11211 | 0.11211 | 0.11211 | 0.97666 | -0.44871 | 0.9768 | -0.44594 | 7.6999
31 | 0.053552 | 0.013469 | -0.053513 | -0.013444 | 3.9131e-05 | 2.485e-05 | 0.081821 | 0.081821 | 0.081821 | 0.97412 | -0.49845 | 0.97335 | -0.51376 | 22.4783
32 | -0.077164 | -0.019446 | 0.077178 | 0.019454 | 1.3427e-05 | 8.0746e-06 | 0.11759 | 0.11759 | 0.11759 | 0.9768 | -0.44594 | 0.97698 | -0.44231 | 8.0761
33 | 0.04599 | 0.011559 | -0.045969 | -0.011545 | 2.0995e-05 | 1.3296e-05 | 0.07032 | 0.07032 | 0.07032 | 0.97335 | -0.51376 | 0.97286 | -0.52332 | 19.3186
34 | -0.19775 | -0.05008 | 0.19781 | 0.050117 | 5.8437e-05 | 3.7046e-05 | 0.29921 | 0.29921 | 0.29921 | 0.98405 | -0.3045 | 0.98437 | -0.29835 | 20.5501
35 | 0.19775 | 0.05008 | -0.19765 | -0.050019 | 9.5239e-05 | 6.0377e-05 | 0.29921 | 0.29921 | 0.29921 | 0.98405 | -0.3045 | 0.98353 | -0.31454 | 20.5501
36 | -0.19951 | -0.050542 | 0.19965 | 0.050636 | 0.00014802 | 9.385e-05 | 0.30178 | 0.30178 | 0.30178 | 0.98437 | -0.29835 | 0.98517 | -0.28292 | 20.7264
37 | 0.19583 | 0.049563 | -0.19579 | -0.049539 | 3.7513e-05 | 2.3777e-05 | 0.29645 | 0.29645 | 0.29645 | 0.98353 | -0.31454 | 0.98333 | -0.31853 | 20.3608
38 | -0.035263 | -0.0088429 | 0.035312 | 0.0088737 | 4.8958e-05 | 3.0779e-05 | 0.054019 | 0.054019 | 0.054019 | 0.97139 | -0.55241 | 0.97286 | -0.52332 | 14.8403
39 | 0.0098211 | 0.0024619 | -0.0098199 | -0.0024613 | 1.2119e-06 | 5.9888e-07 | 0.015045 | 0.015045 | 0.015045 | 0.97139 | -0.55241 | 0.97126 | -0.555 | 4.1331
40 | 0.025442 | 0.006381 | -0.025434 | -0.0063764 | 7.562e-06 | 4.6754e-06 | 0.038974 | 0.038974 | 0.038974 | 0.97139 | -0.55241 | 0.97107 | -0.55865 | 10.7072
41 | 0.010657 | 0.0026717 | -0.010654 | -0.0026702 | 2.9557e-06 | 1.5234e-06 | 0.016301 | 0.016301 | 0.016301 | 0.97286 | -0.52332 | 0.97257 | -0.52914 | 4.4783
42 | 0.0098199 | 0.0024613 | -0.0098192 | -0.0024609 | 6.9141e-07 | 3.417e-07 | 0.015045 | 0.015045 | 0.015045 | 0.97126 | -0.555 | 0.97118 | -0.55648 | 4.1332
43 | 0.017995 | 0.0045119 | -0.01799 | -0.0045091 | 4.7645e-06 | 2.8426e-06 | 0.027575 | 0.027575 | 0.027575 | 0.97107 | -0.55865 | 0.97079 | -0.5642 | 7.5756
44 | 0.0053059 | 0.0013298 | -0.0053056 | -0.0013297 | 3.1181e-07 | 4.2997e-08 | 0.008118 | 0.008118 | 0.008118 | 0.97257 | -0.52914 | 0.9725 | -0.53038 | 2.2302
45 | -0.0058236 | -0.0014593 | 0.005824 | 0.0014593 | 4.4912e-07 | 9.298e-08 | 0.0088259 | 0.0088259 | 0.0088259 | 0.98182 | -0.34862 | 0.9819 | -0.347 | 2.4247
46 | 0.0058236 | 0.0014593 | -0.0058235 | -0.0014592 | 1.1328e-07 | 2.3458e-08 | 0.0088259 | 0.0088259 | 0.0088259 | 0.98182 | -0.34862 | 0.9818 | -0.34903 | 2.4247
47 | -0.0071765 | -0.001798 | 0.0071776 | 0.0017984 | 1.1725e-06 | 4.1595e-07 | 0.010875 | 0.010875 | 0.010875 | 0.9819 | -0.347 | 0.98208 | -0.34357 | 2.9877
48 | 0.0013525 | 0.00033868 | -0.0013524 | -0.00033895 | 3.612e-08 | -2.6691e-07 | 0.0020495 | 0.0020496 | 0.0020496 | 0.9819 | -0.347 | 0.98187 | -0.34756 | 0.56307
49 | 0.004306 | 0.0010789 | -0.0043057 | -0.001079 | 2.7732e-07 | -4.2085e-08 | 0.006526 | 0.0065261 | 0.0065261 | 0.9818 | -0.34903 | 0.98173 | -0.35038 | 1.7929
50 | 0.015394 | 0.0038582 | -0.015393 | -0.0038574 | 1.3836e-06 | 7.9965e-07 | 0.023322 | 0.023322 | 0.023322 | 0.98217 | -0.34169 | 0.98208 | -0.34357 | 6.4073
51 | 0.020702 | 0.0051908 | -0.0207 | -0.0051897 | 1.9184e-06 | 1.162e-06 | 0.031365 | 0.031365 | 0.031365 | 0.98217 | -0.34169 | 0.98208 | -0.34363 | 8.6169
52 | -0.036096 | -0.009049 | 0.036152 | 0.0090837 | 5.5293e-05 | 3.4762e-05 | 0.054688 | 0.054688 | 0.054688 | 0.98217 | -0.34169 | 0.98382 | -0.30959 | 15.0241
53 | 0.0082151 | 0.0020589 | -0.0082148 | -0.0020588 | 2.1496e-07 | 9.076e-08 | 0.012447 | 0.012447 | 0.012447 | 0.98208 | -0.34357 | 0.98205 | -0.34412 | 3.4196
54 | 0.0052214 | 0.0013086 | -0.0052214 | -0.0013086 | 7.3317e-08 | 7.399e-09 | 0.0079114 | 0.0079114 | 0.0079114 | 0.98208 | -0.34363 | 0.98206 | -0.34393 | 2.1735
55 | 0.015479 | 0.003881 | -0.015474 | -0.0038782 | 4.9831e-06 | 2.8836e-06 | 0.023454 | 0.023454 | 0.023454 | 0.98208 | -0.34363 | 0.98173 | -0.35039 | 6.4435
56 | -0.04202 | -0.010555 | 0.042026 | 0.010558 | 5.4311e-06 | 3.4304e-06 | 0.063564 | 0.063564 | 0.063564 | 0.98382 | -0.30959 | 0.98396 | -0.30688 | 17.4626
57 | -0.23398 | -0.059392 | 0.23421 | 0.05954 | 0.00023306 | 0.00014813 | 0.35195 | 0.35195 | 0.35195 | 0.98999 | -0.1901 | 0.99107 | -0.16942 | 24.1726
58 | 0.23398 | 0.059392 | -0.2337 | -0.059216 | 0.0002774 | 0.00017631 | 0.35195 | 0.35195 | 0.35195 | 0.98999 | -0.1901 | 0.98871 | -0.21478 | 24.1726
59 | 0.20622 | 0.052712 | -0.20523 | -0.052082 | 0.00099338 | 0.00063011 | 0.30999 | 0.30999 | 0.30999 | 0.99107 | -0.16942 | 0.98586 | -0.26953 | 21.2907
60 | -0.44043 | -0.11225 | 0.44077 | 0.11247 | 0.00033804 | 0.00021592 | 0.66194 | 0.66194 | 0.66194 | 0.99107 | -0.16942 | 0.9919 | -0.15353 | 45.4631
61 | 0.23113 | 0.058571 | -0.23106 | -0.058526 | 7.0044e-05 | 4.4512e-05 | 0.34808 | 0.34808 | 0.34808 | 0.98871 | -0.21478 | 0.98839 | -0.22109 | 23.9066
62 | -0.19965 | -0.050636 | 0.19978 | 0.050718 | 0.0001286 | 8.1535e-05 | 0.30178 | 0.30178 | 0.30178 | 0.98517 | -0.28292 | 0.98586 | -0.26953 | 20.7264
63 | -0.45025 | -0.11484 | 0.45155 | 0.11568 | 0.0013051 | 0.00083369 | 0.67616 | 0.67616 | 0.67616 | 0.9919 | -0.15353 | 0.99504 | -0.093697 | 46.4395
64 | 0.19397 | 0.049082 | -0.19392 | -0.04905 | 4.9635e-05 | 3.1455e-05 | 0.29369 | 0.29369 | 0.29369 | 0.98333 | -0.31853 | 0.98305 | -0.32386 | 20.1712
65 | 0.010518 | 0.0026365 | -0.010517 | -0.0026357 | 1.4848e-06 | 7.6194e-07 | 0.016122 | 0.016122 | 0.016122 | 0.97079 | -0.5642 | 0.97064 | -0.56717 | 4.4292
66 | 0.0027705 | 0.00069419 | -0.0027704 | -0.00069425 | 4.7736e-08 | -6.0729e-08 | 0.0041991 | 0.0041992 | 0.0041992 | 0.98173 | -0.35038 | 0.98171 | -0.35075 | 1.1536
67 | -0.046578 | -0.011699 | 0.0466 | 0.011713 | 2.1704e-05 | 1.3742e-05 | 0.070448 | 0.070448 | 0.070448 | 0.98396 | -0.30688 | 0.98446 | -0.29712 | 19.3538
68 | -0.0013938 | -0.00034932 | 0.0013938 | 0.00034924 | 1.1278e-08 | -7.7982e-08 | 0.0021127 | 0.0021126 | 0.0021127 | 0.9817 | -0.35092 | 0.98171 | -0.35075 | 0.5804
69 | 0.23028 | 0.058332 | -0.23026 | -0.058317 | 2.3415e-05 | 1.4879e-05 | 0.34691 | 0.34691 | 0.34691 | 0.98839 | -0.22109 | 0.98828 | -0.22321 | 23.8265
70 | -0.45305 | -0.11605 | 0.45327 | 0.11619 | 0.00022212 | 0.00014189 | 0.67839 | 0.67839 | 0.67839 | 0.99504 | -0.093697 | 0.99558 | -0.083584 | 46.5929
71 | -0.0052646 | -0.0013194 | 0.0052649 | 0.0013195 | 3.0516e-07 | 4.0914e-08 | 0.0080713 | 0.0080712 | 0.0080713 | 0.97058 | -0.56838 | 0.97064 | -0.56717 | 2.2174
72 | -0.22025 | -0.055721 | 0.22029 | 0.055745 | 3.8864e-05 | 2.4681e-05 | 0.33219 | 0.33219 | 0.33219 | 0.98717 | -0.24455 | 0.98736 | -0.24087 | 22.815
73 | 0.20231 | 0.051223 | -0.20231 | -0.051223 | 6.9678e-07 | 4.4186e-07 | 0.30514 | 0.30514 | 0.30514 | 0.98717 | -0.24455 | 0.98717 | -0.24462 | 20.9572
74 | -0.22353 | -0.056558 | 0.2236 | 0.056601 | 6.8258e-05 | 4.3357e-05 | 0.33707 | 0.33707 | 0.33707 | 0.98736 | -0.24087 | 0.98769 | -0.23451 | 23.1505
75 | 0.20123 | 0.050952 | -0.20117 | -0.050917 | 5.6102e-05 | 3.5573e-05 | 0.30351 | 0.30351 | 0.30351 | 0.98717 | -0.24462 | 0.98687 | -0.25043 | 20.8455
76 | -0.22437 | -0.056794 | 0.22441 | 0.056815 | 3.2188e-05 | 2.0447e-05 | 0.33823 | 0.33823 | 0.33823 | 0.98769 | -0.23451 | 0.98784 | -0.23152 | 23.2303
77 | 0.20033 | 0.050706 | -0.20033 | -0.050705 | 1.7093e-06 | 1.0838e-06 | 0.30225 | 0.30225 | 0.30225 | 0.98687 | -0.25043 | 0.98686 | -0.25061 | 20.7586
78 | -0.22691 | -0.057442 | 0.22695 | 0.057467 | 3.9633e-05 | 2.518e-05 | 0.342 | 0.342 | 0.342 | 0.98784 | -0.23152 | 0.98803 | -0.22789 | 23.4891
79 | 0.1971 | 0.049896 | -0.19704 | -0.049857 | 6.1251e-05 | 3.8823e-05 | 0.29738 | 0.29738 | 0.29738 | 0.98686 | -0.25061 | 0.98652 | -0.25708 | 20.4241
80 | -0.22772 | -0.05766 | 0.22777 | 0.057693 | 5.1191e-05 | 3.2525e-05 | 0.34316 | 0.34316 | 0.34316 | 0.98803 | -0.22789 | 0.98828 | -0.22321 | 23.569
81 | 0.19573 | 0.049528 | -0.1957 | -0.049511 | 2.6834e-05 | 1.7006e-05 | 0.29539 | 0.29539 | 0.29539 | 0.98652 | -0.25708 | 0.98637 | -0.25994 | 20.2881
82 | -0.0039919 | -0.0010005 | 0.0039919 | 0.0010005 | 1.5124e-09 | -5.2305e-10 | 0.0059497 | 0.0059497 | 0.0059497 | 0.99837 | -0.031358 | 0.99837 | -0.03135 | 1.6345
83 | -0.0079857 | -0.0020014 | 0.0079861 | 0.0020016 | 4.553e-07 | 1.7931e-07 | 0.011902 | 0.011902 | 0.011902 | 0.99837 | -0.03135 | 0.99843 | -0.030153 | 3.2698
84 | -0.011938 | -0.0029921 | 0.011938 | 0.0029921 | 1.3063e-08 | 6.9212e-09 | 0.017792 | 0.017792 | 0.017792 | 0.99843 | -0.030153 | 0.99843 | -0.03013 | 4.888
85 | -0.015887 | -0.0039817 | 0.015887 | 0.003982 | 5.5327e-07 | 3.1967e-07 | 0.023677 | 0.023677 | 0.023677 | 0.99843 | -0.03013 | 0.99847 | -0.029399 | 6.5046
86 | -0.022266 | -0.0055806 | 0.022268 | 0.0055821 | 2.4354e-06 | 1.4815e-06 | 0.033183 | 0.033183 | 0.033183 | 0.99847 | -0.029399 | 0.99859 | -0.027103 | 9.1162
87 | 0.092062 | 0.023184 | -0.092012 | -0.023152 | 5.0517e-05 | 3.2244e-05 | 0.1398 | 0.1398 | 0.1398 | 0.98017 | -0.38053 | 0.97959 | -0.39202 | 38.407
88 | -0.098198 | -0.024722 | 0.098214 | 0.024732 | 1.6082e-05 | 1.0268e-05 | 0.14912 | 0.14912 | 0.14912 | 0.98017 | -0.38053 | 0.98035 | -0.37711 | 40.9661
89 | 0.086329 | 0.021728 | -0.086317 | -0.02172 | 1.1987e-05 | 7.6483e-06 | 0.13117 | 0.13117 | 0.13117 | 0.97959 | -0.39202 | 0.97944 | -0.39492 | 36.0354
90 | -0.10403 | -0.02619 | 0.10411 | 0.02624 | 7.7869e-05 | 4.9731e-05 | 0.15794 | 0.15794 | 0.15794 | 0.98035 | -0.37711 | 0.98115 | -0.36146 | 43.3912
91 | 0.078905 | 0.019862 | -0.078845 | -0.019824 | 6.0079e-05 | 3.831e-05 | 0.11991 | 0.11991 | 0.11991 | 0.97944 | -0.39492 | 0.97862 | -0.41086 | 32.9418
92 | -0.11028 | -0.027786 | 0.11029 | 0.02779 | 6.0441e-06 | 3.8609e-06 | 0.1673 | 0.1673 | 0.1673 | 0.98115 | -0.36146 | 0.98121 | -0.36032 | 45.9626
93 | 0.072156 | 0.018148 | -0.072154 | -0.018146 | 2.0054e-06 | 1.2779e-06 | 0.10974 | 0.10974 | 0.10974 | 0.97862 | -0.41086 | 0.97859 | -0.41145 | 30.1475
94 | -0.11621 | -0.029274 | 0.11631 | 0.029338 | 9.9182e-05 | 6.3369e-05 | 0.17628 | 0.17628 | 0.17628 | 0.98121 | -0.36032 | 0.98212 | -0.34249 | 48.4296
95 | 0.065228 | 0.016411 | -0.065177 | -0.016378 | 5.1272e-05 | 3.264e-05 | 0.099206 | 0.099206 | 0.099206 | 0.97859 | -0.41145 | 0.97775 | -0.42791 | 27.2544
96 | -0.12101 | -0.030516 | 0.12104 | 0.030536 | 3.2068e-05 | 2.0492e-05 | 0.18341 | 0.18341 | 0.18341 | 0.98212 | -0.34249 | 0.98241 | -0.33695 | 50.386
97 | -0.026218 | -0.006572 | 0.026218 | 0.0065721 | 6.6642e-08 | 4.1128e-08 | 0.039069 | 0.039069 | 0.039069 | 0.99859 | -0.027103 | 0.99859 | -0.02705 | 10.7331
98 | -0.0098861 | -0.0024775 | 0.0098868 | 0.0024779 | 6.9562e-07 | 3.3402e-07 | 0.014753 | 0.014753 | 0.014753 | 0.99711 | -0.05488 | 0.99719 | -0.053403 | 4.0531
99 | 0.0072555 | 0.0018182 | -0.0072552 | -0.0018181 | 3.3528e-07 | 1.1511e-07 | 0.010828 | 0.010828 | 0.010828 | 0.99711 | -0.05488 | 0.99706 | -0.05585 | 2.9746
100 | -0.012198 | -0.0030572 | 0.0122 | 0.0030583 | 1.9661e-06 | 1.0518e-06 | 0.018203 | 0.018203 | 0.018203 | 0.99719 | -0.053403 | 0.99736 | -0.05002 | 5.0007
101 | 0.0056037 | 0.0014042 | -0.0056035 | -0.0014042 | 1.6721e-07 | 2.3866e-08 | 0.0083629 | 0.0083629 | 0.0083629 | 0.99706 | -0.05585 | 0.99703 | -0.056476 | 2.2975
102 | -0.033511 | -0.0084 | 0.033535 | 0.0084147 | 2.3617e-05 | 1.4786e-05 | 0.049998 | 0.049998 | 0.049998 | 0.99736 | -0.05002 | 0.99813 | -0.035239 | 13.7356
103 | 0.021311 | 0.0053417 | -0.021309 | -0.0053403 | 2.3579e-06 | 1.4279e-06 | 0.031795 | 0.031795 | 0.031795 | 0.99736 | -0.05002 | 0.99724 | -0.052343 | 8.7349
104 | 0.0040253 | 0.0010087 | -0.0040251 | -0.0010087 | 1.0209e-07 | -3.3037e-08 | 0.0060074 | 0.0060075 | 0.0060075 | 0.99703 | -0.056476 | 0.997 | -0.057009 | 1.6504
105 | -0.49236 | -0.12642 | 0.49311 | 0.1269 | 0.00075386 | 0.00048169 | 0.73508 | 0.73508 | 0.73508 | 0.99813 | -0.035239 | 0.9998 | -0.0037508 | 50.4863
106 | 0.45882 | 0.118 | -0.45814 | -0.11757 | 0.00068228 | 0.00043585 | 0.68508 | 0.68508 | 0.68508 | 0.99813 | -0.035239 | 0.99651 | -0.065882 | 47.0524
107 | 0.0070985 | 0.0017789 | -0.0070981 | -0.0017787 | 3.5163e-07 | 1.16e-07 | 0.010592 | 0.010592 | 0.010592 | 0.99724 | -0.052343 | 0.99719 | -0.053383 | 2.9098
108 | 0.001545 | 0.00038711 | -0.001545 | -0.00038721 | 1.8131e-08 | -1.0697e-07 | 0.0023059 | 0.0023059 | 0.0023059 | 0.997 | -0.057009 | 0.99699 | -0.057255 | 0.6335
109 | -0.4946 | -0.12727 | 0.49463 | 0.12729 | 2.4661e-05 | 1.5758e-05 | 0.7373 | 0.7373 | 0.7373 | 0.9998 | -0.0037508 | 0.99986 | -0.0027255 | 50.6387
110 | 0.45665 | 0.11719 | -0.45642 | -0.11705 | 0.00022392 | 0.00014304 | 0.68285 | 0.68285 | 0.68285 | 0.99651 | -0.065882 | 0.99598 | -0.075992 | 46.8993
111 | 0.003262 | 0.00081732 | -0.0032618 | -0.00081749 | 2.0036e-07 | -1.6594e-07 | 0.0048675 | 0.0048676 | 0.0048676 | 0.99719 | -0.053383 | 0.99712 | -0.054672 | 1.3373
112 | -0.49617 | -0.12767 | 0.49623 | 0.12772 | 6.5769e-05 | 4.2025e-05 | 0.73959 | 0.73959 | 0.73959 | 0.99986 | -0.0027255 | 1 | 0 | 50.7961
113 | 0.45493 | 0.11667 | -0.45476 | -0.11657 | 0.00016743 | 0.00010696 | 0.68062 | 0.68062 | 0.68062 | 0.99598 | -0.075992 | 0.99558 | -0.083584 | 46.7461
114 | -0.16302 | -0.041098 | 0.16312 | 0.041159 | 9.6831e-05 | 6.1123e-05 | 0.24768 | 0.24768 | 0.24768 | 0.97977 | -0.38786 | 0.9804 | -0.37546 | 17.0107
115 | -0.17037 | -0.042975 | 0.17044 | 0.04302 | 7.1372e-05 | 4.5104e-05 | 0.25868 | 0.25868 | 0.25868 | 0.9804 | -0.37546 | 0.98085 | -0.36671 | 17.7662
116 | -0.17443 | -0.044021 | 0.17448 | 0.044054 | 5.2251e-05 | 3.3039e-05 | 0.26473 | 0.26473 | 0.26473 | 0.98085 | -0.36671 | 0.98117 | -0.36046 | 18.182
117 | -0.17848 | -0.045055 | 0.17853 | 0.045086 | 4.8477e-05 | 3.0669e-05 | 0.27079 | 0.27079 | 0.27079 | 0.98117 | -0.36046 | 0.98146 | -0.35479 | 18.5983
118 | 0.0093617 | 0.0023466 | -0.00936 | -0.0023458 | 1.6953e-06 | 8.0574e-07 | 0.014247 | 0.014248 | 0.014248 | 0.97775 | -0.42791 | 0.97756 | -0.43171 | 3.9142
119 | 0.0049038 | 0.001229 | -0.0049036 | -0.001229 | 1.6083e-07 | 6.4315e-09 | 0.0074644 | 0.0074644 | 0.0074644 | 0.97756 | -0.43171 | 0.97753 | -0.4324 | 2.0507
120 | -0.18254 | -0.046091 | 0.18259 | 0.046126 | 5.5405e-05 | 3.5069e-05 | 0.27687 | 0.27687 | 0.27687 | 0.98146 | -0.35479 | 0.98179 | -0.34846 | 19.0157
121 | -0.12872 | -0.032461 | 0.12881 | 0.032522 | 9.5268e-05 | 6.0887e-05 | 0.19504 | 0.19504 | 0.19504 | 0.98241 | -0.33695 | 0.9832 | -0.3215 | 53.5815
122 | -0.13533 | -0.034155 | 0.1355 | 0.034263 | 0.00016796 | 0.00010736 | 0.2049 | 0.2049 | 0.2049 | 0.9832 | -0.3215 | 0.98453 | -0.29562 | 56.2916
123 | 0.054393 | 0.013667 | -0.054389 | -0.013665 | 3.8918e-06 | 2.4712e-06 | 0.082221 | 0.082221 | 0.082221 | 0.98453 | -0.29562 | 0.98446 | -0.29712 | 22.5882
124 | -0.18989 | -0.04793 | 0.18998 | 0.047986 | 8.8246e-05 | 5.6332e-05 | 0.28712 | 0.28712 | 0.28712 | 0.98453 | -0.29562 | 0.98503 | -0.28593 | 39.4399
125 | -0.18998 | -0.047986 | 0.19015 | 0.048091 | 0.00016562 | 0.0001049 | 0.28712 | 0.28712 | 0.28712 | 0.98503 | -0.28593 | 0.98597 | -0.26775 | 19.7199
126 | -0.1923 | -0.048631 | 0.19237 | 0.048677 | 7.2109e-05 | 4.5684e-05 | 0.29037 | 0.29037 | 0.29037 | 0.98597 | -0.26775 | 0.98637 | -0.25994 | 19.9433
127 | 0.03808 | 0.0095514 | -0.038069 | -0.0095446 | 1.0887e-05 | 6.8494e-06 | 0.056715 | 0.056715 | 0.056715 | 0.99914 | -0.016487 | 0.99883 | -0.022487 | 15.581
128 | -0.042094 | -0.010557 | 0.042127 | 0.010578 | 3.3109e-05 | 2.0896e-05 | 0.062693 | 0.062693 | 0.062693 | 0.99914 | -0.016487 | 1 | 0 | 17.2234
129 | 0.034123 | 0.0085556 | -0.034123 | -0.0085555 | 1.1818e-07 | 7.4039e-08 | 0.050836 | 0.050836 | 0.050836 | 0.99883 | -0.022487 | 0.99883 | -0.02256 | 13.9659
130 | 0.030179 | 0.007567 | -0.030172 | -0.007563 | 6.4566e-06 | 4.0208e-06 | 0.04496 | 0.04496 | 0.04496 | 0.99883 | -0.02256 | 0.99859 | -0.02705 | 12.3517
131 | -0.18469 | -0.046653 | 0.18476 | 0.046696 | 6.8312e-05 | 4.325e-05 | 0.28006 | 0.28006 | 0.28006 | 0.98179 | -0.34846 | 0.98218 | -0.34074 | 19.2347
132 | 0.19209 | 0.048592 | -0.19205 | -0.048561 | 4.9006e-05 | 3.1051e-05 | 0.29093 | 0.29093 | 0.29093 | 0.98305 | -0.32386 | 0.98278 | -0.32918 | 19.9814
133 | 0.19022 | 0.048105 | -0.19018 | -0.048074 | 4.8859e-05 | 3.0951e-05 | 0.28817 | 0.28817 | 0.28817 | 0.98278 | -0.32918 | 0.9825 | -0.33454 | 19.792
134 | 0.18829 | 0.047602 | -0.18824 | -0.047567 | 5.6013e-05 | 3.5477e-05 | 0.28532 | 0.28532 | 0.28532 | 0.9825 | -0.33454 | 0.98218 | -0.34074 | 19.5961

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.543 | 0.13904

## res_load
| p_mw | q_mvar
0 | 0.0025541 | 0.00064011
1 | 0.0024738 | 0.00061999
2 | 0.0024646 | 0.00061768
3 | 0.0034748 | 0.00087087
4 | 0.0030636 | 0.00076781
5 | 0.0055579 | 0.0013929
6 | 0.0040073 | 0.0010043
7 | 0.0027017 | 0.0006771
8 | 0.0040186 | 0.0010072
9 | 0.0026823 | 0.00067225
10 | 0.0042549 | 0.0010664
11 | 0.003325 | 0.00083333
12 | 0.0040946 | 0.0010262
13 | 0.0070256 | 0.0017608
14 | 0.0086987 | 0.0021801
15 | 0.0092162 | 0.0023098
16 | 0.0036484 | 0.00091437
17 | 0.0031106 | 0.0007796
18 | 0.038099 | 0.0095484
19 | 0.0176 | 0.004411
20 | 0.0037626 | 0.00094299
21 | 0.0034321 | 0.00086016
22 | 0.0038904 | 0.00097503
23 | 0.0035987 | 0.00090193
24 | 0.0051772 | 0.0012975
25 | 0.0035952 | 0.00090104
26 | 0.0075232 | 0.0018855
27 | 0.0016986 | 0.00042572
28 | 0.0018218 | 0.00045659
29 | 0.0074392 | 0.0018644
30 | 0.0053486 | 0.0013405
31 | 0.0098192 | 0.0024609
32 | 0.0015175 | 0.00038032
33 | 0.0058686 | 0.0014708
34 | 0.0025736 | 0.00064501
35 | 0.0054439 | 0.0013644
36 | 0.0013524 | 0.00033895
37 | 0.0094769 | 0.0023751
38 | 0.0054931 | 0.0013767
39 | 0.0018244 | 0.00045724
40 | 0.0074718 | 0.0018726
41 | 0.0053056 | 0.0013297
42 | 0.0015352 | 0.00038476
43 | 0.0082148 | 0.0020588
44 | 0.0052214 | 0.0013086
45 | 0.015474 | 0.0038782
46 | 0.0045521 | 0.0011409
47 | 0.0013938 | 0.00034932
48 | 0.0013766 | 0.00034501
49 | 0.00077445 | 0.0001941
50 | 0.0014931 | 0.00037421
51 | 0.0052646 | 0.0013194
52 | 0.0052518 | 0.0013162
53 | 0.017945 | 0.0044974
54 | 0.0032418 | 0.00081248
55 | 0.0010795 | 0.00027055
56 | 0.0007713 | 0.00019331
57 | 0.0008387 | 0.0002102
58 | 0.0025012 | 0.00062685
59 | 0.0032299 | 0.0008095
60 | 0.00077227 | 0.00019355
61 | 0.0013135 | 0.00032919
62 | 0.0039919 | 0.0010005
63 | 0.0039938 | 0.0010009
64 | 0.0039523 | 0.00099053
65 | 0.0039484 | 0.00098956
66 | 0.0063786 | 0.0015986
67 | 0.0061359 | 0.0015378
68 | 0.0056829 | 0.0014243
69 | 0.0058158 | 0.0014576
70 | 0.007412 | 0.0018576
71 | 0.0061718 | 0.0015468
72 | 0.0066892 | 0.0016765
73 | 0.0059213 | 0.001484
74 | 0.0069258 | 0.0017358
75 | 0.0047003 | 0.001178
76 | 0.0039499 | 0.00098993
77 | 0.0026306 | 0.0006593
78 | 0.0023116 | 0.00057934
79 | 0.0016514 | 0.00041389
80 | 0.0015783 | 0.00039556
81 | 0.01421 | 0.0035614
82 | 0.0024801 | 0.00062158
83 | 0.0014919 | 0.00037391
84 | 0.0014929 | 0.00037416
85 | 0.0038361 | 0.00096142
86 | 0.001545 | 0.00038721
87 | 0.0015393 | 0.00038577
88 | 0.0014931 | 0.0003742
89 | 0.0032618 | 0.00081749
90 | 0.0036319 | 0.00091025
91 | 0.0072478 | 0.0018165
92 | 0.003991 | 0.0010002
93 | 0.0039964 | 0.0010016
94 | 0.0044562 | 0.0011168
95 | 0.0040089 | 0.0010047
96 | 0.0049036 | 0.001229
97 | 0.0076792 | 0.0019246
98 | 0.0065183 | 0.0016336
99 | 0.0077891 | 0.0019521
100 | 0.0021554 | 0.0005402
101 | 0.0040144 | 0.0010061
102 | 0.0039461 | 0.00098899
103 | 0.0029893 | 0.0007492
104 | 0.0039441 | 0.00098848
105 | 0.0039539 | 0.00099093
106 | 0.0021033 | 0.00052714
107 | 0.0014934 | 0.00037427
108 | 0.0033272 | 0.00083388
109 | 0.0024907 | 0.00062423
110 | 0.0018259 | 0.00045762
111 | 0.0018214 | 0.00045648
112 | 0.0018826 | 0.00047182
113 | 0.0034741 | 0.00087068

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1