## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-312_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-312_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-312_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2701-312_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2701-312_0_4_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_2701-312_0_4_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_2701-312_0_4_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_2701-312_0_4_node_77 | 0.4 | n |  | TRUE
8 | bus_LV_2701-312_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2701-312_0_4_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_2701-312_0_4_node_83 | 0.4 | n |  | TRUE
11 | bus_LV_2701-312_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2701-312_0_4_node_68 | 0.4 | n |  | TRUE
13 | bus_LV_2701-312_0_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_2701-312_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2701-312_0_4_node_65 | 0.4 | n |  | TRUE
16 | bus_LV_2701-312_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_2701-312_0_4_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_2701-312_0_4_node_49 | 0.4 | n |  | TRUE
19 | bus_LV_2701-312_0_4_node_70 | 0.4 | n |  | TRUE
20 | bus_LV_2701-312_0_4_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_2701-312_0_4_node_72 | 0.4 | n |  | TRUE
22 | bus_LV_2701-312_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2701-312_0_4_node_35 | 0.4 | n |  | TRUE
24 | bus_LV_2701-312_0_4_node_36 | 0.4 | n |  | TRUE
25 | bus_LV_2701-312_0_4_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_2701-312_0_4_node_74 | 0.4 | n |  | TRUE
27 | bus_LV_2701-312_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_2701-312_0_4_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_2701-312_0_4_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_2701-312_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2701-312_0_4_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_2701-312_0_4_node_55 | 0.4 | n |  | TRUE
33 | bus_LV_2701-312_0_4_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_2701-312_0_4_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_2701-312_0_4_node_63 | 0.4 | n |  | TRUE
36 | bus_LV_2701-312_0_4_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_2701-312_0_4_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_2701-312_0_4_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_2701-312_0_4_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_2701-312_0_4_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_2701-312_0_4_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_2701-312_0_4_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_2701-312_0_4_node_78 | 0.4 | n |  | TRUE
44 | bus_LV_2701-312_0_4_node_81 | 0.4 | n |  | TRUE
45 | bus_LV_2701-312_0_4_node_66 | 0.4 | n |  | TRUE
46 | bus_LV_2701-312_0_4_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_2701-312_0_4_node_71 | 0.4 | n |  | TRUE
48 | bus_LV_2701-312_0_4_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_2701-312_0_4_node_82 | 0.4 | n |  | TRUE
50 | bus_LV_2701-312_0_4_node_76 | 0.4 | n |  | TRUE
51 | bus_LV_2701-312_0_4_node_73 | 0.4 | n |  | TRUE
52 | bus_LV_2701-312_0_4_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_2701-312_0_4_node_75 | 0.4 | n |  | TRUE
54 | bus_LV_2701-312_0_4_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_2701-312_0_4_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_2701-312_0_4_node_59 | 0.4 | n |  | TRUE
57 | bus_LV_2701-312_0_4_node_64 | 0.4 | n |  | TRUE
58 | bus_LV_2701-312_0_4_node_27 | 0.4 | n |  | TRUE
59 | bus_LV_2701-312_0_4_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_2701-312_0_4_node_30 | 0.4 | n |  | TRUE
61 | bus_LV_2701-312_0_4_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_2701-312_0_4_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_2701-312_0_4_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_2701-312_0_4_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_2701-312_0_4_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_2701-312_0_4_node_38 | 0.4 | n |  | TRUE
67 | bus_LV_2701-312_0_4_node_39 | 0.4 | n |  | TRUE
68 | bus_LV_2701-312_0_4_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_2701-312_0_4_node_42 | 0.4 | n |  | TRUE
70 | bus_LV_2701-312_0_4_node_43 | 0.4 | n |  | TRUE
71 | bus_LV_2701-312_0_4_node_53 | 0.4 | n |  | TRUE
72 | bus_LV_2701-312_0_4_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_2701-312_0_4_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_2701-312_0_4_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_2701-312_0_4_node_69 | 0.4 | n |  | TRUE
76 | bus_LV_2701-312_0_4_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_2701-312_0_4_node_79 | 0.4 | n |  | TRUE
78 | bus_LV_2701-312_0_4_node_80 | 0.4 | n |  | TRUE
79 | bus_MV_564_0_node_28 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-312_0_4_load_0 | 0 | 0.0095417 | 0.0023914 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-312_0_4_load_3 | 2 | 0.0047112 | 0.0011807 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-312_0_4_load_77 | 7 | 0.0020667 | 0.00051796 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-312_0_4_load_83 | 10 | 0.0050673 | 0.00127 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-312_0_4_load_68 | 12 | 0.014858 | 0.0037238 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-312_0_4_load_65 | 15 | 0.017706 | 0.0044375 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-312_0_4_load_50 | 17 | 0.0015 | 0.00037594 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-312_0_4_load_49 | 18 | 0.0015632 | 0.00039178 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-312_0_4_load_46 | 20 | 0.0027052 | 0.00067798 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-312_0_4_load_72 | 21 | 0.004467 | 0.0011195 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-312_0_4_load_35 | 23 | 0.0020417 | 0.00051169 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-312_0_4_load_36 | 24 | 0.001826 | 0.00045763 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-312_0_4_load_32 | 25 | 0.0016394 | 0.00041087 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-312_0_4_load_74 | 26 | 0.0027343 | 0.00068527 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-312_0_4_load_31 | 28 | 0.0058958 | 0.0014776 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-312_0_4_load_28 | 29 | 0.003699 | 0.00092706 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-312_0_4_load_34 | 31 | 0.0021618 | 0.00054181 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-312_0_4_load_55 | 32 | 0.0020775 | 0.00052067 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-312_0_4_load_61 | 34 | 0.015365 | 0.0038509 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-312_0_4_load_63 | 35 | 0.015414 | 0.003863 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-312_0_4_load_26 | 37 | 0.0058681 | 0.0014707 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-312_0_4_load_23 | 38 | 0.040461 | 0.01014 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-312_0_4_load_54 | 41 | 0.0015045 | 0.00037705 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-312_0_4_load_47 | 42 | 0.0017025 | 0.0004267 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-312_0_4_load_78 | 43 | 0.0027157 | 0.00068063 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-312_0_4_load_81 | 44 | 0.0026562 | 0.00066571 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-312_0_4_load_66 | 45 | 0.015513 | 0.0038879 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-312_0_4_load_41 | 46 | 0.001732 | 0.00043407 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-312_0_4_load_71 | 47 | 0.0015774 | 0.00039535 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-312_0_4_load_44 | 48 | 0.0017423 | 0.00043667 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-312_0_4_load_82 | 49 | 0.0019009 | 0.00047641 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-312_0_4_load_76 | 50 | 0.0017999 | 0.00045111 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-312_0_4_load_73 | 51 | 0.004839 | 0.0012128 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-312_0_4_load_33 | 52 | 0.0016379 | 0.0004105 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-312_0_4_load_75 | 53 | 0.0027474 | 0.00068856 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-312_0_4_load_29 | 54 | 0.0036004 | 0.00090234 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-312_0_4_load_45 | 55 | 0.0017984 | 0.00045073 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-312_0_4_load_59 | 56 | 0.015364 | 0.0038505 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-312_0_4_load_64 | 57 | 0.015539 | 0.0038944 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-312_0_4_load_27 | 58 | 0.0051353 | 0.001287 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-312_0_4_load_48 | 59 | 0.0015598 | 0.00039093 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2701-312_0_4_load_30 | 60 | 0.0036029 | 0.00090297 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2701-312_0_4_load_56 | 61 | 0.003635 | 0.00091103 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2701-312_0_4_load_57 | 62 | 0.0036421 | 0.0009128 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2701-312_0_4_load_52 | 63 | 0.0021556 | 0.00054025 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2701-312_0_4_load_37 | 65 | 0.0015634 | 0.00039182 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2701-312_0_4_load_38 | 66 | 0.0011354 | 0.00028455 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2701-312_0_4_load_39 | 67 | 0.0017283 | 0.00043314 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2701-312_0_4_load_40 | 68 | 0.0014572 | 0.00036522 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2701-312_0_4_load_42 | 69 | 0.0015244 | 0.00038205 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2701-312_0_4_load_43 | 70 | 0.0015569 | 0.00039019 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2701-312_0_4_load_53 | 71 | 0.0016175 | 0.00040539 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2701-312_0_4_load_58 | 72 | 0.015333 | 0.0038428 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2701-312_0_4_load_60 | 73 | 0.01553 | 0.0038923 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2701-312_0_4_load_62 | 74 | 0.023658 | 0.0059293 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2701-312_0_4_load_69 | 75 | 0.015556 | 0.0038987 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2701-312_0_4_load_67 | 76 | 0.015547 | 0.0038965 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2701-312_0_4_load_79 | 77 | 0.0017924 | 0.00044922 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2701-312_0_4_load_80 | 78 | 0.0018745 | 0.00046979 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-312_0_4_line_0 |  | 0 | 1 | 0.014597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-312_0_4_line_1 |  | 1 | 2 | 0.016842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-312_0_4_line_2 |  | 1 | 3 | 0.093043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-312_0_4_line_3 |  | 2 | 5 | 0.018866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-312_0_4_line_4 |  | 3 | 7 | 0.039639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-312_0_4_line_5 |  | 4 | 5 | 0.006876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-312_0_4_line_6 |  | 4 | 6 | 0.053079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-312_0_4_line_7 |  | 5 | 28 | 0.0037099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-312_0_4_line_8 |  | 6 | 36 | 0.01812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-312_0_4_line_9 |  | 6 | 37 | 0.011127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-312_0_4_line_10 |  | 7 | 43 | 0.0086415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-312_0_4_line_11 |  | 8 | 9 | 0.020094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-312_0_4_line_12 |  | 8 | 10 | 0.0090745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-312_0_4_line_13 |  | 9 | 26 | 0.0091361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-312_0_4_line_14 |  | 10 | 44 | 0.0020045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-312_0_4_line_15 |  | 11 | 12 | 0.023376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-312_0_4_line_16 |  | 11 | 13 | 0.028387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-312_0_4_line_17 |  | 11 | 14 | 0.026589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-312_0_4_line_18 |  | 11 | 15 | 0.021207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-312_0_4_line_19 |  | 13 | 21 | 0.034337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-312_0_4_line_20 |  | 14 | 19 | 0.011959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-312_0_4_line_21 |  | 14 | 20 | 0.015625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-312_0_4_line_22 |  | 15 | 45 | 0.0086663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-312_0_4_line_23 |  | 16 | 17 | 0.015697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-312_0_4_line_24 |  | 16 | 18 | 0.018786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-312_0_4_line_25 |  | 18 | 46 | 0.0072206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-312_0_4_line_26 |  | 19 | 47 | 0.010784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2701-312_0_4_line_27 |  | 20 | 48 | 0.019722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2701-312_0_4_line_28 |  | 21 | 51 | 0.014825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-312_0_4_line_29 |  | 22 | 23 | 0.031905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-312_0_4_line_30 |  | 22 | 24 | 0.011534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-312_0_4_line_31 |  | 22 | 25 | 0.017858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-312_0_4_line_32 |  | 23 | 41 | 0.00062817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-312_0_4_line_33 |  | 25 | 52 | 0.0073255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2701-312_0_4_line_34 |  | 26 | 53 | 0.0026817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2701-312_0_4_line_35 |  | 27 | 28 | 0.022738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-312_0_4_line_36 |  | 27 | 29 | 0.021138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-312_0_4_line_37 |  | 29 | 54 | 0.0085615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-312_0_4_line_38 |  | 30 | 31 | 0.013262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2701-312_0_4_line_39 |  | 30 | 32 | 0.032618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2701-312_0_4_line_40 |  | 31 | 52 | 0.0083974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2701-312_0_4_line_41 |  | 32 | 55 | 0.008015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-312_0_4_line_42 |  | 33 | 34 | 0.0055866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_2701-312_0_4_line_43 |  | 33 | 35 | 0.0029146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_2701-312_0_4_line_44 |  | 34 | 56 | 0.0085004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_2701-312_0_4_line_45 |  | 35 | 57 | 0.0085358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2701-312_0_4_line_46 |  | 36 | 38 | 0.011665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2701-312_0_4_line_47 |  | 37 | 58 | 0.010299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2701-312_0_4_line_48 |  | 39 | 40 | 0.011266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2701-312_0_4_line_49 |  | 39 | 41 | 0.0061455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2701-312_0_4_line_50 |  | 40 | 42 | 0.022687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2701-312_0_4_line_51 |  | 42 | 59 | 0.0073694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2701-312_0_4_line_52 |  | 43 | 77 | 0.0076498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2701-312_0_4_line_53 |  | 44 | 78 | 0.0076622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2701-312_0_4_line_54 |  | 45 | 76 | 0.0084998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2701-312_0_4_line_55 |  | 46 | 67 | 0.0066353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2701-312_0_4_line_56 |  | 47 | 71 | 0.0072409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2701-312_0_4_line_57 |  | 48 | 69 | 0.0075226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2701-312_0_4_line_58 |  | 49 | 50 | 0.0066848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2701-312_0_4_line_59 |  | 50 | 53 | 0.0077162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2701-312_0_4_line_60 |  | 54 | 60 | 0.0084999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2701-312_0_4_line_61 |  | 55 | 70 | 0.0070992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2701-312_0_4_line_62 |  | 56 | 72 | 0.0085015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_2701-312_0_4_line_63 |  | 57 | 62 | 0.0085023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2701-312_0_4_line_64 |  | 59 | 68 | 0.0066356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2701-312_0_4_line_65 |  | 60 | 61 | 0.0084611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2701-312_0_4_line_66 |  | 61 | 62 | 0.0084974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2701-312_0_4_line_67 |  | 63 | 64 | 0.012147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2701-312_0_4_line_68 |  | 64 | 71 | 0.01624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2701-312_0_4_line_69 |  | 65 | 66 | 0.0059261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2701-312_0_4_line_70 |  | 65 | 67 | 0.0072248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2701-312_0_4_line_71 |  | 66 | 68 | 0.0058293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2701-312_0_4_line_72 |  | 69 | 70 | 0.0071005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2701-312_0_4_line_73 |  | 72 | 73 | 0.0084571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_2701-312_0_4_line_74 |  | 73 | 74 | 0.010721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_2701-312_0_4_line_75 |  | 74 | 75 | 0.010722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2701-312_0_4_line_76 |  | 75 | 76 | 0.0085005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2701-312_0_4_line_77 |  | 77 | 78 | 0.0066367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-312_0_4_trafo_61 | 0.63 MVA 20/0.4 kV | 79 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2609628.424 | 1267057.9707 | 2609627.7799 | 1267065.2636 | 2609635.0415 | 1267065.7222
1 | 2609628.424 | 1267057.9707 | 2609645.218 | 1267059.2408
2 | 2609546.9681 | 1267042.5064 | 2609546.0556 | 1267052.99 | 2609562.418 | 1267053.9392 | 2609592.4031 | 1267055.6664 | 2609625.4963 | 1267057.7547 | 2609628.424 | 1267057.9707
3 | 2609664.0303 | 1267060.6636 | 2609645.218 | 1267059.2408
4 | 2609546.9681 | 1267042.5064 | 2609550.4021 | 1267003.0162
5 | 2609663.56 | 1267067.5232 | 2609664.0303 | 1267060.6636
6 | 2609663.56 | 1267067.5232 | 2609681.1334 | 1267068.9528 | 2609678.5543 | 1267104.3066
7 | 2609664.0303 | 1267060.6636 | 2609667.7297 | 1267060.9422
8 | 2609678.5543 | 1267104.3066 | 2609696.6694 | 1267105.7704
9 | 2609678.5543 | 1267104.3066 | 2609677.7437 | 1267115.4037
10 | 2609550.4021 | 1267003.0162 | 2609551.1508 | 1266994.4071
11 | 2609547.0301 | 1266947.6403 | 2609546.9152 | 1266948.8854 | 2609545.4419 | 1266966.3619 | 2609545.342 | 1266967.6627
12 | 2609545.342 | 1266967.6627 | 2609551.3855 | 1266968.1616 | 2609553.2259 | 1266970.544 | 2609553.2259 | 1266970.544
13 | 2609547.0301 | 1266947.6403 | 2609553.2316 | 1266948.2062 | 2609554.8524 | 1266945.7907
14 | 2609553.2259 | 1266970.544 | 2609553.0522 | 1266972.5409
15 | 2609693.4185 | 1266888.28 | 2609670.3678 | 1266884.3934
16 | 2609693.4185 | 1266888.28 | 2609701.7941 | 1266889.6946 | 2609704.7164 | 1266879.4366 | 2609707.8168 | 1266870.7467
17 | 2609693.4185 | 1266888.28 | 2609701.7941 | 1266889.6946 | 2609711.7199 | 1266891.3897 | 2609719.6212 | 1266892.7925
18 | 2609693.4185 | 1266888.28 | 2609691.8852 | 1266909.4312
19 | 2609707.8168 | 1266870.7467 | 2609673.8748 | 1266865.5504
20 | 2609719.6212 | 1266892.7925 | 2609731.4433 | 1266894.8132
21 | 2609719.6212 | 1266892.7925 | 2609718.3691 | 1266908.3677
22 | 2609691.8852 | 1266909.4312 | 2609691.2586 | 1266918.0748
23 | 2609814.3928 | 1266909.2485 | 2609798.9334 | 1266906.528
24 | 2609814.3928 | 1266909.2485 | 2609813.1066 | 1266927.9908
25 | 2609813.1066 | 1266927.9908 | 2609812.6122 | 1266935.1945
26 | 2609731.4433 | 1266894.8132 | 2609742.0725 | 1266896.6329
27 | 2609716.7887 | 1266928.026 | 2609718.3691 | 1266908.3677
28 | 2609673.8748 | 1266865.5504 | 2609659.2206 | 1266863.3068
29 | 2609758.515 | 1266993.5265 | 2609790.3257 | 1266995.9726
30 | 2609758.515 | 1266993.5265 | 2609759.3446 | 1266982.0225
31 | 2609758.515 | 1266993.5265 | 2609740.7026 | 1266992.2511
32 | 2609790.3257 | 1266995.9726 | 2609790.952 | 1266996.0208
33 | 2609740.7026 | 1266992.2511 | 2609733.3958 | 1266991.7279
34 | 2609554.8524 | 1266945.7907 | 2609555.6537 | 1266944.5964 | 2609555.764 | 1266943.3579
35 | 2609688.8071 | 1267057.4795 | 2609686.5975 | 1267060.0443 | 2609683.9981 | 1267061.5967 | 2609680.934 | 1267061.9364 | 2609667.7297 | 1267060.9422
36 | 2609688.8071 | 1267057.4795 | 2609682.4654 | 1267055.2565 | 2609681.414 | 1267053.8093 | 2609682.328 | 1267041.2129
37 | 2609682.9476 | 1267032.6739 | 2609682.328 | 1267041.2129
38 | 2609711.7918 | 1266990.181 | 2609725.0198 | 1266991.1282
39 | 2609711.7918 | 1266990.181 | 2609714.4057 | 1266957.6677
40 | 2609725.0198 | 1266991.1282 | 2609733.3958 | 1266991.7279
41 | 2609715.048 | 1266949.6784 | 2609714.4057 | 1266957.6677
42 | 2609686.2341 | 1266987.3819 | 2609686.6381 | 1266981.8099
43 | 2609686.2341 | 1266987.3819 | 2609686.0232 | 1266990.2888
44 | 2609687.2527 | 1266973.3318 | 2609686.6381 | 1266981.8099
45 | 2609686.0232 | 1266990.2888 | 2609685.4054 | 1266998.8022
46 | 2609696.6694 | 1267105.7704 | 2609695.8089 | 1267117.4041
47 | 2609677.7437 | 1267115.4037 | 2609676.9934 | 1267125.6749
48 | 2609808.3461 | 1266997.3556 | 2609797.0794 | 1266996.4919
49 | 2609797.0794 | 1266996.4919 | 2609790.952 | 1266996.0208
50 | 2609808.3461 | 1266997.3556 | 2609809.8994 | 1266974.7219
51 | 2609810.404 | 1266967.3698 | 2609809.8994 | 1266974.7219
52 | 2609551.8135 | 1266986.786 | 2609551.1508 | 1266994.4071
53 | 2609552.3884 | 1266980.1743 | 2609553.0522 | 1266972.5409
54 | 2609691.2586 | 1266918.0748 | 2609690.644 | 1266926.5523
55 | 2609812.1579 | 1266941.8142 | 2609812.6122 | 1266935.1945
56 | 2609742.0725 | 1266896.6329 | 2609749.2096 | 1266897.8547
57 | 2609716.7887 | 1266928.026 | 2609716.1859 | 1266935.5245
58 | 2609556.4484 | 1266935.6721 | 2609557.0413 | 1266929.0136
59 | 2609556.4484 | 1266935.6721 | 2609555.764 | 1266943.3579
60 | 2609683.5628 | 1267024.1962 | 2609682.9476 | 1267032.6739
61 | 2609715.048 | 1266949.6784 | 2609715.6169 | 1266942.6021
62 | 2609687.8674 | 1266964.8525 | 2609687.2527 | 1266973.3318
63 | 2609684.7901 | 1267007.2823 | 2609685.4054 | 1266998.8022
64 | 2609810.8583 | 1266960.7498 | 2609810.404 | 1266967.3698
65 | 2609683.5628 | 1267024.1962 | 2609684.1751 | 1267015.7573
66 | 2609684.7901 | 1267007.2823 | 2609684.1751 | 1267015.7573
67 | 2609765.2163 | 1266900.5948 | 2609764.3427 | 1266912.7103
68 | 2609765.2163 | 1266900.5948 | 2609749.2096 | 1266897.8547
69 | 2609811.2575 | 1266954.9342 | 2609811.6632 | 1266949.022
70 | 2609812.1579 | 1266941.8142 | 2609811.6632 | 1266949.022
71 | 2609810.8583 | 1266960.7498 | 2609811.2575 | 1266954.9342
72 | 2609715.6169 | 1266942.6021 | 2609716.1859 | 1266935.5245
73 | 2609687.8674 | 1266964.8525 | 2609688.4789 | 1266956.4175
74 | 2609688.4789 | 1266956.4175 | 2609689.2541 | 1266945.7244
75 | 2609690.0293 | 1266935.0306 | 2609689.2541 | 1266945.7244
76 | 2609690.644 | 1266926.5523 | 2609690.0293 | 1266935.0306
77 | 2609551.8135 | 1266986.786 | 2609552.3884 | 1266980.1743

## bus_geodata
| x | y | coords
0 | 2609635.0415 | 1267065.7222
1 | 2609628.424 | 1267057.9707
2 | 2609645.218 | 1267059.2408
3 | 2609546.9681 | 1267042.5064
4 | 2609663.56 | 1267067.5232
5 | 2609664.0303 | 1267060.6636
6 | 2609678.5543 | 1267104.3066
7 | 2609550.4021 | 1267003.0162
8 | 2609545.342 | 1266967.6627
9 | 2609547.0301 | 1266947.6403
10 | 2609553.2259 | 1266970.544
11 | 2609693.4185 | 1266888.28
12 | 2609670.3678 | 1266884.3934
13 | 2609707.8168 | 1266870.7467
14 | 2609719.6212 | 1266892.7925
15 | 2609691.8852 | 1266909.4312
16 | 2609814.3928 | 1266909.2485
17 | 2609798.9334 | 1266906.528
18 | 2609813.1066 | 1266927.9908
19 | 2609731.4433 | 1266894.8132
20 | 2609718.3691 | 1266908.3677
21 | 2609673.8748 | 1266865.5504
22 | 2609758.515 | 1266993.5265
23 | 2609790.3257 | 1266995.9726
24 | 2609759.3446 | 1266982.0225
25 | 2609740.7026 | 1266992.2511
26 | 2609554.8524 | 1266945.7907
27 | 2609688.8071 | 1267057.4795
28 | 2609667.7297 | 1267060.9422
29 | 2609682.328 | 1267041.2129
30 | 2609711.7918 | 1266990.181
31 | 2609725.0198 | 1266991.1282
32 | 2609714.4057 | 1266957.6677
33 | 2609686.2341 | 1266987.3819
34 | 2609686.6381 | 1266981.8099
35 | 2609686.0232 | 1266990.2888
36 | 2609696.6694 | 1267105.7704
37 | 2609677.7437 | 1267115.4037
38 | 2609695.8089 | 1267117.4041
39 | 2609797.0794 | 1266996.4919
40 | 2609808.3461 | 1266997.3556
41 | 2609790.952 | 1266996.0208
42 | 2609809.8994 | 1266974.7219
43 | 2609551.1508 | 1266994.4071
44 | 2609553.0522 | 1266972.5409
45 | 2609691.2586 | 1266918.0748
46 | 2609812.6122 | 1266935.1945
47 | 2609742.0725 | 1266896.6329
48 | 2609716.7887 | 1266928.026
49 | 2609557.0413 | 1266929.0136
50 | 2609556.4484 | 1266935.6721
51 | 2609659.2206 | 1266863.3068
52 | 2609733.3958 | 1266991.7279
53 | 2609555.764 | 1266943.3579
54 | 2609682.9476 | 1267032.6739
55 | 2609715.048 | 1266949.6784
56 | 2609687.2527 | 1266973.3318
57 | 2609685.4054 | 1266998.8022
58 | 2609676.9934 | 1267125.6749
59 | 2609810.404 | 1266967.3698
60 | 2609683.5628 | 1267024.1962
61 | 2609684.1751 | 1267015.7573
62 | 2609684.7901 | 1267007.2823
63 | 2609764.3427 | 1266912.7103
64 | 2609765.2163 | 1266900.5948
65 | 2609811.6632 | 1266949.022
66 | 2609811.2575 | 1266954.9342
67 | 2609812.1579 | 1266941.8142
68 | 2609810.8583 | 1266960.7498
69 | 2609716.1859 | 1266935.5245
70 | 2609715.6169 | 1266942.6021
71 | 2609749.2096 | 1266897.8547
72 | 2609687.8674 | 1266964.8525
73 | 2609688.4789 | 1266956.4175
74 | 2609689.2541 | 1266945.7244
75 | 2609690.0293 | 1266935.0306
76 | 2609690.644 | 1266926.5523
77 | 2609551.8135 | 1266986.7861
78 | 2609552.3884 | 1266980.1743
79 | 2609686.2341 | 1266987.3819

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98861 | -0.21848 | 0.0095417 | 0.0023914
1 | 0.98874 | -0.21599 | 0 | 0
2 | 0.98928 | -0.20552 | 0.0047112 | 0.0011807
3 | 0.98657 | -0.25816 | 0 | 0
4 | 0.98964 | -0.19851 | 0 | 0
5 | 0.98997 | -0.19222 | 0 | 0
6 | 0.98713 | -0.24725 | 0 | 0
7 | 0.98564 | -0.27617 | 0.0020667 | 0.00051796
8 | 0.98498 | -0.28919 | 0 | 0
9 | 0.98481 | -0.2925 | 0 | 0
10 | 0.98505 | -0.28769 | 0.0050673 | 0.00127
11 | 0.99223 | -0.14925 | 0 | 0
12 | 0.99191 | -0.1554 | 0.014858 | 0.0037238
13 | 0.99199 | -0.15393 | 0 | 0
14 | 0.99122 | -0.16881 | 0 | 0
15 | 0.99351 | -0.12462 | 0.017706 | 0.0044375
16 | 0.98622 | -0.2658 | 0 | 0
17 | 0.9862 | -0.26623 | 0.0015 | 0.00037594
18 | 0.98625 | -0.2653 | 0.0015632 | 0.00039178
19 | 0.99116 | -0.16995 | 0 | 0
20 | 0.9907 | -0.17885 | 0.0027052 | 0.00067798
21 | 0.9917 | -0.15959 | 0.004467 | 0.0011195
22 | 0.98762 | -0.23862 | 0 | 0
23 | 0.98711 | -0.2486 | 0.0020417 | 0.00051169
24 | 0.9876 | -0.239 | 0.001826 | 0.00045763
25 | 0.98794 | -0.23246 | 0.0016394 | 0.00041087
26 | 0.98473 | -0.29401 | 0.0027343 | 0.00068527
27 | 0.99231 | -0.1471 | 0 | 0
28 | 0.99028 | -0.18621 | 0.0058958 | 0.0014776
29 | 0.99419 | -0.11088 | 0.003699 | 0.00092706
30 | 0.98855 | -0.22047 | 0 | 0
31 | 0.98825 | -0.22633 | 0.0021618 | 0.00054181
32 | 0.98929 | -0.20608 | 0.0020775 | 0.00052067
33 | 0.99963 | -0.0071164 | 0 | 0
34 | 1 | 0 | -0.35002 | -0.088226
35 | 0.99943 | -0.010831 | 0.015414 | 0.003863
36 | 0.98646 | -0.26038 | 0 | 0
37 | 0.98702 | -0.24944 | 0.0058681 | 0.0014707
38 | 0.98602 | -0.26883 | 0.040461 | 0.01014
39 | 0.98702 | -0.25031 | 0 | 0
40 | 0.98687 | -0.25312 | 0 | 0
41 | 0.9871 | -0.24877 | 0.0015045 | 0.00037705
42 | 0.98658 | -0.25878 | 0.0017025 | 0.0004267
43 | 0.98546 | -0.27979 | 0.0027157 | 0.00068063
44 | 0.98508 | -0.28718 | 0.0026562 | 0.00066571
45 | 0.99417 | -0.11187 | 0.015513 | 0.0038879
46 | 0.98627 | -0.2649 | 0.001732 | 0.00043407
47 | 0.99111 | -0.17097 | 0.0015774 | 0.00039535
48 | 0.99009 | -0.19057 | 0.0017423 | 0.00043667
49 | 0.98468 | -0.29506 | 0.0019009 | 0.00047641
50 | 0.98469 | -0.29483 | 0.0017999 | 0.00045111
51 | 0.99163 | -0.16086 | 0.004839 | 0.0012128
52 | 0.98808 | -0.22972 | 0.0016379 | 0.0004105
53 | 0.98471 | -0.29432 | 0.0027474 | 0.00068856
54 | 0.99498 | -0.095692 | 0.0036004 | 0.00090234
55 | 0.98949 | -0.20225 | 0.0017984 | 0.00045073
56 | 0.99922 | -0.01482 | 0.015364 | 0.0038505
57 | 0.99841 | -0.030318 | 0.015539 | 0.0038944
58 | 0.98697 | -0.25039 | 0.0051353 | 0.001287
59 | 0.9865 | -0.2604 | 0.0015598 | 0.00039093
60 | 0.9958 | -0.080099 | 0.0036029 | 0.00090297
61 | 0.99664 | -0.064068 | 0.003635 | 0.00091103
62 | 0.99751 | -0.047454 | 0.0036421 | 0.0009128
63 | 0.99103 | -0.17255 | 0.0021556 | 0.00054025
64 | 0.99105 | -0.17208 | 0 | 0
65 | 0.98634 | -0.26349 | 0.0015634 | 0.00039182
66 | 0.98639 | -0.26263 | 0.0011354 | 0.00028455
67 | 0.9863 | -0.26433 | 0.0017283 | 0.00043314
68 | 0.98644 | -0.26167 | 0.0014572 | 0.00036522
69 | 0.98988 | -0.19482 | 0.0015244 | 0.00038205
70 | 0.98968 | -0.19863 | 0.0015569 | 0.00039019
71 | 0.99108 | -0.17146 | 0.0016175 | 0.00040539
72 | 0.99851 | -0.028523 | 0.015333 | 0.0038428
73 | 0.99786 | -0.041039 | 0.01553 | 0.0038923
74 | 0.9971 | -0.055469 | 0.023658 | 0.0059293
75 | 0.99583 | -0.079938 | 0.015556 | 0.0038987
76 | 0.99494 | -0.097053 | 0.015547 | 0.0038965
77 | 0.98531 | -0.28261 | 0.0017924 | 0.00044922
78 | 0.9852 | -0.28485 | 0.0018745 | 0.00046979
79 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0095417 | -0.0023914 | 0.0095429 | 0.0023919 | 1.1291e-06 | 5.3541e-07 | 0.014362 | 0.014362 | 0.014362 | 0.98861 | -0.21848 | 0.98874 | -0.21599 | 3.9455
1 | -0.034985 | -0.0087994 | 0.035003 | 0.0088104 | 1.7516e-05 | 1.0994e-05 | 0.052662 | 0.052662 | 0.052662 | 0.98874 | -0.21599 | 0.98928 | -0.20552 | 14.4677
2 | 0.025442 | 0.0064075 | -0.025391 | -0.0063759 | 5.1184e-05 | 3.1567e-05 | 0.038301 | 0.038301 | 0.038301 | 0.98874 | -0.21599 | 0.98657 | -0.25816 | 10.5223
3 | -0.039714 | -0.0099911 | 0.039739 | 0.010007 | 2.5256e-05 | 1.5921e-05 | 0.059749 | 0.059749 | 0.059749 | 0.98928 | -0.20552 | 0.98997 | -0.19222 | 16.4145
4 | 0.025391 | 0.0063759 | -0.025369 | -0.0063625 | 2.1806e-05 | 1.345e-05 | 0.038301 | 0.038301 | 0.038301 | 0.98657 | -0.25816 | 0.98564 | -0.27617 | 10.5224
5 | -0.051627 | -0.013001 | 0.051643 | 0.013011 | 1.5547e-05 | 9.8614e-06 | 0.077648 | 0.077648 | 0.077648 | 0.98964 | -0.19851 | 0.98997 | -0.19222 | 21.332
6 | 0.051627 | 0.013001 | -0.051507 | -0.012925 | 0.00012001 | 7.6127e-05 | 0.077648 | 0.077649 | 0.077649 | 0.98964 | -0.19851 | 0.98713 | -0.24725 | 21.3321
7 | -0.091382 | -0.023018 | 0.091408 | 0.023035 | 2.6263e-05 | 1.6761e-05 | 0.1374 | 0.1374 | 0.1374 | 0.98997 | -0.19222 | 0.99028 | -0.18621 | 37.7464
8 | 0.040503 | 0.010167 | -0.040477 | -0.010151 | 2.5334e-05 | 1.5982e-05 | 0.06106 | 0.06106 | 0.06106 | 0.98713 | -0.24725 | 0.98646 | -0.26038 | 16.7747
9 | 0.011005 | 0.0027583 | -0.011004 | -0.0027577 | 1.1482e-06 | 5.9265e-07 | 0.016589 | 0.016589 | 0.016589 | 0.98713 | -0.24725 | 0.98702 | -0.24944 | 4.5574
10 | 0.023303 | 0.0058445 | -0.023299 | -0.0058421 | 4.0109e-06 | 2.4569e-06 | 0.035181 | 0.035181 | 0.035181 | 0.98564 | -0.27617 | 0.98546 | -0.27979 | 9.6652
11 | 0.0091848 | 0.0023022 | -0.0091834 | -0.0023016 | 1.4508e-06 | 6.728e-07 | 0.013876 | 0.013876 | 0.013876 | 0.98498 | -0.28919 | 0.98481 | -0.2925 | 3.812
12 | -0.0091848 | -0.0023022 | 0.0091855 | 0.0023025 | 6.5518e-07 | 3.0381e-07 | 0.013876 | 0.013876 | 0.013876 | 0.98498 | -0.28919 | 0.98505 | -0.28769 | 3.812
13 | 0.0091834 | 0.0023016 | -0.0091827 | -0.0023013 | 6.5964e-07 | 3.0594e-07 | 0.013876 | 0.013876 | 0.013876 | 0.98481 | -0.2925 | 0.98473 | -0.29401 | 3.812
14 | -0.014253 | -0.0035725 | 0.014253 | 0.0035727 | 3.4844e-07 | 1.9748e-07 | 0.02153 | 0.02153 | 0.02153 | 0.98505 | -0.28769 | 0.98508 | -0.28718 | 5.9149
15 | 0.014863 | 0.0037263 | -0.014858 | -0.0037238 | 4.3551e-06 | 2.4855e-06 | 0.022289 | 0.022289 | 0.022289 | 0.99223 | -0.14925 | 0.99191 | -0.1554 | 6.1235
16 | 0.0093108 | 0.0023344 | -0.0093088 | -0.0023335 | 2.0756e-06 | 9.618e-07 | 0.013963 | 0.013964 | 0.013964 | 0.99223 | -0.14925 | 0.99199 | -0.15393 | 3.8362
17 | 0.04166 | 0.010495 | -0.041621 | -0.01047 | 3.8942e-05 | 2.458e-05 | 0.062495 | 0.062495 | 0.062495 | 0.99223 | -0.14925 | 0.99122 | -0.16881 | 17.1691
18 | -0.065834 | -0.016556 | 0.065911 | 0.016605 | 7.7547e-05 | 4.9356e-05 | 0.098748 | 0.098748 | 0.098748 | 0.99223 | -0.14925 | 0.99351 | -0.12462 | 27.1286
19 | 0.0093088 | 0.0023335 | -0.0093063 | -0.0023323 | 2.5107e-06 | 1.1637e-06 | 0.013964 | 0.013964 | 0.013964 | 0.99199 | -0.15393 | 0.9917 | -0.15959 | 3.8362
20 | 0.0053513 | 0.0013407 | -0.005351 | -0.0013407 | 2.8941e-07 | 3.108e-08 | 0.0080333 | 0.0080333 | 0.0080333 | 0.99122 | -0.16881 | 0.99116 | -0.16995 | 2.207
21 | 0.03627 | 0.0091297 | -0.036252 | -0.0091188 | 1.738e-05 | 1.0922e-05 | 0.054462 | 0.054462 | 0.054462 | 0.99122 | -0.16881 | 0.9907 | -0.17885 | 14.9622
22 | -0.083617 | -0.021043 | 0.083668 | 0.021075 | 5.0996e-05 | 3.2525e-05 | 0.12527 | 0.12527 | 0.12527 | 0.99351 | -0.12462 | 0.99417 | -0.11187 | 34.414
23 | 0.0015 | 0.00037576 | -0.0015 | -0.00037594 | 3.0151e-08 | -1.81e-07 | 0.0022632 | 0.0022633 | 0.0022633 | 0.98622 | -0.2658 | 0.9862 | -0.26623 | 0.62178
24 | -0.0015 | -0.00037576 | 0.0015001 | 0.00037554 | 3.6083e-08 | -2.1663e-07 | 0.0022632 | 0.0022631 | 0.0022632 | 0.98622 | -0.2658 | 0.98625 | -0.2653 | 0.62176
25 | -0.0030633 | -0.00076732 | 0.0030634 | 0.00076727 | 5.7836e-08 | -5.5129e-08 | 0.0046217 | 0.0046216 | 0.0046217 | 0.98625 | -0.2653 | 0.98627 | -0.2649 | 1.2697
26 | 0.005351 | 0.0013407 | -0.0053508 | -0.0013407 | 2.6097e-07 | 2.8044e-08 | 0.0080333 | 0.0080334 | 0.0080334 | 0.99116 | -0.16995 | 0.99111 | -0.17097 | 2.207
27 | 0.033547 | 0.0084408 | -0.033528 | -0.0084291 | 1.8786e-05 | 1.1769e-05 | 0.050399 | 0.050399 | 0.050399 | 0.9907 | -0.17885 | 0.99009 | -0.19057 | 13.846
28 | 0.0048393 | 0.0012128 | -0.004839 | -0.0012128 | 2.9312e-07 | -3.6696e-09 | 0.0072612 | 0.0072612 | 0.0072612 | 0.9917 | -0.15959 | 0.99163 | -0.16086 | 1.9948
29 | 0.017506 | 0.0043924 | -0.017498 | -0.0043875 | 8.3244e-06 | 4.9195e-06 | 0.026377 | 0.026378 | 0.026378 | 0.98762 | -0.23862 | 0.98711 | -0.2486 | 7.2466
30 | 0.001826 | 0.0004575 | -0.001826 | -0.00045763 | 3.2737e-08 | -1.2664e-07 | 0.0027511 | 0.0027512 | 0.0027512 | 0.98762 | -0.23862 | 0.9876 | -0.239 | 0.75582
31 | -0.019332 | -0.0048499 | 0.019338 | 0.0048533 | 5.682e-06 | 3.4079e-06 | 0.029129 | 0.029128 | 0.029129 | 0.98762 | -0.23862 | 0.98794 | -0.23246 | 8.0024
32 | 0.015456 | 0.0038758 | -0.015456 | -0.0038757 | 1.2788e-07 | 7.3816e-08 | 0.0233 | 0.0233 | 0.0233 | 0.98711 | -0.2486 | 0.9871 | -0.24877 | 6.4011
33 | -0.020977 | -0.0052642 | 0.02098 | 0.0052659 | 2.7427e-06 | 1.6615e-06 | 0.031598 | 0.031598 | 0.031598 | 0.98794 | -0.23246 | 0.98808 | -0.22972 | 8.6807
34 | 0.0064484 | 0.001616 | -0.0064483 | -0.001616 | 9.5481e-08 | 2.6994e-08 | 0.0097441 | 0.0097441 | 0.0097441 | 0.98473 | -0.29401 | 0.98471 | -0.29432 | 2.677
35 | 0.097487 | 0.024629 | -0.097304 | -0.024513 | 0.00018239 | 0.00011644 | 0.14626 | 0.14626 | 0.14626 | 0.99231 | -0.1471 | 0.99028 | -0.18621 | 40.1802
36 | -0.097487 | -0.024629 | 0.097656 | 0.024737 | 0.00016956 | 0.00010825 | 0.14626 | 0.14626 | 0.14626 | 0.99231 | -0.1471 | 0.99419 | -0.11088 | 40.1802
37 | -0.10136 | -0.025664 | 0.10143 | 0.025711 | 7.3974e-05 | 4.7232e-05 | 0.15179 | 0.15179 | 0.15179 | 0.99419 | -0.11088 | 0.99498 | -0.095692 | 41.7011
38 | 0.02479 | 0.0062247 | -0.024783 | -0.0062204 | 6.9263e-06 | 4.2629e-06 | 0.037319 | 0.037319 | 0.037319 | 0.98855 | -0.22047 | 0.98825 | -0.22633 | 10.2526
39 | -0.02479 | -0.0062247 | 0.024807 | 0.0062352 | 1.7036e-05 | 1.0484e-05 | 0.037319 | 0.037319 | 0.037319 | 0.98855 | -0.22047 | 0.98929 | -0.20608 | 10.2526
40 | 0.022621 | 0.0056786 | -0.022618 | -0.0056764 | 3.6541e-06 | 2.231e-06 | 0.034064 | 0.034064 | 0.034064 | 0.98825 | -0.22633 | 0.98808 | -0.22972 | 9.3583
41 | -0.026885 | -0.0067558 | 0.02689 | 0.0067589 | 4.9164e-06 | 3.0435e-06 | 0.040444 | 0.040444 | 0.040444 | 0.98929 | -0.20608 | 0.98949 | -0.20225 | 11.111
42 | -0.14736 | -0.037416 | 0.14741 | 0.037449 | 5.0481e-05 | 3.2161e-05 | 0.21953 | 0.21953 | 0.21953 | 0.99963 | -0.0071164 | 1 | 0 | 30.1549
43 | 0.14736 | 0.037416 | -0.14733 | -0.0374 | 2.6336e-05 | 1.6779e-05 | 0.21953 | 0.21953 | 0.21953 | 0.99963 | -0.0071164 | 0.99943 | -0.010831 | 30.1549
44 | 0.20096 | 0.050777 | -0.20082 | -0.050686 | 0.00014266 | 9.1078e-05 | 0.29918 | 0.29918 | 0.29918 | 1 | 0 | 0.99922 | -0.01482 | 41.0956
45 | 0.13192 | 0.033537 | -0.1318 | -0.033458 | 0.0001237 | 7.9053e-05 | 0.19658 | 0.19658 | 0.19658 | 0.99943 | -0.010831 | 0.99841 | -0.030318 | 54.0053
46 | 0.040477 | 0.010151 | -0.040461 | -0.01014 | 1.631e-05 | 1.0289e-05 | 0.06106 | 0.06106 | 0.06106 | 0.98646 | -0.26038 | 0.98602 | -0.26883 | 16.7747
47 | 0.0051355 | 0.001287 | -0.0051353 | -0.001287 | 2.315e-07 | 1.6539e-08 | 0.0077423 | 0.0077423 | 0.0077423 | 0.98702 | -0.24944 | 0.98697 | -0.25039 | 2.127
48 | 0.01395 | 0.0034981 | -0.013948 | -0.0034971 | 1.8688e-06 | 1.0521e-06 | 0.021032 | 0.021032 | 0.021032 | 0.98702 | -0.25031 | 0.98687 | -0.25312 | 5.778
49 | -0.01395 | -0.0034981 | 0.013951 | 0.0034987 | 1.0194e-06 | 5.7387e-07 | 0.021032 | 0.021032 | 0.021032 | 0.98702 | -0.25031 | 0.9871 | -0.24877 | 5.778
50 | 0.013948 | 0.0034971 | -0.013945 | -0.0034949 | 3.7633e-06 | 2.1187e-06 | 0.021032 | 0.021032 | 0.021032 | 0.98687 | -0.25312 | 0.98658 | -0.25878 | 5.7781
51 | 0.012242 | 0.0030682 | -0.012241 | -0.0030677 | 9.4217e-07 | 5.0889e-07 | 0.018464 | 0.018464 | 0.018464 | 0.98658 | -0.25878 | 0.9865 | -0.2604 | 5.0726
52 | 0.020583 | 0.0051614 | -0.02058 | -0.0051598 | 2.7712e-06 | 1.6761e-06 | 0.031081 | 0.031081 | 0.031081 | 0.98546 | -0.27979 | 0.98531 | -0.28261 | 8.5386
53 | -0.016909 | -0.0042384 | 0.016911 | 0.0042396 | 1.8746e-06 | 1.1022e-06 | 0.025543 | 0.025543 | 0.025543 | 0.98508 | -0.28718 | 0.9852 | -0.28485 | 7.0172
54 | -0.099181 | -0.024963 | 0.099251 | 0.025008 | 7.0277e-05 | 4.4867e-05 | 0.14849 | 0.14849 | 0.14849 | 0.99417 | -0.11187 | 0.99494 | -0.097053 | 40.7928
55 | -0.0047953 | -0.0012013 | 0.0047955 | 0.0012013 | 1.3024e-07 | -1.3276e-09 | 0.0072347 | 0.0072347 | 0.0072347 | 0.98627 | -0.2649 | 0.9863 | -0.26433 | 1.9876
56 | 0.0037733 | 0.00094531 | -0.0037733 | -0.00094534 | 8.7143e-08 | -3.754e-08 | 0.005665 | 0.0056651 | 0.0056651 | 0.99111 | -0.17097 | 0.99108 | -0.17146 | 1.5563
57 | 0.031786 | 0.0079924 | -0.03178 | -0.0079884 | 6.4403e-06 | 4.0251e-06 | 0.047781 | 0.047781 | 0.047781 | 0.99009 | -0.19057 | 0.98988 | -0.19482 | 13.1266
58 | -0.0019009 | -0.00047641 | 0.0019009 | 0.00047634 | 2.0685e-08 | -7.1795e-08 | 0.0028726 | 0.0028725 | 0.0028726 | 0.98468 | -0.29506 | 0.98469 | -0.29483 | 0.78917
59 | -0.0037009 | -0.00092744 | 0.0037009 | 0.0009274 | 9.05e-08 | -4.0237e-08 | 0.0055925 | 0.0055925 | 0.0055925 | 0.98469 | -0.29483 | 0.98471 | -0.29432 | 1.5364
60 | -0.10503 | -0.026614 | 0.10511 | 0.026664 | 7.8745e-05 | 5.0286e-05 | 0.15718 | 0.15718 | 0.15718 | 0.99498 | -0.095692 | 0.9958 | -0.080099 | 43.1804
61 | -0.028688 | -0.0072096 | 0.028693 | 0.0072127 | 4.9564e-06 | 3.0809e-06 | 0.043148 | 0.043148 | 0.043148 | 0.98949 | -0.20225 | 0.98968 | -0.19863 | 11.854
62 | 0.18545 | 0.046836 | -0.18533 | -0.046758 | 0.00012169 | 7.7658e-05 | 0.2763 | 0.2763 | 0.2763 | 0.99922 | -0.01482 | 0.99851 | -0.028523 | 37.9529
63 | 0.11626 | 0.029563 | -0.11616 | -0.029502 | 9.5889e-05 | 6.1258e-05 | 0.17342 | 0.17342 | 0.17342 | 0.99841 | -0.030318 | 0.99751 | -0.047454 | 47.643
64 | 0.010681 | 0.0026768 | -0.010681 | -0.0026765 | 6.4592e-07 | 3.2868e-07 | 0.016111 | 0.016112 | 0.016112 | 0.9865 | -0.2604 | 0.98644 | -0.26167 | 4.4262
65 | -0.10871 | -0.027567 | 0.10879 | 0.027621 | 8.3847e-05 | 5.3552e-05 | 0.16256 | 0.16256 | 0.16256 | 0.9958 | -0.080099 | 0.99664 | -0.064068 | 44.6594
66 | -0.11243 | -0.028532 | 0.11252 | 0.028589 | 8.9923e-05 | 5.744e-05 | 0.16799 | 0.16799 | 0.16799 | 0.99664 | -0.064068 | 0.99751 | -0.047454 | 46.1504
67 | -0.0021556 | -0.00054025 | 0.0021557 | 0.00054013 | 4.7718e-08 | -1.2598e-07 | 0.0032367 | 0.0032366 | 0.0032367 | 0.99103 | -0.17255 | 0.99105 | -0.17208 | 0.88919
68 | -0.0021557 | -0.00054013 | 0.0021557 | 0.00053996 | 6.3793e-08 | -1.6843e-07 | 0.0032366 | 0.0032365 | 0.0032366 | 0.99105 | -0.17208 | 0.99108 | -0.17146 | 0.88918
69 | -0.0080874 | -0.0020264 | 0.0080877 | 0.0020265 | 3.3079e-07 | 1.3607e-07 | 0.012201 | 0.012201 | 0.012201 | 0.98634 | -0.26349 | 0.98639 | -0.26263 | 3.3518
70 | 0.006524 | 0.0016346 | -0.0065237 | -0.0016345 | 2.6244e-07 | 7.5752e-08 | 0.0098421 | 0.0098421 | 0.0098421 | 0.98634 | -0.26349 | 0.9863 | -0.26433 | 2.7039
71 | -0.0092231 | -0.0023111 | 0.0092235 | 0.0023113 | 4.2317e-07 | 1.9641e-07 | 0.013913 | 0.013913 | 0.013913 | 0.98639 | -0.26263 | 0.98644 | -0.26167 | 3.8223
72 | 0.030255 | 0.0076063 | -0.03025 | -0.0076029 | 5.5098e-06 | 3.435e-06 | 0.045489 | 0.045489 | 0.045489 | 0.98988 | -0.19482 | 0.98968 | -0.19863 | 12.497
73 | 0.17 | 0.042915 | -0.1699 | -0.04285 | 0.00010186 | 6.4969e-05 | 0.25345 | 0.25345 | 0.25345 | 0.99851 | -0.028523 | 0.99786 | -0.041039 | 34.8142
74 | 0.15437 | 0.038958 | -0.15426 | -0.03889 | 0.00010661 | 6.7949e-05 | 0.23029 | 0.23029 | 0.23029 | 0.99786 | -0.041039 | 0.9971 | -0.055469 | 31.633
75 | 0.1306 | 0.032961 | -0.13045 | -0.032863 | 0.00015286 | 9.769e-05 | 0.19498 | 0.19498 | 0.19498 | 0.9971 | -0.055469 | 0.99583 | -0.079938 | 53.5666
76 | 0.11489 | 0.028964 | -0.1148 | -0.028904 | 9.4018e-05 | 6.0061e-05 | 0.17174 | 0.17174 | 0.17174 | 0.99583 | -0.079938 | 0.99494 | -0.097053 | 47.1807
77 | 0.018788 | 0.0047105 | -0.018786 | -0.0047093 | 2.0036e-06 | 1.1978e-06 | 0.028374 | 0.028374 | 0.028374 | 0.98531 | -0.28261 | 0.9852 | -0.28485 | 7.795

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36539 | 0.092077

## res_load
| p_mw | q_mvar
0 | 0.0095417 | 0.0023914
1 | 0.0047112 | 0.0011807
2 | 0.0020667 | 0.00051796
3 | 0.0050673 | 0.00127
4 | 0.014858 | 0.0037238
5 | 0.017706 | 0.0044375
6 | 0.0015 | 0.00037594
7 | 0.0015632 | 0.00039178
8 | 0.0027052 | 0.00067798
9 | 0.004467 | 0.0011195
10 | 0.0020417 | 0.00051169
11 | 0.001826 | 0.00045763
12 | 0.0016394 | 0.00041087
13 | 0.0027343 | 0.00068527
14 | 0.0058958 | 0.0014776
15 | 0.003699 | 0.00092706
16 | 0.0021618 | 0.00054181
17 | 0.0020775 | 0.00052067
18 | 0.015365 | 0.0038509
19 | 0.015414 | 0.003863
20 | 0.0058681 | 0.0014707
21 | 0.040461 | 0.01014
22 | 0.0015045 | 0.00037705
23 | 0.0017025 | 0.0004267
24 | 0.0027157 | 0.00068063
25 | 0.0026562 | 0.00066571
26 | 0.015513 | 0.0038879
27 | 0.001732 | 0.00043407
28 | 0.0015774 | 0.00039535
29 | 0.0017423 | 0.00043667
30 | 0.0019009 | 0.00047641
31 | 0.0017999 | 0.00045111
32 | 0.004839 | 0.0012128
33 | 0.0016379 | 0.0004105
34 | 0.0027474 | 0.00068856
35 | 0.0036004 | 0.00090234
36 | 0.0017984 | 0.00045073
37 | 0.015364 | 0.0038505
38 | 0.015539 | 0.0038944
39 | 0.0051353 | 0.001287
40 | 0.0015598 | 0.00039093
41 | 0.0036029 | 0.00090297
42 | 0.003635 | 0.00091103
43 | 0.0036421 | 0.0009128
44 | 0.0021556 | 0.00054025
45 | 0.0015634 | 0.00039182
46 | 0.0011354 | 0.00028455
47 | 0.0017283 | 0.00043314
48 | 0.0014572 | 0.00036522
49 | 0.0015244 | 0.00038205
50 | 0.0015569 | 0.00039019
51 | 0.0016175 | 0.00040539
52 | 0.015333 | 0.0038428
53 | 0.01553 | 0.0038923
54 | 0.023658 | 0.0059293
55 | 0.015556 | 0.0038987
56 | 0.015547 | 0.0038965
57 | 0.0017924 | 0.00044922
58 | 0.0018745 | 0.00046979

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1