## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2701-334_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2701-334_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2701-334_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2701-334_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2701-334_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2701-334_0_6_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_2701-334_0_6_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_2701-334_0_6_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_2701-334_0_6_node_34 | 0.4 | n |  | TRUE
9 | bus_LV_2701-334_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2701-334_0_6_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2701-334_0_6_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2701-334_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2701-334_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2701-334_0_6_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_2701-334_0_6_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_2701-334_0_6_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_2701-334_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_2701-334_0_6_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2701-334_0_6_node_40 | 0.4 | n |  | TRUE
20 | bus_LV_2701-334_0_6_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_2701-334_0_6_node_37 | 0.4 | n |  | TRUE
22 | bus_LV_2701-334_0_6_node_77 | 0.4 | n |  | TRUE
23 | bus_LV_2701-334_0_6_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_2701-334_0_6_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2701-334_0_6_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_2701-334_0_6_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_2701-334_0_6_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_2701-334_0_6_node_39 | 0.4 | n |  | TRUE
29 | bus_LV_2701-334_0_6_node_74 | 0.4 | n |  | TRUE
30 | bus_LV_2701-334_0_6_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_2701-334_0_6_node_45 | 0.4 | n |  | TRUE
32 | bus_LV_2701-334_0_6_node_160 | 0.4 | n |  | TRUE
33 | bus_LV_2701-334_0_6_node_183 | 0.4 | n |  | TRUE
34 | bus_LV_2701-334_0_6_node_117 | 0.4 | n |  | TRUE
35 | bus_LV_2701-334_0_6_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_2701-334_0_6_node_101 | 0.4 | n |  | TRUE
37 | bus_LV_2701-334_0_6_node_87 | 0.4 | n |  | TRUE
38 | bus_LV_2701-334_0_6_node_97 | 0.4 | n |  | TRUE
39 | bus_LV_2701-334_0_6_node_44 | 0.4 | n |  | TRUE
40 | bus_LV_2701-334_0_6_node_179 | 0.4 | n |  | TRUE
41 | bus_LV_2701-334_0_6_node_48 | 0.4 | n |  | TRUE
42 | bus_LV_2701-334_0_6_node_176 | 0.4 | n |  | TRUE
43 | bus_LV_2701-334_0_6_node_127 | 0.4 | n |  | TRUE
44 | bus_LV_2701-334_0_6_node_47 | 0.4 | n |  | TRUE
45 | bus_LV_2701-334_0_6_node_146 | 0.4 | n |  | TRUE
46 | bus_LV_2701-334_0_6_node_164 | 0.4 | n |  | TRUE
47 | bus_LV_2701-334_0_6_node_161 | 0.4 | n |  | TRUE
48 | bus_LV_2701-334_0_6_node_134 | 0.4 | n |  | TRUE
49 | bus_LV_2701-334_0_6_node_131 | 0.4 | n |  | TRUE
50 | bus_LV_2701-334_0_6_node_133 | 0.4 | n |  | TRUE
51 | bus_LV_2701-334_0_6_node_49 | 0.4 | n |  | TRUE
52 | bus_LV_2701-334_0_6_node_132 | 0.4 | n |  | TRUE
53 | bus_LV_2701-334_0_6_node_125 | 0.4 | n |  | TRUE
54 | bus_LV_2701-334_0_6_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_2701-334_0_6_node_136 | 0.4 | n |  | TRUE
56 | bus_LV_2701-334_0_6_node_135 | 0.4 | n |  | TRUE
57 | bus_LV_2701-334_0_6_node_76 | 0.4 | n |  | TRUE
58 | bus_LV_2701-334_0_6_node_69 | 0.4 | n |  | TRUE
59 | bus_LV_2701-334_0_6_node_18 | 0.4 | n |  | TRUE
60 | bus_LV_2701-334_0_6_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_2701-334_0_6_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_2701-334_0_6_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_2701-334_0_6_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_2701-334_0_6_node_67 | 0.4 | n |  | TRUE
65 | bus_LV_2701-334_0_6_node_29 | 0.4 | n |  | TRUE
66 | bus_LV_2701-334_0_6_node_27 | 0.4 | n |  | TRUE
67 | bus_LV_2701-334_0_6_node_122 | 0.4 | n |  | TRUE
68 | bus_LV_2701-334_0_6_node_121 | 0.4 | n |  | TRUE
69 | bus_LV_2701-334_0_6_node_26 | 0.4 | n |  | TRUE
70 | bus_LV_2701-334_0_6_node_28 | 0.4 | n |  | TRUE
71 | bus_LV_2701-334_0_6_node_30 | 0.4 | n |  | TRUE
72 | bus_LV_2701-334_0_6_node_36 | 0.4 | n |  | TRUE
73 | bus_LV_2701-334_0_6_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_2701-334_0_6_node_159 | 0.4 | n |  | TRUE
75 | bus_LV_2701-334_0_6_node_173 | 0.4 | n |  | TRUE
76 | bus_LV_2701-334_0_6_node_180 | 0.4 | n |  | TRUE
77 | bus_LV_2701-334_0_6_node_181 | 0.4 | n |  | TRUE
78 | bus_LV_2701-334_0_6_node_116 | 0.4 | n |  | TRUE
79 | bus_LV_2701-334_0_6_node_107 | 0.4 | n |  | TRUE
80 | bus_LV_2701-334_0_6_node_88 | 0.4 | n |  | TRUE
81 | bus_LV_2701-334_0_6_node_86 | 0.4 | n |  | TRUE
82 | bus_LV_2701-334_0_6_node_96 | 0.4 | n |  | TRUE
83 | bus_LV_2701-334_0_6_node_187 | 0.4 | n |  | TRUE
84 | bus_LV_2701-334_0_6_node_186 | 0.4 | n |  | TRUE
85 | bus_LV_2701-334_0_6_node_108 | 0.4 | n |  | TRUE
86 | bus_LV_2701-334_0_6_node_182 | 0.4 | n |  | TRUE
87 | bus_LV_2701-334_0_6_node_177 | 0.4 | n |  | TRUE
88 | bus_LV_2701-334_0_6_node_128 | 0.4 | n |  | TRUE
89 | bus_LV_2701-334_0_6_node_167 | 0.4 | n |  | TRUE
90 | bus_LV_2701-334_0_6_node_168 | 0.4 | n |  | TRUE
91 | bus_LV_2701-334_0_6_node_145 | 0.4 | n |  | TRUE
92 | bus_LV_2701-334_0_6_node_162 | 0.4 | n |  | TRUE
93 | bus_LV_2701-334_0_6_node_148 | 0.4 | n |  | TRUE
94 | bus_LV_2701-334_0_6_node_130 | 0.4 | n |  | TRUE
95 | bus_LV_2701-334_0_6_node_123 | 0.4 | n |  | TRUE
96 | bus_LV_2701-334_0_6_node_53 | 0.4 | n |  | TRUE
97 | bus_LV_2701-334_0_6_node_55 | 0.4 | n |  | TRUE
98 | bus_LV_2701-334_0_6_node_89 | 0.4 | n |  | TRUE
99 | bus_LV_2701-334_0_6_node_92 | 0.4 | n |  | TRUE
100 | bus_LV_2701-334_0_6_node_83 | 0.4 | n |  | TRUE
101 | bus_LV_2701-334_0_6_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_2701-334_0_6_node_105 | 0.4 | n |  | TRUE
103 | bus_LV_2701-334_0_6_node_103 | 0.4 | n |  | TRUE
104 | bus_LV_2701-334_0_6_node_59 | 0.4 | n |  | TRUE
105 | bus_LV_2701-334_0_6_node_60 | 0.4 | n |  | TRUE
106 | bus_LV_2701-334_0_6_node_61 | 0.4 | n |  | TRUE
107 | bus_LV_2701-334_0_6_node_62 | 0.4 | n |  | TRUE
108 | bus_LV_2701-334_0_6_node_63 | 0.4 | n |  | TRUE
109 | bus_LV_2701-334_0_6_node_93 | 0.4 | n |  | TRUE
110 | bus_LV_2701-334_0_6_node_94 | 0.4 | n |  | TRUE
111 | bus_LV_2701-334_0_6_node_64 | 0.4 | n |  | TRUE
112 | bus_LV_2701-334_0_6_node_65 | 0.4 | n |  | TRUE
113 | bus_LV_2701-334_0_6_node_66 | 0.4 | n |  | TRUE
114 | bus_LV_2701-334_0_6_node_68 | 0.4 | n |  | TRUE
115 | bus_LV_2701-334_0_6_node_99 | 0.4 | n |  | TRUE
116 | bus_LV_2701-334_0_6_node_100 | 0.4 | n |  | TRUE
117 | bus_LV_2701-334_0_6_node_70 | 0.4 | n |  | TRUE
118 | bus_LV_2701-334_0_6_node_71 | 0.4 | n |  | TRUE
119 | bus_LV_2701-334_0_6_node_73 | 0.4 | n |  | TRUE
120 | bus_LV_2701-334_0_6_node_75 | 0.4 | n |  | TRUE
121 | bus_LV_2701-334_0_6_node_78 | 0.4 | n |  | TRUE
122 | bus_LV_2701-334_0_6_node_79 | 0.4 | n |  | TRUE
123 | bus_LV_2701-334_0_6_node_80 | 0.4 | n |  | TRUE
124 | bus_LV_2701-334_0_6_node_81 | 0.4 | n |  | TRUE
125 | bus_LV_2701-334_0_6_node_82 | 0.4 | n |  | TRUE
126 | bus_LV_2701-334_0_6_node_84 | 0.4 | n |  | TRUE
127 | bus_LV_2701-334_0_6_node_85 | 0.4 | n |  | TRUE
128 | bus_LV_2701-334_0_6_node_90 | 0.4 | n |  | TRUE
129 | bus_LV_2701-334_0_6_node_110 | 0.4 | n |  | TRUE
130 | bus_LV_2701-334_0_6_node_111 | 0.4 | n |  | TRUE
131 | bus_LV_2701-334_0_6_node_95 | 0.4 | n |  | TRUE
132 | bus_LV_2701-334_0_6_node_98 | 0.4 | n |  | TRUE
133 | bus_LV_2701-334_0_6_node_102 | 0.4 | n |  | TRUE
134 | bus_LV_2701-334_0_6_node_104 | 0.4 | n |  | TRUE
135 | bus_LV_2701-334_0_6_node_106 | 0.4 | n |  | TRUE
136 | bus_LV_2701-334_0_6_node_114 | 0.4 | n |  | TRUE
137 | bus_LV_2701-334_0_6_node_115 | 0.4 | n |  | TRUE
138 | bus_LV_2701-334_0_6_node_112 | 0.4 | n |  | TRUE
139 | bus_LV_2701-334_0_6_node_113 | 0.4 | n |  | TRUE
140 | bus_LV_2701-334_0_6_node_118 | 0.4 | n |  | TRUE
141 | bus_LV_2701-334_0_6_node_119 | 0.4 | n |  | TRUE
142 | bus_LV_2701-334_0_6_node_120 | 0.4 | n |  | TRUE
143 | bus_LV_2701-334_0_6_node_124 | 0.4 | n |  | TRUE
144 | bus_LV_2701-334_0_6_node_126 | 0.4 | n |  | TRUE
145 | bus_LV_2701-334_0_6_node_142 | 0.4 | n |  | TRUE
146 | bus_LV_2701-334_0_6_node_143 | 0.4 | n |  | TRUE
147 | bus_LV_2701-334_0_6_node_129 | 0.4 | n |  | TRUE
148 | bus_LV_2701-334_0_6_node_144 | 0.4 | n |  | TRUE
149 | bus_LV_2701-334_0_6_node_149 | 0.4 | n |  | TRUE
150 | bus_LV_2701-334_0_6_node_137 | 0.4 | n |  | TRUE
151 | bus_LV_2701-334_0_6_node_138 | 0.4 | n |  | TRUE
152 | bus_LV_2701-334_0_6_node_139 | 0.4 | n |  | TRUE
153 | bus_LV_2701-334_0_6_node_140 | 0.4 | n |  | TRUE
154 | bus_LV_2701-334_0_6_node_141 | 0.4 | n |  | TRUE
155 | bus_LV_2701-334_0_6_node_165 | 0.4 | n |  | TRUE
156 | bus_LV_2701-334_0_6_node_163 | 0.4 | n |  | TRUE
157 | bus_LV_2701-334_0_6_node_166 | 0.4 | n |  | TRUE
158 | bus_LV_2701-334_0_6_node_147 | 0.4 | n |  | TRUE
159 | bus_LV_2701-334_0_6_node_151 | 0.4 | n |  | TRUE
160 | bus_LV_2701-334_0_6_node_152 | 0.4 | n |  | TRUE
161 | bus_LV_2701-334_0_6_node_150 | 0.4 | n |  | TRUE
162 | bus_LV_2701-334_0_6_node_157 | 0.4 | n |  | TRUE
163 | bus_LV_2701-334_0_6_node_155 | 0.4 | n |  | TRUE
164 | bus_LV_2701-334_0_6_node_153 | 0.4 | n |  | TRUE
165 | bus_LV_2701-334_0_6_node_154 | 0.4 | n |  | TRUE
166 | bus_LV_2701-334_0_6_node_156 | 0.4 | n |  | TRUE
167 | bus_LV_2701-334_0_6_node_158 | 0.4 | n |  | TRUE
168 | bus_LV_2701-334_0_6_node_169 | 0.4 | n |  | TRUE
169 | bus_LV_2701-334_0_6_node_170 | 0.4 | n |  | TRUE
170 | bus_LV_2701-334_0_6_node_171 | 0.4 | n |  | TRUE
171 | bus_LV_2701-334_0_6_node_172 | 0.4 | n |  | TRUE
172 | bus_LV_2701-334_0_6_node_174 | 0.4 | n |  | TRUE
173 | bus_LV_2701-334_0_6_node_175 | 0.4 | n |  | TRUE
174 | bus_LV_2701-334_0_6_node_185 | 0.4 | n |  | TRUE
175 | bus_LV_2701-334_0_6_node_178 | 0.4 | n |  | TRUE
176 | bus_LV_2701-334_0_6_node_184 | 0.4 | n |  | TRUE
177 | bus_MV_564_0_node_70 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2701-334_0_6_load_0 | 0 | 0.0028492 | 0.00071407 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2701-334_0_6_load_1 | 1 | 0.0026643 | 0.00066774 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2701-334_0_6_load_2 | 2 | 0.0016557 | 0.00041496 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2701-334_0_6_load_3 | 3 | 0.0016306 | 0.00040868 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2701-334_0_6_load_4 | 4 | 0.001973 | 0.00049449 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2701-334_0_6_load_31 | 5 | 0.0018852 | 0.00047246 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2701-334_0_6_load_35 | 6 | 0.0016325 | 0.00040915 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2701-334_0_6_load_32 | 7 | 0.0031719 | 0.00079494 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2701-334_0_6_load_34 | 8 | 0.0016632 | 0.00041684 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2701-334_0_6_load_5 | 9 | 0.0049178 | 0.0012325 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2701-334_0_6_load_6 | 11 | 0.019963 | 0.0050031 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2701-334_0_6_load_9 | 13 | 0.0080066 | 0.0020066 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2701-334_0_6_load_19 | 15 | 0.0050083 | 0.0012552 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2701-334_0_6_load_22 | 16 | 0.0078661 | 0.0019714 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2701-334_0_6_load_24 | 20 | 0.0018669 | 0.0004679 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2701-334_0_6_load_77 | 22 | 0.01203 | 0.0030149 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2701-334_0_6_load_17 | 23 | 0.0024496 | 0.00061393 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2701-334_0_6_load_12 | 24 | 0.0023173 | 0.00058076 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2701-334_0_6_load_33 | 27 | 0.0042243 | 0.0010587 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2701-334_0_6_load_74 | 29 | 0.0054171 | 0.0013577 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2701-334_0_6_load_160 | 32 | 0.0013573 | 0.00034016 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2701-334_0_6_load_183 | 33 | 0.0068792 | 0.0017241 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2701-334_0_6_load_117 | 34 | 0.0095699 | 0.0023984 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2701-334_0_6_load_101 | 36 | 0.0033046 | 0.0008282 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2701-334_0_6_load_97 | 38 | 0.0036627 | 0.00091796 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2701-334_0_6_load_179 | 40 | 0.010486 | 0.0026282 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2701-334_0_6_load_176 | 42 | 0.0065853 | 0.0016504 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2701-334_0_6_load_127 | 43 | 0.0016329 | 0.00040923 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2701-334_0_6_load_146 | 45 | 0.0013054 | 0.00032717 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2701-334_0_6_load_164 | 46 | 0.0013052 | 0.00032711 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2701-334_0_6_load_161 | 47 | 0.0013561 | 0.00033987 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2701-334_0_6_load_134 | 48 | 0.0059574 | 0.0014931 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2701-334_0_6_load_131 | 49 | 0.0033889 | 0.00084933 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2701-334_0_6_load_133 | 50 | 0.0078294 | 0.0019622 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2701-334_0_6_load_125 | 53 | 0.0021785 | 0.00054599 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2701-334_0_6_load_136 | 55 | 0.0073715 | 0.0018475 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2701-334_0_6_load_135 | 56 | 0.0051978 | 0.0013027 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2701-334_0_6_load_76 | 57 | 0.002317 | 0.00058069 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2701-334_0_6_load_69 | 58 | 0.0023285 | 0.00058359 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2701-334_0_6_load_18 | 59 | 0.0077832 | 0.0019507 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2701-334_0_6_load_56 | 61 | 0.002838 | 0.00071127 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2701-334_0_6_load_57 | 62 | 0.0019322 | 0.00048425 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2701-334_0_6_load_52 | 63 | 0.0018488 | 0.00046336 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2701-334_0_6_load_67 | 64 | 0.0023453 | 0.00058779 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2701-334_0_6_load_29 | 65 | 0.0016587 | 0.00041571 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2701-334_0_6_load_27 | 66 | 0.0016588 | 0.00041573 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2701-334_0_6_load_122 | 67 | 0.0017738 | 0.00044456 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2701-334_0_6_load_121 | 68 | 0.0015462 | 0.00038752 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2701-334_0_6_load_26 | 69 | 0.0016633 | 0.00041686 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2701-334_0_6_load_28 | 70 | 0.0016925 | 0.00042419 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2701-334_0_6_load_30 | 71 | 0.0016634 | 0.00041689 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2701-334_0_6_load_36 | 72 | 0.0018537 | 0.00046458 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2701-334_0_6_load_72 | 73 | 0.0038137 | 0.0009558 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2701-334_0_6_load_159 | 74 | 0.001361 | 0.00034111 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2701-334_0_6_load_173 | 75 | 0.0036881 | 0.00092433 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2701-334_0_6_load_180 | 76 | 0.0085684 | 0.0021474 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2701-334_0_6_load_181 | 77 | 0.0058622 | 0.0014692 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2701-334_0_6_load_116 | 78 | 0.0021992 | 0.00055118 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2701-334_0_6_load_107 | 79 | 0.0026495 | 0.00066403 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2701-334_0_6_load_88 | 80 | 0.0014068 | 0.00035258 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2701-334_0_6_load_86 | 81 | 0.0032685 | 0.00081917 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2701-334_0_6_load_96 | 82 | 0.0028586 | 0.00071642 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2701-334_0_6_load_187 | 83 | 0.0029716 | 0.00074475 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2701-334_0_6_load_186 | 84 | 0.0027656 | 0.00069311 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2701-334_0_6_load_108 | 85 | 0.0023577 | 0.00059088 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2701-334_0_6_load_182 | 86 | 0.0083419 | 0.0020907 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2701-334_0_6_load_177 | 87 | 0.0062556 | 0.0015678 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2701-334_0_6_load_128 | 88 | 0.0013037 | 0.00032675 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2701-334_0_6_load_167 | 89 | 0.0015464 | 0.00038756 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2701-334_0_6_load_168 | 90 | 0.0013058 | 0.00032726 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2701-334_0_6_load_145 | 91 | 0.001305 | 0.00032706 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2701-334_0_6_load_162 | 92 | 0.0013628 | 0.00034156 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2701-334_0_6_load_148 | 93 | 0.0035016 | 0.00087758 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2701-334_0_6_load_130 | 94 | 0.0040353 | 0.0010113 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2701-334_0_6_load_123 | 95 | 0.001834 | 0.00045963 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2701-334_0_6_load_53 | 96 | 0.0017045 | 0.00042718 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2701-334_0_6_load_55 | 97 | 0.0018499 | 0.00046364 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2701-334_0_6_load_89 | 98 | 0.0018397 | 0.00046107 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2701-334_0_6_load_92 | 99 | 0.0017723 | 0.00044417 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2701-334_0_6_load_83 | 100 | 0.0018396 | 0.00046105 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2701-334_0_6_load_91 | 101 | 0.0016737 | 0.00041946 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2701-334_0_6_load_105 | 102 | 0.0013537 | 0.00033927 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2701-334_0_6_load_103 | 103 | 0.0013212 | 0.00033113 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2701-334_0_6_load_59 | 104 | 0.001998 | 0.00050074 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2701-334_0_6_load_60 | 105 | 0.0018404 | 0.00046126 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2701-334_0_6_load_61 | 106 | 0.0018414 | 0.0004615 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2701-334_0_6_load_62 | 107 | 0.001829 | 0.00045838 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2701-334_0_6_load_63 | 108 | 0.002063 | 0.00051704 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2701-334_0_6_load_93 | 109 | 0.0018542 | 0.0004647 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2701-334_0_6_load_94 | 110 | 0.0021765 | 0.00054547 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2701-334_0_6_load_64 | 111 | 0.0023428 | 0.00058717 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2701-334_0_6_load_65 | 112 | 0.0021039 | 0.00052728 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2701-334_0_6_load_66 | 113 | 0.0021042 | 0.00052737 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2701-334_0_6_load_68 | 114 | 0.0021653 | 0.00054268 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2701-334_0_6_load_99 | 115 | 0.0021065 | 0.00052795 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2701-334_0_6_load_100 | 116 | 0.0021622 | 0.00054189 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2701-334_0_6_load_70 | 117 | 0.0029053 | 0.00072814 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2701-334_0_6_load_71 | 118 | 0.0028996 | 0.0007267 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2701-334_0_6_load_73 | 119 | 0.0028545 | 0.00071539 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2701-334_0_6_load_75 | 120 | 0.0028573 | 0.00071611 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2701-334_0_6_load_78 | 121 | 0.0032497 | 0.00081444 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2701-334_0_6_load_79 | 122 | 0.0021288 | 0.00053352 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2701-334_0_6_load_80 | 123 | 0.0016711 | 0.00041883 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2701-334_0_6_load_82 | 125 | 0.0028208 | 0.00070695 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2701-334_0_6_load_84 | 126 | 0.0021278 | 0.00053329 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2701-334_0_6_load_85 | 127 | 0.0013603 | 0.00034093 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2701-334_0_6_load_90 | 128 | 0.0016703 | 0.00041862 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2701-334_0_6_load_110 | 129 | 0.0013181 | 0.00033035 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2701-334_0_6_load_111 | 130 | 0.0013538 | 0.00033929 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2701-334_0_6_load_95 | 131 | 0.0021605 | 0.00054148 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2701-334_0_6_load_98 | 132 | 0.0021679 | 0.00054332 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2701-334_0_6_load_102 | 133 | 0.010461 | 0.0026218 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2701-334_0_6_load_104 | 134 | 0.0013545 | 0.00033947 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2701-334_0_6_load_106 | 135 | 0.0013186 | 0.00033047 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2701-334_0_6_load_114 | 136 | 0.0013548 | 0.00033954 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2701-334_0_6_load_115 | 137 | 0.0013222 | 0.00033137 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2701-334_0_6_load_112 | 138 | 0.0013228 | 0.00033152 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2701-334_0_6_load_113 | 139 | 0.0013551 | 0.00033962 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2701-334_0_6_load_118 | 140 | 0.0018986 | 0.00047583 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2701-334_0_6_load_119 | 141 | 0.0016161 | 0.00040502 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2701-334_0_6_load_120 | 142 | 0.0015453 | 0.00038728 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2701-334_0_6_load_124 | 143 | 0.0016411 | 0.0004113 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2701-334_0_6_load_126 | 144 | 0.0013085 | 0.00032793 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2701-334_0_6_load_142 | 145 | 0.0013054 | 0.00032716 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2701-334_0_6_load_143 | 146 | 0.001307 | 0.00032757 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2701-334_0_6_load_129 | 147 | 0.0013043 | 0.00032688 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2701-334_0_6_load_144 | 148 | 0.0013037 | 0.00032675 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2701-334_0_6_load_149 | 149 | 0.0035065 | 0.00087881 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2701-334_0_6_load_137 | 150 | 0.0013054 | 0.00032716 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2701-334_0_6_load_138 | 151 | 0.0013066 | 0.00032747 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2701-334_0_6_load_139 | 152 | 0.0013074 | 0.00032766 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2701-334_0_6_load_140 | 153 | 0.0013052 | 0.00032711 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2701-334_0_6_load_141 | 154 | 0.0013611 | 0.00034114 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2701-334_0_6_load_165 | 155 | 0.0013062 | 0.00032738 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2701-334_0_6_load_163 | 156 | 0.0013633 | 0.00034168 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2701-334_0_6_load_166 | 157 | 0.0013048 | 0.00032702 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_2701-334_0_6_load_147 | 158 | 0.0013042 | 0.00032686 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_2701-334_0_6_load_151 | 159 | 0.0013061 | 0.00032734 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_2701-334_0_6_load_152 | 160 | 0.0013045 | 0.00032693 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_2701-334_0_6_load_150 | 161 | 0.0035038 | 0.00087813 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_2701-334_0_6_load_157 | 162 | 0.0035056 | 0.0008786 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_2701-334_0_6_load_155 | 163 | 0.0013028 | 0.00032651 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_2701-334_0_6_load_153 | 164 | 0.0013065 | 0.00032745 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_2701-334_0_6_load_154 | 165 | 0.0013019 | 0.00032628 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_2701-334_0_6_load_156 | 166 | 0.0013028 | 0.00032651 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_2701-334_0_6_load_158 | 167 | 0.0013022 | 0.00032637 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_2701-334_0_6_load_169 | 168 | 0.0063253 | 0.0015853 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_2701-334_0_6_load_170 | 169 | 0.0027567 | 0.0006909 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_2701-334_0_6_load_171 | 170 | 0.0027628 | 0.00069242 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_2701-334_0_6_load_172 | 171 | 0.0040002 | 0.0010025 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_2701-334_0_6_load_174 | 172 | 0.0027533 | 0.00069004 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_2701-334_0_6_load_175 | 173 | 0.0027951 | 0.00070053 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_2701-334_0_6_load_185 | 174 | 0.0027625 | 0.00069234 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_2701-334_0_6_load_178 | 175 | 0.0037477 | 0.00093926 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_2701-334_0_6_load_184 | 176 | 0.0040108 | 0.0010052 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2701-334_0_6_line_0 |  | 0 | 1 | 0.0032885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2701-334_0_6_line_1 |  | 0 | 2 | 0.0027433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2701-334_0_6_line_2 |  | 1 | 3 | 0.00036164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2701-334_0_6_line_3 |  | 2 | 4 | 0.0041774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2701-334_0_6_line_4 |  | 3 | 5 | 0.012306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2701-334_0_6_line_5 |  | 4 | 6 | 0.002185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2701-334_0_6_line_6 |  | 5 | 7 | 0.0004352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2701-334_0_6_line_7 |  | 6 | 8 | 0.0039054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2701-334_0_6_line_8 |  | 7 | 27 | 0.010486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2701-334_0_6_line_9 |  | 8 | 72 | 0.0026299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2701-334_0_6_line_10 |  | 9 | 10 | 0.026356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2701-334_0_6_line_11 |  | 10 | 13 | 0.011095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2701-334_0_6_line_12 |  | 11 | 12 | 0.033445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2701-334_0_6_line_13 |  | 12 | 14 | 0.006791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2701-334_0_6_line_14 |  | 12 | 15 | 0.030187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2701-334_0_6_line_15 |  | 13 | 16 | 0.019149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2701-334_0_6_line_16 |  | 14 | 23 | 0.014762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2701-334_0_6_line_17 |  | 14 | 24 | 0.015848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2701-334_0_6_line_18 |  | 16 | 25 | 0.005147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2701-334_0_6_line_19 |  | 17 | 18 | 0.01539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2701-334_0_6_line_20 |  | 17 | 19 | 0.014343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2701-334_0_6_line_21 |  | 17 | 20 | 0.006535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2701-334_0_6_line_22 |  | 18 | 21 | 0.014971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2701-334_0_6_line_23 |  | 18 | 22 | 0.032426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2701-334_0_6_line_24 |  | 19 | 34 | 0.032876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2701-334_0_6_line_25 |  | 20 | 25 | 0.025357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2701-334_0_6_line_26 |  | 21 | 28 | 0.018613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2701-334_0_6_line_27 |  | 21 | 29 | 0.0038922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2701-334_0_6_line_28 |  | 22 | 57 | 0.012377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2701-334_0_6_line_29 |  | 23 | 58 | 0.0030129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2701-334_0_6_line_30 |  | 25 | 26 | 0.004549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2701-334_0_6_line_31 |  | 26 | 27 | 0.019595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2701-334_0_6_line_32 |  | 28 | 33 | 0.023696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2701-334_0_6_line_33 |  | 28 | 30 | 0.013221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_2701-334_0_6_line_34 |  | 29 | 73 | 0.010601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2701-334_0_6_line_35 |  | 30 | 31 | 0.012807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2701-334_0_6_line_36 |  | 30 | 32 | 0.0069105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2701-334_0_6_line_37 |  | 31 | 43 | 0.0044376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2701-334_0_6_line_38 |  | 32 | 74 | 0.025326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2701-334_0_6_line_39 |  | 33 | 75 | 0.019169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2701-334_0_6_line_40 |  | 34 | 78 | 0.018126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2701-334_0_6_line_41 |  | 35 | 36 | 0.012841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2701-334_0_6_line_42 |  | 35 | 37 | 0.030332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2701-334_0_6_line_43 |  | 35 | 38 | 0.014447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2701-334_0_6_line_44 |  | 36 | 79 | 0.0098514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2701-334_0_6_line_45 |  | 37 | 80 | 0.0097457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2701-334_0_6_line_46 |  | 37 | 81 | 0.0086816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2701-334_0_6_line_47 |  | 38 | 82 | 0.009566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2701-334_0_6_line_48 |  | 39 | 40 | 0.0222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2701-334_0_6_line_49 |  | 39 | 41 | 0.025472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2701-334_0_6_line_50 |  | 39 | 42 | 0.013468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2701-334_0_6_line_51 |  | 40 | 86 | 0.013801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2701-334_0_6_line_52 |  | 41 | 48 | 0.020854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2701-334_0_6_line_53 |  | 41 | 49 | 0.024592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2701-334_0_6_line_54 |  | 41 | 50 | 0.019179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2701-334_0_6_line_55 |  | 42 | 87 | 0.019632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2701-334_0_6_line_56 |  | 43 | 88 | 0.0061951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2701-334_0_6_line_57 |  | 44 | 45 | 0.017788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2701-334_0_6_line_58 |  | 44 | 46 | 0.01781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2701-334_0_6_line_59 |  | 44 | 47 | 0.011667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2701-334_0_6_line_60 |  | 45 | 91 | 0.0063839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2701-334_0_6_line_61 |  | 46 | 90 | 0.0063792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2701-334_0_6_line_62 |  | 47 | 92 | 9.4366e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2701-334_0_6_line_63 |  | 48 | 93 | 0.008678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2701-334_0_6_line_64 |  | 49 | 94 | 0.023044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2701-334_0_6_line_65 |  | 51 | 52 | 0.009093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2701-334_0_6_line_66 |  | 51 | 53 | 0.017157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2701-334_0_6_line_67 |  | 52 | 56 | 0.011607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2701-334_0_6_line_68 |  | 53 | 95 | 0.001151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2701-334_0_6_line_69 |  | 54 | 55 | 0.038874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2701-334_0_6_line_70 |  | 54 | 56 | 0.017784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2701-334_0_6_line_71 |  | 57 | 59 | 0.0073987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2701-334_0_6_line_72 |  | 58 | 64 | 0.0046293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2701-334_0_6_line_73 |  | 60 | 61 | 0.014437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2701-334_0_6_line_74 |  | 60 | 62 | 0.013651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2701-334_0_6_line_75 |  | 60 | 63 | 0.017889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2701-334_0_6_line_76 |  | 62 | 99 | 0.024637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2701-334_0_6_line_77 |  | 63 | 96 | 0.0019454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2701-334_0_6_line_78 |  | 64 | 112 | 0.0028184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2701-334_0_6_line_79 |  | 65 | 66 | 0.0063389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2701-334_0_6_line_80 |  | 66 | 69 | 0.003156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2701-334_0_6_line_81 |  | 67 | 68 | 0.0065514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2701-334_0_6_line_82 |  | 68 | 142 | 0.0063838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2701-334_0_6_line_83 |  | 69 | 70 | 0.003242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2701-334_0_6_line_84 |  | 70 | 71 | 0.0028075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2701-334_0_6_line_85 |  | 71 | 72 | 0.0034181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2701-334_0_6_line_86 |  | 73 | 117 | 0.0086545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2701-334_0_6_line_87 |  | 74 | 167 | 0.0065194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2701-334_0_6_line_88 |  | 75 | 170 | 0.012697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2701-334_0_6_line_89 |  | 76 | 77 | 0.012565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2701-334_0_6_line_90 |  | 77 | 86 | 0.011235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2701-334_0_6_line_91 |  | 78 | 140 | 0.0074194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2701-334_0_6_line_92 |  | 79 | 85 | 0.0085914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2701-334_0_6_line_93 |  | 81 | 126 | 0.010792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2701-334_0_6_line_94 |  | 82 | 120 | 0.0086486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_2701-334_0_6_line_95 |  | 83 | 84 | 0.0086059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2701-334_0_6_line_96 |  | 84 | 174 | 0.0085955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2701-334_0_6_line_97 |  | 87 | 175 | 0.0085426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2701-334_0_6_line_98 |  | 88 | 147 | 0.0063797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2701-334_0_6_line_99 |  | 89 | 90 | 0.0063811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2701-334_0_6_line_100 |  | 91 | 148 | 0.0063805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2701-334_0_6_line_101 |  | 92 | 156 | 0.027863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2701-334_0_6_line_102 |  | 93 | 149 | 0.0063781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2701-334_0_6_line_103 |  | 95 | 143 | 0.0063859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2701-334_0_6_line_104 |  | 96 | 97 | 0.0047191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2701-334_0_6_line_105 |  | 97 | 98 | 0.00077847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2701-334_0_6_line_106 |  | 98 | 100 | 0.0054981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2701-334_0_6_line_107 |  | 99 | 101 | 0.0066933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2701-334_0_6_line_108 |  | 100 | 107 | 5.7894e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2701-334_0_6_line_109 |  | 101 | 128 | 0.0064048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2701-334_0_6_line_110 |  | 102 | 103 | 0.0021084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2701-334_0_6_line_111 |  | 103 | 133 | 0.00068968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2701-334_0_6_line_112 |  | 104 | 105 | 0.0011909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2701-334_0_6_line_113 |  | 104 | 106 | 0.0043103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2701-334_0_6_line_114 |  | 105 | 107 | 0.0054404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2701-334_0_6_line_115 |  | 106 | 108 | 0.0027026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2701-334_0_6_line_116 |  | 108 | 109 | 0.0028186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2701-334_0_6_line_117 |  | 109 | 110 | 0.0046018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2701-334_0_6_line_118 |  | 110 | 131 | 0.0020282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2701-334_0_6_line_119 |  | 111 | 112 | 0.0047048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2701-334_0_6_line_120 |  | 111 | 113 | 0.0025673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2701-334_0_6_line_121 |  | 113 | 114 | 0.0050349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2701-334_0_6_line_122 |  | 114 | 115 | 0.0022366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2701-334_0_6_line_123 |  | 115 | 116 | 0.0052598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2701-334_0_6_line_124 |  | 116 | 132 | 0.0020907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2701-334_0_6_line_125 |  | 117 | 118 | 0.0087024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
126 | LV_2701-334_0_6_line_126 |  | 118 | 119 | 0.0087152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_2701-334_0_6_line_127 |  | 119 | 120 | 0.0086537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
128 | LV_2701-334_0_6_line_128 |  | 121 | 122 | 0.010745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2701-334_0_6_line_129 |  | 121 | 123 | 0.0097039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2701-334_0_6_line_130 |  | 122 | 124 | 0.0054906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2701-334_0_6_line_131 |  | 123 | 125 | 0.0045606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2701-334_0_6_line_132 |  | 124 | 126 | 0.0031482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2701-334_0_6_line_133 |  | 124 | 127 | 0.010372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2701-334_0_6_line_134 |  | 125 | 128 | 0.0018348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2701-334_0_6_line_135 |  | 127 | 129 | 0.0051271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2701-334_0_6_line_136 |  | 129 | 130 | 0.0024999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2701-334_0_6_line_137 |  | 130 | 138 | 0.0025487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2701-334_0_6_line_138 |  | 131 | 132 | 0.0054085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2701-334_0_6_line_139 |  | 133 | 134 | 0.0021534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2701-334_0_6_line_140 |  | 134 | 135 | 0.0022047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2701-334_0_6_line_141 |  | 135 | 136 | 0.0027468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2701-334_0_6_line_142 |  | 136 | 137 | 0.0023005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2701-334_0_6_line_143 |  | 137 | 139 | 0.0026498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2701-334_0_6_line_144 |  | 138 | 139 | 0.0024028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2701-334_0_6_line_145 |  | 140 | 141 | 0.0066713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2701-334_0_6_line_146 |  | 141 | 142 | 0.0064555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2701-334_0_6_line_147 |  | 143 | 144 | 9.3235e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2701-334_0_6_line_148 |  | 144 | 145 | 0.0062848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2701-334_0_6_line_149 |  | 145 | 146 | 9.6562e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2701-334_0_6_line_150 |  | 146 | 158 | 0.0062841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_2701-334_0_6_line_151 |  | 147 | 148 | 0.0063795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_2701-334_0_6_line_152 |  | 149 | 161 | 0.0063807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2701-334_0_6_line_153 |  | 150 | 151 | 0.0062869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_2701-334_0_6_line_154 |  | 150 | 152 | 9.378e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_2701-334_0_6_line_155 |  | 151 | 153 | 9.4949e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_2701-334_0_6_line_156 |  | 152 | 154 | 0.0064225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_2701-334_0_6_line_157 |  | 153 | 155 | 0.0062819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_2701-334_0_6_line_158 |  | 154 | 156 | 9.2005e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_2701-334_0_6_line_159 |  | 155 | 157 | 9.6429e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_2701-334_0_6_line_160 |  | 157 | 164 | 0.0062823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_2701-334_0_6_line_161 |  | 158 | 159 | 9.6669e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_2701-334_0_6_line_162 |  | 159 | 160 | 0.0062802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_2701-334_0_6_line_163 |  | 160 | 164 | 9.6716e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_2701-334_0_6_line_164 |  | 161 | 162 | 0.0063779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_2701-334_0_6_line_165 |  | 162 | 163 | 0.0063783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_2701-334_0_6_line_166 |  | 163 | 165 | 0.0063796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_2701-334_0_6_line_167 |  | 165 | 166 | 0.0063793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_2701-334_0_6_line_168 |  | 166 | 167 | 0.0063787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_2701-334_0_6_line_169 |  | 168 | 169 | 0.0026795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_2701-334_0_6_line_170 |  | 168 | 170 | 0.005916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_2701-334_0_6_line_171 |  | 169 | 171 | 0.010275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_2701-334_0_6_line_172 |  | 171 | 172 | 0.0098231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_2701-334_0_6_line_173 |  | 172 | 173 | 0.0086507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_2701-334_0_6_line_174 |  | 173 | 174 | 0.0086501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_2701-334_0_6_line_175 |  | 175 | 176 | 0.022608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2701-334_0_6_trafo_74 | 0.63 MVA 20/0.4 kV | 177 | 29 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2609557.7981 | 1266477.6246 | 2609558.5644 | 1266480.8226
1 | 2609557.7981 | 1266477.6246 | 2609557.1589 | 1266474.9568
2 | 2609558.6486 | 1266481.1743 | 2609558.6043 | 1266480.989 | 2609558.5644 | 1266480.8226
3 | 2609556.1854 | 1266470.8944 | 2609557.1589 | 1266474.9568
4 | 2609561.5128 | 1266493.142 | 2609558.6486 | 1266481.1743
5 | 2609556.1854 | 1266470.8944 | 2609555.6762 | 1266468.7695
6 | 2609561.6141 | 1266493.5652 | 2609561.5128 | 1266493.142
7 | 2609554.7662 | 1266464.9717 | 2609555.6762 | 1266468.7695
8 | 2609564.0547 | 1266503.7628 | 2609561.6141 | 1266493.5652
9 | 2609554.1534 | 1266462.4142 | 2609554.7662 | 1266464.9717
10 | 2609547.6919 | 1266554.178 | 2609523.411 | 1266543.9287
11 | 2609547.6919 | 1266554.178 | 2609552.8593 | 1266544.3603
12 | 2609461.2037 | 1266517.67 | 2609492.0161 | 1266530.6764
13 | 2609459.4769 | 1266524.2385 | 2609461.2037 | 1266517.67
14 | 2609461.2037 | 1266517.67 | 2609468.8738 | 1266488.4736
15 | 2609552.8593 | 1266544.3603 | 2609561.778 | 1266527.4151
16 | 2609459.4769 | 1266524.2385 | 2609455.6482 | 1266538.4951
17 | 2609459.4769 | 1266524.2385 | 2609444.7638 | 1266518.3504
18 | 2609564.1753 | 1266522.8605 | 2609561.778 | 1266527.4151
19 | 2609569.2577 | 1266568.9341 | 2609569.0576 | 1266562.2958 | 2609570.8637 | 1266557.9846 | 2609571.3369 | 1266553.9381
20 | 2609571.3369 | 1266553.9381 | 2609575.6933 | 1266550.5983 | 2609581.0753 | 1266546.115 | 2609582.6697 | 1266547.0515
21 | 2609571.3369 | 1266553.9381 | 2609569.8694 | 1266547.57
22 | 2609569.2577 | 1266568.9341 | 2609568.7036 | 1266576.4384 | 2609570.8303 | 1266578.699 | 2609570.5222 | 1266583.0348
23 | 2609569.2577 | 1266568.9341 | 2609539.2252 | 1266556.7068
24 | 2609582.6697 | 1266547.0515 | 2609599.123 | 1266518.5888
25 | 2609564.1753 | 1266522.8605 | 2609569.8694 | 1266547.57
26 | 2609570.5222 | 1266583.0348 | 2609578.8768 | 1266583.7599 | 2609584.9959 | 1266584.3257 | 2609588.863 | 1266585.6328
27 | 2609570.5222 | 1266583.0348 | 2609570.1821 | 1266586.9121
28 | 2609539.2252 | 1266556.7068 | 2609527.7622 | 1266552.0398
29 | 2609455.6482 | 1266538.4951 | 2609454.8667 | 1266541.4049
30 | 2609568.7372 | 1266522.79 | 2609564.1753 | 1266522.8605
31 | 2609568.7372 | 1266522.79 | 2609564.7882 | 1266506.8281 | 2609564.0547 | 1266503.7628
32 | 2609588.863 | 1266585.6328 | 2609586.8735 | 1266596.3371 | 2609585.7524 | 1266609.0963
33 | 2609588.863 | 1266585.6328 | 2609591.2894 | 1266579.4213 | 2609594.34 | 1266573.6222
34 | 2609569.2558 | 1266597.4727 | 2609570.1821 | 1266586.9121
35 | 2609596.5649 | 1266561.673 | 2609593.3555 | 1266567.9055 | 2609594.34 | 1266573.6222
36 | 2609594.34 | 1266573.6222 | 2609599.9079 | 1266577.7152
37 | 2609596.5649 | 1266561.673 | 2609598.8097 | 1266557.845
38 | 2609620.3138 | 1266592.7157 | 2609599.9079 | 1266577.7152
39 | 2609585.7524 | 1266609.0963 | 2609584.0746 | 1266628.1918
40 | 2609608.1941 | 1266502.8964 | 2609599.123 | 1266518.5888
41 | 2609563.3677 | 1266664.6024 | 2609562.2531 | 1266677.3953
42 | 2609563.3677 | 1266664.6024 | 2609534.0608 | 1266656.4608
43 | 2609563.3677 | 1266664.6024 | 2609564.6301 | 1266650.2106
44 | 2609562.2531 | 1266677.3953 | 2609561.3981 | 1266687.2096
45 | 2609534.0608 | 1266656.4608 | 2609533.228 | 1266666.1708
46 | 2609534.0608 | 1266656.4608 | 2609525.6955 | 1266654.1389
47 | 2609565.4659 | 1266640.6812 | 2609564.6301 | 1266650.2106
48 | 2609668.3949 | 1266644.7027 | 2609650.5724 | 1266631.4656
49 | 2609668.3949 | 1266644.7027 | 2609672.8144 | 1266639.5396 | 2609682.5061 | 1266646.5825 | 2609685.3388 | 1266640.5162
50 | 2609668.3949 | 1266644.7027 | 2609660.2511 | 1266655.4295
51 | 2609639.4932 | 1266623.2369 | 2609650.5724 | 1266631.4656
52 | 2609685.3388 | 1266640.5162 | 2609668.5363 | 1266628.1645
53 | 2609685.3388 | 1266640.5162 | 2609695.7604 | 1266618.2419
54 | 2609685.3388 | 1266640.5162 | 2609700.649 | 1266652.0679
55 | 2609660.2511 | 1266655.4295 | 2609653.1263 | 1266664.8141 | 2609651.1772 | 1266669.1584 | 2609650.2047 | 1266672.0894
56 | 2609601.9435 | 1266552.5011 | 2609598.8097 | 1266557.845
57 | 2609623.8529 | 1266515.1402 | 2609614.8549 | 1266530.484
58 | 2609623.8529 | 1266515.1402 | 2609632.7893 | 1266499.7347
59 | 2609623.8529 | 1266515.1402 | 2609633.9733 | 1266520.9456
60 | 2609614.8549 | 1266530.484 | 2609611.6255 | 1266535.9909
61 | 2609635.9902 | 1266494.2166 | 2609632.7893 | 1266499.7347
62 | 2609633.9733 | 1266520.9456 | 2609634.0552 | 1266520.9925
63 | 2609661.5442 | 1266623.0246 | 2609668.5363 | 1266628.1645
64 | 2609695.7604 | 1266618.2419 | 2609705.526 | 1266597.3695
65 | 2609718.5764 | 1266569.4764 | 2609726.4731 | 1266574.0258
66 | 2609718.5764 | 1266569.4764 | 2609703.6946 | 1266560.9397
67 | 2609726.4731 | 1266574.0258 | 2609736.5327 | 1266579.8166
68 | 2609703.6946 | 1266560.9397 | 2609702.6962 | 1266560.367
69 | 2609736.3123 | 1266624.2992 | 2609751.9454 | 1266588.6889
70 | 2609751.9454 | 1266588.6889 | 2609736.5327 | 1266579.8166
71 | 2609520.9097 | 1266549.2499 | 2609527.7622 | 1266552.0398
72 | 2609453.666 | 1266545.8757 | 2609454.8667 | 1266541.4049
73 | 2609431.8525 | 1266627.0997 | 2609418.0104 | 1266622.9987
74 | 2609431.8525 | 1266627.0997 | 2609444.9634 | 1266630.9005
75 | 2609431.8525 | 1266627.0997 | 2609436.4924 | 1266609.8226
76 | 2609468.6265 | 1266637.7604 | 2609444.9634 | 1266630.9005
77 | 2609436.4924 | 1266609.8226 | 2609436.997 | 1266607.9438
78 | 2609453.666 | 1266545.8757 | 2609452.935 | 1266548.5977
79 | 2609551.2118 | 1266450.1382 | 2609549.7346 | 1266443.9738
80 | 2609551.9472 | 1266453.2073 | 2609551.2118 | 1266450.1382
81 | 2609621.6716 | 1266479.5816 | 2609624.9503 | 1266473.9097
82 | 2609618.4767 | 1266485.1085 | 2609621.6716 | 1266479.5816
83 | 2609551.9472 | 1266453.2073 | 2609552.7026 | 1266456.36
84 | 2609552.7026 | 1266456.36 | 2609553.3569 | 1266459.0902
85 | 2609554.1534 | 1266462.4142 | 2609553.3569 | 1266459.0902
86 | 2609568.4996 | 1266606.0941 | 2609569.2558 | 1266597.4727
87 | 2609620.3138 | 1266592.7157 | 2609625.5666 | 1266596.5771
88 | 2609584.0746 | 1266628.1918 | 2609582.9633 | 1266640.8399
89 | 2609620.3863 | 1266609.0458 | 2609630.4737 | 1266616.5378
90 | 2609630.4737 | 1266616.5378 | 2609639.4932 | 1266623.2369
91 | 2609608.1941 | 1266502.8964 | 2609611.9072 | 1266496.4731
92 | 2609561.3981 | 1266687.2096 | 2609560.6523 | 1266695.7686
93 | 2609525.6955 | 1266654.1389 | 2609515.2966 | 1266651.2526
94 | 2609565.4659 | 1266640.6812 | 2609566.2216 | 1266632.0657
95 | 2609578.1851 | 1266695.2208 | 2609577.4319 | 1266703.7936
96 | 2609578.1851 | 1266695.2208 | 2609578.9375 | 1266686.6583
97 | 2609647.5145 | 1266680.1973 | 2609650.2047 | 1266672.0894
98 | 2609601.9435 | 1266552.5011 | 2609605.1707 | 1266546.9978
99 | 2609639.1921 | 1266488.697 | 2609635.9902 | 1266494.2166
100 | 2609611.6255 | 1266535.9909 | 2609608.3979 | 1266541.4948
101 | 2609634.0552 | 1266520.9925 | 2609658.2244 | 1266534.8567
102 | 2609661.5442 | 1266623.0246 | 2609656.4052 | 1266619.2469
103 | 2609697.1569 | 1266557.1896 | 2609702.6962 | 1266560.367
104 | 2609436.997 | 1266607.9438 | 2609438.221 | 1266603.3862
105 | 2609438.221 | 1266603.3862 | 2609438.4229 | 1266602.6344
106 | 2609439.8489 | 1266597.3245 | 2609438.4229 | 1266602.6344
107 | 2609475.0551 | 1266639.6241 | 2609468.6265 | 1266637.7604
108 | 2609439.8489 | 1266597.3245 | 2609439.864 | 1266597.2686
109 | 2609481.2066 | 1266641.4074 | 2609475.0551 | 1266639.6241
110 | 2609506.1891 | 1266685.5856 | 2609505.8303 | 1266687.6633
111 | 2609506.3064 | 1266684.906 | 2609506.1891 | 1266685.5856
112 | 2609441.5839 | 1266590.8642 | 2609441.275 | 1266592.0143
113 | 2609441.5839 | 1266590.8642 | 2609442.7019 | 1266586.7014
114 | 2609441.275 | 1266592.0143 | 2609439.864 | 1266597.2686
115 | 2609442.7019 | 1266586.7014 | 2609443.4029 | 1266584.0912
116 | 2609444.1339 | 1266581.3691 | 2609443.4029 | 1266584.0912
117 | 2609444.1339 | 1266581.3691 | 2609445.3275 | 1266576.9248
118 | 2609445.3275 | 1266576.9248 | 2609445.8535 | 1266574.966
119 | 2609451.7147 | 1266553.1415 | 2609452.935 | 1266548.5977
120 | 2609451.7147 | 1266553.1415 | 2609451.0488 | 1266555.621
121 | 2609451.0488 | 1266555.621 | 2609449.743 | 1266560.4835
122 | 2609449.1628 | 1266562.6436 | 2609449.743 | 1266560.4835
123 | 2609449.1628 | 1266562.6436 | 2609447.7986 | 1266567.7234
124 | 2609447.2563 | 1266569.7425 | 2609447.7986 | 1266567.7234
125 | 2609568.4996 | 1266606.0941 | 2609567.7392 | 1266614.7633
126 | 2609567.7392 | 1266614.7633 | 2609566.9777 | 1266623.4451
127 | 2609566.9777 | 1266623.4451 | 2609566.2216 | 1266632.0657
128 | 2609496.6693 | 1266645.89 | 2609506.9896 | 1266648.8818
129 | 2609496.6693 | 1266645.89 | 2609487.3491 | 1266643.1881
130 | 2609512.2631 | 1266650.4106 | 2609506.9896 | 1266648.8818
131 | 2609487.3491 | 1266643.1881 | 2609482.9689 | 1266641.9183
132 | 2609512.2631 | 1266650.4106 | 2609515.2966 | 1266651.2526
133 | 2609512.2631 | 1266650.4106 | 2609510.4981 | 1266660.6315
134 | 2609481.2066 | 1266641.4074 | 2609482.9689 | 1266641.9183
135 | 2609509.6257 | 1266665.6838 | 2609510.4981 | 1266660.6315
136 | 2609509.6257 | 1266665.6838 | 2609509.2003 | 1266668.1472
137 | 2609509.2003 | 1266668.1472 | 2609508.7666 | 1266670.6588
138 | 2609445.8535 | 1266574.966 | 2609447.2563 | 1266569.7425
139 | 2609506.3064 | 1266684.906 | 2609506.6728 | 1266682.784
140 | 2609506.6728 | 1266682.784 | 2609507.048 | 1266680.6115
141 | 2609507.5154 | 1266677.9047 | 2609507.048 | 1266680.6115
142 | 2609507.5154 | 1266677.9047 | 2609507.9068 | 1266675.6377
143 | 2609507.9068 | 1266675.6377 | 2609508.3577 | 1266673.0266
144 | 2609508.3577 | 1266673.0266 | 2609508.7666 | 1266670.6588
145 | 2609611.9072 | 1266496.4731 | 2609615.246 | 1266490.6974
146 | 2609618.4767 | 1266485.1085 | 2609615.246 | 1266490.6974
147 | 2609697.0761 | 1266557.1432 | 2609697.1569 | 1266557.1896
148 | 2609691.6245 | 1266554.016 | 2609697.0761 | 1266557.1432
149 | 2609691.5407 | 1266553.9679 | 2609691.6245 | 1266554.016
150 | 2609686.0898 | 1266550.8411 | 2609691.5407 | 1266553.9679
151 | 2609605.1707 | 1266546.9978 | 2609608.3979 | 1266541.4948
152 | 2609651.2642 | 1266615.4676 | 2609656.4052 | 1266619.2469
153 | 2609669.41 | 1266541.2731 | 2609663.9566 | 1266538.1448
154 | 2609663.8752 | 1266538.0982 | 2609663.9566 | 1266538.1448
155 | 2609669.41 | 1266541.2731 | 2609669.4923 | 1266541.3203
156 | 2609663.8752 | 1266538.0982 | 2609658.3042 | 1266534.9025
157 | 2609669.4923 | 1266541.3203 | 2609674.9414 | 1266544.4461
158 | 2609658.2244 | 1266534.8567 | 2609658.3042 | 1266534.9025
159 | 2609674.9414 | 1266544.4461 | 2609675.025 | 1266544.494
160 | 2609680.4745 | 1266547.62 | 2609675.025 | 1266544.494
161 | 2609686.0059 | 1266550.793 | 2609686.0898 | 1266550.8411
162 | 2609686.0059 | 1266550.793 | 2609680.5584 | 1266547.6681
163 | 2609680.4745 | 1266547.62 | 2609680.5584 | 1266547.6681
164 | 2609646.1254 | 1266611.6901 | 2609651.2642 | 1266615.4676
165 | 2609646.1254 | 1266611.6901 | 2609640.9862 | 1266607.9122
166 | 2609635.8461 | 1266604.1337 | 2609640.9862 | 1266607.9122
167 | 2609635.8461 | 1266604.1337 | 2609630.7061 | 1266600.3552
168 | 2609625.5666 | 1266596.5771 | 2609630.7061 | 1266600.3552
169 | 2609582.4455 | 1266646.7332 | 2609582.2109 | 1266649.4024
170 | 2609582.4455 | 1266646.7332 | 2609582.9633 | 1266640.8399
171 | 2609581.3115 | 1266659.6385 | 2609582.2109 | 1266649.4024
172 | 2609581.3115 | 1266659.6385 | 2609580.4518 | 1266669.4238
173 | 2609580.4518 | 1266669.4238 | 2609579.6946 | 1266678.0413
174 | 2609579.6946 | 1266678.0413 | 2609578.9375 | 1266686.6583
175 | 2609637.3972 | 1266699.813 | 2609642.8183 | 1266694.3513 | 2609647.5145 | 1266680.1973

## bus_geodata
| x | y | coords
0 | 2609557.7981 | 1266477.6246
1 | 2609558.5644 | 1266480.8226
2 | 2609557.1589 | 1266474.9568
3 | 2609558.6486 | 1266481.1743
4 | 2609556.1854 | 1266470.8944
5 | 2609561.5128 | 1266493.142
6 | 2609555.6762 | 1266468.7695
7 | 2609561.6141 | 1266493.5652
8 | 2609554.7662 | 1266464.9717
9 | 2609523.411 | 1266543.9287
10 | 2609547.6919 | 1266554.178
11 | 2609492.0161 | 1266530.6764
12 | 2609461.2037 | 1266517.67
13 | 2609552.8593 | 1266544.3603
14 | 2609459.4769 | 1266524.2385
15 | 2609468.8738 | 1266488.4736
16 | 2609561.778 | 1266527.4151
17 | 2609571.3369 | 1266553.9381
18 | 2609569.2577 | 1266568.9341
19 | 2609582.6697 | 1266547.0515
20 | 2609569.8694 | 1266547.57
21 | 2609570.5222 | 1266583.0348
22 | 2609539.2252 | 1266556.7068
23 | 2609455.6482 | 1266538.4951
24 | 2609444.7638 | 1266518.3504
25 | 2609564.1753 | 1266522.8605
26 | 2609568.7372 | 1266522.79
27 | 2609564.0547 | 1266503.7628
28 | 2609588.863 | 1266585.6328
29 | 2609570.1821 | 1266586.9121
30 | 2609594.34 | 1266573.6222
31 | 2609596.5649 | 1266561.673
32 | 2609599.9079 | 1266577.7152
33 | 2609585.7524 | 1266609.0963
34 | 2609599.123 | 1266518.5888
35 | 2609563.3677 | 1266664.6024
36 | 2609562.2531 | 1266677.3953
37 | 2609534.0608 | 1266656.4608
38 | 2609564.6301 | 1266650.2106
39 | 2609668.3949 | 1266644.7027
40 | 2609650.5724 | 1266631.4656
41 | 2609685.3388 | 1266640.5162
42 | 2609660.2511 | 1266655.4295
43 | 2609598.8097 | 1266557.845
44 | 2609623.8529 | 1266515.1402
45 | 2609614.8549 | 1266530.484
46 | 2609632.7893 | 1266499.7347
47 | 2609633.9733 | 1266520.9456
48 | 2609668.5363 | 1266628.1645
49 | 2609695.7604 | 1266618.2419
50 | 2609700.649 | 1266652.0679
51 | 2609718.5764 | 1266569.4764
52 | 2609726.4731 | 1266574.0258
53 | 2609703.6946 | 1266560.9397
54 | 2609751.9454 | 1266588.6889
55 | 2609736.3123 | 1266624.2992
56 | 2609736.5327 | 1266579.8166
57 | 2609527.7622 | 1266552.0398
58 | 2609454.8667 | 1266541.4049
59 | 2609520.9097 | 1266549.2499
60 | 2609431.8525 | 1266627.0997
61 | 2609418.0104 | 1266622.9987
62 | 2609444.9634 | 1266630.9005
63 | 2609436.4924 | 1266609.8226
64 | 2609453.666 | 1266545.8757
65 | 2609549.7346 | 1266443.9738
66 | 2609551.2118 | 1266450.1382
67 | 2609624.9503 | 1266473.9097
68 | 2609621.6716 | 1266479.5816
69 | 2609551.9472 | 1266453.2073
70 | 2609552.7026 | 1266456.36
71 | 2609553.3569 | 1266459.0902
72 | 2609554.1534 | 1266462.4142
73 | 2609569.2558 | 1266597.4727
74 | 2609620.3138 | 1266592.7157
75 | 2609584.0746 | 1266628.1918
76 | 2609620.3863 | 1266609.0458
77 | 2609630.4737 | 1266616.5378
78 | 2609608.1941 | 1266502.8964
79 | 2609561.3981 | 1266687.2096
80 | 2609533.228 | 1266666.1708
81 | 2609525.6955 | 1266654.1389
82 | 2609565.4659 | 1266640.6812
83 | 2609577.4319 | 1266703.7936
84 | 2609578.1851 | 1266695.2208
85 | 2609560.6523 | 1266695.7686
86 | 2609639.4932 | 1266623.2369
87 | 2609650.2047 | 1266672.0894
88 | 2609601.9435 | 1266552.5011
89 | 2609639.1921 | 1266488.697
90 | 2609635.9902 | 1266494.2166
91 | 2609611.6255 | 1266535.9909
92 | 2609634.0552 | 1266520.9925
93 | 2609661.5442 | 1266623.0246
94 | 2609705.526 | 1266597.3695
95 | 2609702.6962 | 1266560.367
96 | 2609436.997 | 1266607.9438
97 | 2609438.221 | 1266603.3862
98 | 2609438.4229 | 1266602.6344
99 | 2609468.6265 | 1266637.7604
100 | 2609439.8489 | 1266597.3245
101 | 2609475.0551 | 1266639.6241
102 | 2609505.8303 | 1266687.6633
103 | 2609506.1891 | 1266685.5856
104 | 2609441.5839 | 1266590.8642
105 | 2609441.275 | 1266592.0143
106 | 2609442.7019 | 1266586.7014
107 | 2609439.864 | 1266597.2686
108 | 2609443.4029 | 1266584.0912
109 | 2609444.1339 | 1266581.3691
110 | 2609445.3275 | 1266576.9248
111 | 2609451.7147 | 1266553.1415
112 | 2609452.935 | 1266548.5977
113 | 2609451.0488 | 1266555.621
114 | 2609449.743 | 1266560.4835
115 | 2609449.1628 | 1266562.6436
116 | 2609447.7986 | 1266567.7234
117 | 2609568.4996 | 1266606.0941
118 | 2609567.7392 | 1266614.7633
119 | 2609566.9777 | 1266623.4451
120 | 2609566.2216 | 1266632.0657
121 | 2609496.6693 | 1266645.89
122 | 2609506.9896 | 1266648.8818
123 | 2609487.3491 | 1266643.1881
124 | 2609512.263 | 1266650.4106
125 | 2609482.9689 | 1266641.9183
126 | 2609515.2966 | 1266651.2526
127 | 2609510.4981 | 1266660.6315
128 | 2609481.2066 | 1266641.4074
129 | 2609509.6257 | 1266665.6838
130 | 2609509.2003 | 1266668.1472
131 | 2609445.8535 | 1266574.966
132 | 2609447.2563 | 1266569.7425
133 | 2609506.3064 | 1266684.906
134 | 2609506.6728 | 1266682.784
135 | 2609507.048 | 1266680.6115
136 | 2609507.5154 | 1266677.9047
137 | 2609507.9068 | 1266675.6377
138 | 2609508.7666 | 1266670.6588
139 | 2609508.3577 | 1266673.0266
140 | 2609611.9072 | 1266496.4731
141 | 2609615.246 | 1266490.6974
142 | 2609618.4767 | 1266485.1085
143 | 2609697.1569 | 1266557.1896
144 | 2609697.0761 | 1266557.1432
145 | 2609691.6245 | 1266554.016
146 | 2609691.5407 | 1266553.9679
147 | 2609605.1707 | 1266546.9978
148 | 2609608.3979 | 1266541.4948
149 | 2609656.4052 | 1266619.2469
150 | 2609663.9566 | 1266538.1448
151 | 2609669.41 | 1266541.2731
152 | 2609663.8752 | 1266538.0982
153 | 2609669.4923 | 1266541.3203
154 | 2609658.3042 | 1266534.9025
155 | 2609674.9414 | 1266544.4461
156 | 2609658.2244 | 1266534.8567
157 | 2609675.025 | 1266544.494
158 | 2609686.0898 | 1266550.8411
159 | 2609686.0059 | 1266550.793
160 | 2609680.5584 | 1266547.6681
161 | 2609651.2642 | 1266615.4676
162 | 2609646.1254 | 1266611.6901
163 | 2609640.9862 | 1266607.9122
164 | 2609680.4745 | 1266547.62
165 | 2609635.8461 | 1266604.1337
166 | 2609630.7061 | 1266600.3552
167 | 2609625.5666 | 1266596.5771
168 | 2609582.4455 | 1266646.7332
169 | 2609582.2109 | 1266649.4024
170 | 2609582.9633 | 1266640.8399
171 | 2609581.3115 | 1266659.6385
172 | 2609580.4518 | 1266669.4238
173 | 2609579.6946 | 1266678.0413
174 | 2609578.9375 | 1266686.6583
175 | 2609647.5146 | 1266680.1973
176 | 2609637.3972 | 1266699.813
177 | 2609570.5222 | 1266583.0348

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1