## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2702-2_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2702-2_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2702-2_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2702-2_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2702-2_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2702-2_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2702-2_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2702-2_0_2_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2702-2_0_2_node_52 | 0.4 | n |  | TRUE
9 | bus_LV_2702-2_0_2_node_53 | 0.4 | n |  | TRUE
10 | bus_LV_2702-2_0_2_node_201 | 0.4 | n |  | TRUE
11 | bus_LV_2702-2_0_2_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_2702-2_0_2_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_2702-2_0_2_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_2702-2_0_2_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_2702-2_0_2_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_2702-2_0_2_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_2702-2_0_2_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_2702-2_0_2_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_2702-2_0_2_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_2702-2_0_2_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_2702-2_0_2_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_2702-2_0_2_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_2702-2_0_2_node_165 | 0.4 | n |  | TRUE
24 | bus_LV_2702-2_0_2_node_150 | 0.4 | n |  | TRUE
25 | bus_LV_2702-2_0_2_node_111 | 0.4 | n |  | TRUE
26 | bus_LV_2702-2_0_2_node_142 | 0.4 | n |  | TRUE
27 | bus_LV_2702-2_0_2_node_81 | 0.4 | n |  | TRUE
28 | bus_LV_2702-2_0_2_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_2702-2_0_2_node_48 | 0.4 | n |  | TRUE
30 | bus_LV_2702-2_0_2_node_49 | 0.4 | n |  | TRUE
31 | bus_LV_2702-2_0_2_node_239 | 0.4 | n |  | TRUE
32 | bus_LV_2702-2_0_2_node_236 | 0.4 | n |  | TRUE
33 | bus_LV_2702-2_0_2_node_271 | 0.4 | n |  | TRUE
34 | bus_LV_2702-2_0_2_node_220 | 0.4 | n |  | TRUE
35 | bus_LV_2702-2_0_2_node_68 | 0.4 | n |  | TRUE
36 | bus_LV_2702-2_0_2_node_64 | 0.4 | n |  | TRUE
37 | bus_LV_2702-2_0_2_node_65 | 0.4 | n |  | TRUE
38 | bus_LV_2702-2_0_2_node_66 | 0.4 | n |  | TRUE
39 | bus_LV_2702-2_0_2_node_67 | 0.4 | n |  | TRUE
40 | bus_LV_2702-2_0_2_node_69 | 0.4 | n |  | TRUE
41 | bus_LV_2702-2_0_2_node_70 | 0.4 | n |  | TRUE
42 | bus_LV_2702-2_0_2_node_72 | 0.4 | n |  | TRUE
43 | bus_LV_2702-2_0_2_node_134 | 0.4 | n |  | TRUE
44 | bus_LV_2702-2_0_2_node_82 | 0.4 | n |  | TRUE
45 | bus_LV_2702-2_0_2_node_83 | 0.4 | n |  | TRUE
46 | bus_LV_2702-2_0_2_node_84 | 0.4 | n |  | TRUE
47 | bus_LV_2702-2_0_2_node_117 | 0.4 | n |  | TRUE
48 | bus_LV_2702-2_0_2_node_85 | 0.4 | n |  | TRUE
49 | bus_LV_2702-2_0_2_node_86 | 0.4 | n |  | TRUE
50 | bus_LV_2702-2_0_2_node_87 | 0.4 | n |  | TRUE
51 | bus_LV_2702-2_0_2_node_88 | 0.4 | n |  | TRUE
52 | bus_LV_2702-2_0_2_node_89 | 0.4 | n |  | TRUE
53 | bus_LV_2702-2_0_2_node_90 | 0.4 | n |  | TRUE
54 | bus_LV_2702-2_0_2_node_91 | 0.4 | n |  | TRUE
55 | bus_LV_2702-2_0_2_node_138 | 0.4 | n |  | TRUE
56 | bus_LV_2702-2_0_2_node_92 | 0.4 | n |  | TRUE
57 | bus_LV_2702-2_0_2_node_93 | 0.4 | n |  | TRUE
58 | bus_LV_2702-2_0_2_node_94 | 0.4 | n |  | TRUE
59 | bus_LV_2702-2_0_2_node_95 | 0.4 | n |  | TRUE
60 | bus_LV_2702-2_0_2_node_112 | 0.4 | n |  | TRUE
61 | bus_LV_2702-2_0_2_node_110 | 0.4 | n |  | TRUE
62 | bus_LV_2702-2_0_2_node_113 | 0.4 | n |  | TRUE
63 | bus_LV_2702-2_0_2_node_114 | 0.4 | n |  | TRUE
64 | bus_LV_2702-2_0_2_node_115 | 0.4 | n |  | TRUE
65 | bus_LV_2702-2_0_2_node_116 | 0.4 | n |  | TRUE
66 | bus_LV_2702-2_0_2_node_200 | 0.4 | n |  | TRUE
67 | bus_LV_2702-2_0_2_node_256 | 0.4 | n |  | TRUE
68 | bus_LV_2702-2_0_2_node_254 | 0.4 | n |  | TRUE
69 | bus_LV_2702-2_0_2_node_135 | 0.4 | n |  | TRUE
70 | bus_LV_2702-2_0_2_node_136 | 0.4 | n |  | TRUE
71 | bus_LV_2702-2_0_2_node_137 | 0.4 | n |  | TRUE
72 | bus_LV_2702-2_0_2_node_139 | 0.4 | n |  | TRUE
73 | bus_LV_2702-2_0_2_node_140 | 0.4 | n |  | TRUE
74 | bus_LV_2702-2_0_2_node_141 | 0.4 | n |  | TRUE
75 | bus_LV_2702-2_0_2_node_143 | 0.4 | n |  | TRUE
76 | bus_LV_2702-2_0_2_node_144 | 0.4 | n |  | TRUE
77 | bus_LV_2702-2_0_2_node_145 | 0.4 | n |  | TRUE
78 | bus_LV_2702-2_0_2_node_146 | 0.4 | n |  | TRUE
79 | bus_LV_2702-2_0_2_node_149 | 0.4 | n |  | TRUE
80 | bus_LV_2702-2_0_2_node_147 | 0.4 | n |  | TRUE
81 | bus_LV_2702-2_0_2_node_148 | 0.4 | n |  | TRUE
82 | bus_LV_2702-2_0_2_node_151 | 0.4 | n |  | TRUE
83 | bus_LV_2702-2_0_2_node_152 | 0.4 | n |  | TRUE
84 | bus_LV_2702-2_0_2_node_237 | 0.4 | n |  | TRUE
85 | bus_LV_2702-2_0_2_node_161 | 0.4 | n |  | TRUE
86 | bus_LV_2702-2_0_2_node_162 | 0.4 | n |  | TRUE
87 | bus_LV_2702-2_0_2_node_163 | 0.4 | n |  | TRUE
88 | bus_LV_2702-2_0_2_node_164 | 0.4 | n |  | TRUE
89 | bus_LV_2702-2_0_2_node_166 | 0.4 | n |  | TRUE
90 | bus_LV_2702-2_0_2_node_221 | 0.4 | n |  | TRUE
91 | bus_LV_2702-2_0_2_node_177 | 0.4 | n |  | TRUE
92 | bus_LV_2702-2_0_2_node_178 | 0.4 | n |  | TRUE
93 | bus_LV_2702-2_0_2_node_179 | 0.4 | n |  | TRUE
94 | bus_LV_2702-2_0_2_node_180 | 0.4 | n |  | TRUE
95 | bus_LV_2702-2_0_2_node_233 | 0.4 | n |  | TRUE
96 | bus_LV_2702-2_0_2_node_181 | 0.4 | n |  | TRUE
97 | bus_LV_2702-2_0_2_node_182 | 0.4 | n |  | TRUE
98 | bus_LV_2702-2_0_2_node_184 | 0.4 | n |  | TRUE
99 | bus_LV_2702-2_0_2_node_186 | 0.4 | n |  | TRUE
100 | bus_LV_2702-2_0_2_node_187 | 0.4 | n |  | TRUE
101 | bus_LV_2702-2_0_2_node_199 | 0.4 | n |  | TRUE
102 | bus_LV_2702-2_0_2_node_222 | 0.4 | n |  | TRUE
103 | bus_LV_2702-2_0_2_node_223 | 0.4 | n |  | TRUE
104 | bus_LV_2702-2_0_2_node_224 | 0.4 | n |  | TRUE
105 | bus_LV_2702-2_0_2_node_281 | 0.4 | n |  | TRUE
106 | bus_LV_2702-2_0_2_node_232 | 0.4 | n |  | TRUE
107 | bus_LV_2702-2_0_2_node_225 | 0.4 | n |  | TRUE
108 | bus_LV_2702-2_0_2_node_234 | 0.4 | n |  | TRUE
109 | bus_LV_2702-2_0_2_node_235 | 0.4 | n |  | TRUE
110 | bus_LV_2702-2_0_2_node_284 | 0.4 | n |  | TRUE
111 | bus_LV_2702-2_0_2_node_244 | 0.4 | n |  | TRUE
112 | bus_LV_2702-2_0_2_node_251 | 0.4 | n |  | TRUE
113 | bus_LV_2702-2_0_2_node_253 | 0.4 | n |  | TRUE
114 | bus_LV_2702-2_0_2_node_272 | 0.4 | n |  | TRUE
115 | bus_LV_2702-2_0_2_node_285 | 0.4 | n |  | TRUE
116 | bus_MV_347_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2702-2_0_2_load_0 | 0 | 0.0019596 | 0.00049113 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2702-2_0_2_load_1 | 1 | 0.001891 | 0.00047393 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2702-2_0_2_load_2 | 2 | 0.0016482 | 0.00041308 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2702-2_0_2_load_4 | 4 | 0.00089793 | 0.00022504 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2702-2_0_2_load_6 | 6 | 0.0032903 | 0.00082463 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2702-2_0_2_load_7 | 7 | 0.001632 | 0.00040903 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2702-2_0_2_load_52 | 8 | 0.0042402 | 0.0010627 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2702-2_0_2_load_53 | 9 | 0.004808 | 0.001205 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2702-2_0_2_load_201 | 10 | 0.00089896 | 0.0002253 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2702-2_0_2_load_16 | 11 | 0.0012404 | 0.00031088 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2702-2_0_2_load_17 | 12 | 0.00080589 | 0.00020197 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2702-2_0_2_load_20 | 15 | 0.001259 | 0.00031554 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2702-2_0_2_load_21 | 16 | 0.0014955 | 0.0003748 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2702-2_0_2_load_22 | 17 | 0.0021125 | 0.00052944 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2702-2_0_2_load_23 | 18 | 0.0011392 | 0.00028551 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2702-2_0_2_load_24 | 19 | 0.0021554 | 0.00054019 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2702-2_0_2_load_25 | 20 | 0.0021026 | 0.00052695 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2702-2_0_2_load_26 | 21 | 0.0014175 | 0.00035526 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2702-2_0_2_load_27 | 22 | 0.001698 | 0.00042557 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2702-2_0_2_load_165 | 23 | 0.00077118 | 0.00019328 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2702-2_0_2_load_150 | 24 | 0.00083086 | 0.00020823 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2702-2_0_2_load_142 | 26 | 0.0014069 | 0.0003526 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2702-2_0_2_load_81 | 27 | 0.0010227 | 0.00025632 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2702-2_0_2_load_49 | 30 | 0.0015857 | 0.00039742 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2702-2_0_2_load_239 | 31 | 0.0061531 | 0.0015421 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2702-2_0_2_load_236 | 32 | 0.0011886 | 0.00029789 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2702-2_0_2_load_271 | 33 | 0.0014704 | 0.00036852 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2702-2_0_2_load_220 | 34 | 0.0020106 | 0.00050391 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2702-2_0_2_load_68 | 35 | 0.002531 | 0.00063434 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2702-2_0_2_load_64 | 36 | 0.0026093 | 0.00065395 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2702-2_0_2_load_65 | 37 | 0.0017924 | 0.00044922 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2702-2_0_2_load_67 | 39 | 0.0018819 | 0.00047166 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2702-2_0_2_load_69 | 40 | 0.002306 | 0.00057794 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2702-2_0_2_load_70 | 41 | 0.0015009 | 0.00037616 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2702-2_0_2_load_72 | 42 | 0.0014911 | 0.00037369 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2702-2_0_2_load_134 | 43 | 0.0021004 | 0.00052642 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2702-2_0_2_load_82 | 44 | 0.0017172 | 0.00043037 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2702-2_0_2_load_83 | 45 | 0.00059673 | 0.00014955 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2702-2_0_2_load_84 | 46 | 0.0012624 | 0.00031638 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2702-2_0_2_load_117 | 47 | 0.00058195 | 0.00014585 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2702-2_0_2_load_85 | 48 | 0.0017161 | 0.0004301 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2702-2_0_2_load_86 | 49 | 0.0015859 | 0.00039746 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2702-2_0_2_load_87 | 50 | 0.0019469 | 0.00048793 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2702-2_0_2_load_88 | 51 | 0.0017769 | 0.00044533 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2702-2_0_2_load_89 | 52 | 0.0016185 | 0.00040564 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2702-2_0_2_load_90 | 53 | 0.0018374 | 0.0004605 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2702-2_0_2_load_91 | 54 | 0.0013254 | 0.00033216 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2702-2_0_2_load_138 | 55 | 0.0014933 | 0.00037427 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2702-2_0_2_load_92 | 56 | 0.0019064 | 0.00047779 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2702-2_0_2_load_93 | 57 | 0.0014989 | 0.00037565 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2702-2_0_2_load_94 | 58 | 0.001244 | 0.00031177 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2702-2_0_2_load_95 | 59 | 0.0013686 | 0.000343 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2702-2_0_2_load_110 | 61 | 0.0030096 | 0.00075429 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2702-2_0_2_load_113 | 62 | 0.0031767 | 0.00079614 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2702-2_0_2_load_114 | 63 | 0.0016768 | 0.00042026 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2702-2_0_2_load_115 | 64 | 0.0017845 | 0.00044724 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2702-2_0_2_load_116 | 65 | 0.003132 | 0.00078495 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2702-2_0_2_load_200 | 66 | 0.0023319 | 0.00058442 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2702-2_0_2_load_256 | 67 | 0.0018988 | 0.0004759 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2702-2_0_2_load_254 | 68 | 0.00036097 | 9.0468e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2702-2_0_2_load_135 | 69 | 0.0014913 | 0.00037374 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2702-2_0_2_load_136 | 70 | 0.0025834 | 0.00064746 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2702-2_0_2_load_137 | 71 | 0.0025094 | 0.00062891 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2702-2_0_2_load_139 | 72 | 0.0012115 | 0.00030362 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2702-2_0_2_load_140 | 73 | 0.0014954 | 0.00037479 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2702-2_0_2_load_141 | 74 | 0.0012741 | 0.00031931 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2702-2_0_2_load_143 | 75 | 0.0014966 | 0.0003751 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2702-2_0_2_load_145 | 77 | 0.00084021 | 0.00021058 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2702-2_0_2_load_146 | 78 | 0.0022827 | 0.00057209 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2702-2_0_2_load_147 | 80 | 0.0016149 | 0.00040474 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2702-2_0_2_load_148 | 81 | 0.0018043 | 0.0004522 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2702-2_0_2_load_152 | 83 | 0.0022135 | 0.00055476 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2702-2_0_2_load_237 | 84 | 0.0023572 | 0.00059078 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2702-2_0_2_load_161 | 85 | 0.0009002 | 0.00022561 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2702-2_0_2_load_162 | 86 | 0.0017636 | 0.00044199 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2702-2_0_2_load_163 | 87 | 0.0012874 | 0.00032264 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2702-2_0_2_load_164 | 88 | 0.0018597 | 0.00046609 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2702-2_0_2_load_166 | 89 | 0.0011565 | 0.00028986 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2702-2_0_2_load_221 | 90 | 0.0014884 | 0.00037303 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2702-2_0_2_load_177 | 91 | 0.0015693 | 0.0003933 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2702-2_0_2_load_178 | 92 | 0.0042649 | 0.0010689 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2702-2_0_2_load_179 | 93 | 0.001487 | 0.00037268 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2702-2_0_2_load_180 | 94 | 0.0016955 | 0.00042494 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2702-2_0_2_load_181 | 96 | 0.0010732 | 0.00026897 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2702-2_0_2_load_182 | 97 | 0.001051 | 0.00026342 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2702-2_0_2_load_184 | 98 | 0.0015852 | 0.0003973 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2702-2_0_2_load_186 | 99 | 0.0015939 | 0.00039946 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2702-2_0_2_load_187 | 100 | 0.0021328 | 0.00053453 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2702-2_0_2_load_199 | 101 | 0.0017195 | 0.00043095 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2702-2_0_2_load_223 | 103 | 0.0013742 | 0.00034442 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2702-2_0_2_load_281 | 105 | 0.0015995 | 0.00040088 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2702-2_0_2_load_232 | 106 | 0.0033608 | 0.00084231 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2702-2_0_2_load_234 | 108 | 0.0033566 | 0.00084124 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2702-2_0_2_load_235 | 109 | 0.0011437 | 0.00028664 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2702-2_0_2_load_244 | 111 | 0.0013811 | 0.00034614 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2702-2_0_2_load_251 | 112 | 0.0020822 | 0.00052184 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2702-2_0_2_load_272 | 114 | 0.0021288 | 0.00053352 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 64 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2702-2_0_2_line_0 |  | 0 | 1 | 0.017427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2702-2_0_2_line_1 |  | 0 | 2 | 0.0049425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2702-2_0_2_line_2 |  | 1 | 3 | 0.0416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2702-2_0_2_line_3 |  | 2 | 4 | 0.01537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2702-2_0_2_line_4 |  | 3 | 5 | 0.016638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2702-2_0_2_line_5 |  | 3 | 6 | 0.032208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2702-2_0_2_line_6 |  | 4 | 7 | 0.0049536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2702-2_0_2_line_7 |  | 5 | 8 | 0.024427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2702-2_0_2_line_8 |  | 5 | 9 | 0.016507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2702-2_0_2_line_9 |  | 7 | 10 | 0.0020752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2702-2_0_2_line_10 |  | 8 | 34 | 0.0059631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2702-2_0_2_line_11 |  | 9 | 35 | 0.025473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2702-2_0_2_line_12 |  | 10 | 101 | 0.015151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2702-2_0_2_line_13 |  | 11 | 12 | 0.018222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2702-2_0_2_line_14 |  | 11 | 13 | 0.013441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2702-2_0_2_line_15 |  | 12 | 14 | 0.013804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2702-2_0_2_line_16 |  | 13 | 15 | 0.033308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2702-2_0_2_line_17 |  | 13 | 16 | 0.029656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2702-2_0_2_line_18 |  | 13 | 17 | 0.01386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2702-2_0_2_line_19 |  | 14 | 18 | 0.0093698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2702-2_0_2_line_20 |  | 14 | 19 | 0.018292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2702-2_0_2_line_21 |  | 15 | 20 | 0.017453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2702-2_0_2_line_22 |  | 16 | 21 | 0.015659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2702-2_0_2_line_23 |  | 17 | 22 | 0.022079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2702-2_0_2_line_24 |  | 18 | 23 | 0.0115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2702-2_0_2_line_25 |  | 19 | 24 | 0.004106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2702-2_0_2_line_26 |  | 20 | 25 | 0.016704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2702-2_0_2_line_27 |  | 21 | 26 | 0.0054697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2702-2_0_2_line_28 |  | 22 | 27 | 0.0049123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2702-2_0_2_line_29 |  | 23 | 87 | 0.016739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2702-2_0_2_line_30 |  | 24 | 81 | 0.022312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2702-2_0_2_line_31 |  | 25 | 62 | 0.014971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2702-2_0_2_line_32 |  | 26 | 74 | 0.012893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2702-2_0_2_line_33 |  | 27 | 44 | 0.0014719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2702-2_0_2_line_34 |  | 28 | 29 | 0.007724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2702-2_0_2_line_35 |  | 28 | 30 | 0.016222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2702-2_0_2_line_36 |  | 29 | 31 | 0.03201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2702-2_0_2_line_37 |  | 29 | 32 | 0.010413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2702-2_0_2_line_38 |  | 30 | 33 | 0.028046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2702-2_0_2_line_39 |  | 31 | 111 | 0.0082937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2702-2_0_2_line_40 |  | 32 | 108 | 0.023341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2702-2_0_2_line_41 |  | 33 | 114 | 0.019608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2702-2_0_2_line_42 |  | 34 | 100 | 0.0095126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2702-2_0_2_line_43 |  | 35 | 38 | 0.015576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2702-2_0_2_line_44 |  | 36 | 37 | 0.028089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2702-2_0_2_line_45 |  | 36 | 38 | 0.008641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2702-2_0_2_line_46 |  | 37 | 39 | 0.0092806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2702-2_0_2_line_47 |  | 38 | 40 | 0.010607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2702-2_0_2_line_48 |  | 39 | 41 | 0.00465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2702-2_0_2_line_49 |  | 41 | 42 | 0.018169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2702-2_0_2_line_50 |  | 42 | 43 | 0.0038034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2702-2_0_2_line_51 |  | 43 | 69 | 0.01158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2702-2_0_2_line_52 |  | 44 | 45 | 0.00070498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2702-2_0_2_line_53 |  | 45 | 46 | 0.022065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2702-2_0_2_line_54 |  | 46 | 47 | 0.0069771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2702-2_0_2_line_55 |  | 47 | 68 | 3.8941e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2702-2_0_2_line_56 |  | 48 | 49 | 0.016424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2702-2_0_2_line_57 |  | 48 | 50 | 0.012661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2702-2_0_2_line_58 |  | 49 | 51 | 0.0057589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2702-2_0_2_line_59 |  | 50 | 52 | 0.0063978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2702-2_0_2_line_60 |  | 51 | 53 | 0.012422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2702-2_0_2_line_61 |  | 52 | 54 | 0.0011599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2702-2_0_2_line_62 |  | 53 | 55 | 0.0045196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2702-2_0_2_line_63 |  | 54 | 56 | 0.04155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2702-2_0_2_line_64 |  | 55 | 72 | 0.018841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2702-2_0_2_line_65 |  | 56 | 57 | 0.0005687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2702-2_0_2_line_66 |  | 57 | 58 | 0.018072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2702-2_0_2_line_67 |  | 58 | 59 | 0.0049194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2702-2_0_2_line_68 |  | 59 | 60 | 0.0048607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2702-2_0_2_line_69 |  | 60 | 63 | 0.023901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2702-2_0_2_line_70 |  | 60 | 61 | 0.016494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2702-2_0_2_line_71 |  | 62 | 64 | 0.016289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2702-2_0_2_line_72 |  | 63 | 65 | 0.0061282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2702-2_0_2_line_73 |  | 64 | 66 | 0.0091606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2702-2_0_2_line_74 |  | 65 | 67 | 0.0017187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2702-2_0_2_line_75 |  | 66 | 101 | 0.022348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2702-2_0_2_line_76 |  | 67 | 71 | 0.020679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2702-2_0_2_line_77 |  | 68 | 113 | 0.027968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2702-2_0_2_line_78 |  | 69 | 70 | 0.014756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2702-2_0_2_line_79 |  | 70 | 71 | 0.0024269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2702-2_0_2_line_80 |  | 72 | 73 | 0.014159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2702-2_0_2_line_81 |  | 74 | 75 | 0.0022766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2702-2_0_2_line_82 |  | 75 | 76 | 0.0032074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2702-2_0_2_line_83 |  | 76 | 77 | 0.010512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2702-2_0_2_line_84 |  | 78 | 79 | 0.013973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2702-2_0_2_line_85 |  | 79 | 82 | 0.03135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2702-2_0_2_line_86 |  | 79 | 80 | 0.022148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2702-2_0_2_line_87 |  | 80 | 81 | 0.0029022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2702-2_0_2_line_88 |  | 82 | 83 | 0.017134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2702-2_0_2_line_89 |  | 83 | 84 | 0.023422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2702-2_0_2_line_90 |  | 85 | 86 | 0.022542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2702-2_0_2_line_91 |  | 85 | 87 | 0.019507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2702-2_0_2_line_92 |  | 86 | 88 | 0.012595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2702-2_0_2_line_93 |  | 88 | 89 | 0.0085263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2702-2_0_2_line_94 |  | 89 | 90 | 0.0091333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2702-2_0_2_line_95 |  | 90 | 102 | 0.013054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2702-2_0_2_line_96 |  | 91 | 92 | 0.014699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2702-2_0_2_line_97 |  | 92 | 93 | 0.0088589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2702-2_0_2_line_98 |  | 93 | 94 | 0.02197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2702-2_0_2_line_99 |  | 94 | 95 | 0.036716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2702-2_0_2_line_100 |  | 95 | 109 | 0.0047612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2702-2_0_2_line_101 |  | 96 | 97 | 0.0055739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2702-2_0_2_line_102 |  | 97 | 98 | 0.0055703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2702-2_0_2_line_103 |  | 98 | 99 | 0.0056365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2702-2_0_2_line_104 |  | 99 | 100 | 0.0065456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2702-2_0_2_line_105 |  | 102 | 103 | 0.025879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2702-2_0_2_line_106 |  | 102 | 104 | 0.00374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2702-2_0_2_line_107 |  | 103 | 105 | 0.021561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2702-2_0_2_line_108 |  | 104 | 106 | 0.0044478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2702-2_0_2_line_109 |  | 105 | 115 | 0.0033278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2702-2_0_2_line_110 |  | 106 | 107 | 0.0035825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2702-2_0_2_line_111 |  | 107 | 108 | 0.030323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2702-2_0_2_line_112 |  | 109 | 110 | 0.002473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2702-2_0_2_line_113 |  | 110 | 115 | 0.016041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2702-2_0_2_line_114 |  | 112 | 113 | 0.070778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2702-2_0_2_trafo_115 | 0.63 MVA 20/0.4 kV | 116 | 64 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2616870.88 | 1268792.5783 | 2616882.7402 | 1268793.1195 | 2616888.2151 | 1268794.0545
1 | 2616870.88 | 1268792.5783 | 2616865.9427 | 1268792.3529
2 | 2616929.2214 | 1268801.0576 | 2616888.2151 | 1268794.0545
3 | 2616865.9427 | 1268792.3529 | 2616850.5887 | 1268791.6523
4 | 2616921.6184 | 1268786.2477 | 2616929.2214 | 1268801.0576
5 | 2616929.2214 | 1268801.0576 | 2616948.404 | 1268826.9305
6 | 2616845.6403 | 1268791.4264 | 2616850.5887 | 1268791.6523
7 | 2616921.6184 | 1268786.2477 | 2616933.1918 | 1268786.2363 | 2616945.4691 | 1268790.0407 | 2616945.4691 | 1268790.0407
8 | 2616921.6184 | 1268786.2477 | 2616912.8662 | 1268772.2524
9 | 2616843.5672 | 1268791.3318 | 2616845.6403 | 1268791.4264
10 | 2616949.9729 | 1268793.949 | 2616945.4691 | 1268790.0407
11 | 2616899.3598 | 1268750.6548 | 2616912.8662 | 1268772.2524
12 | 2616843.5672 | 1268791.3318 | 2616828.4324 | 1268790.6411 | 2616828.4324 | 1268790.6411
13 | 2616723.8545 | 1268860.8873 | 2616714.3808 | 1268845.322
14 | 2616707.3927 | 1268833.8405 | 2616714.3808 | 1268845.322
15 | 2616731.0315 | 1268872.679 | 2616723.8545 | 1268860.8873
16 | 2616707.3927 | 1268833.8405 | 2616730.6607 | 1268820.1186 | 2616736.2826 | 1268817.2863
17 | 2616707.3927 | 1268833.8405 | 2616682.7241 | 1268850.3008
18 | 2616707.3927 | 1268833.8405 | 2616700.8802 | 1268821.6053
19 | 2616731.0315 | 1268872.679 | 2616739.2929 | 1268868.2584
20 | 2616731.0315 | 1268872.679 | 2616715.8118 | 1268882.8251
21 | 2616736.2826 | 1268817.2863 | 2616751.869 | 1268809.4341
22 | 2616682.7241 | 1268850.3008 | 2616669.6988 | 1268858.9921
23 | 2616690.506 | 1268802.115 | 2616700.8802 | 1268821.6053
24 | 2616749.4327 | 1268862.8327 | 2616739.2929 | 1268868.2584
25 | 2616712.3954 | 1268885.1027 | 2616715.8118 | 1268882.8251
26 | 2616766.7864 | 1268801.9189 | 2616751.869 | 1268809.4341
27 | 2616669.6988 | 1268858.9921 | 2616665.149 | 1268862.0281
28 | 2616688.2927 | 1268797.7295 | 2616690.506 | 1268802.115 | 2616690.506 | 1268802.115
29 | 2616764.1918 | 1268854.9351 | 2616749.4327 | 1268862.8327
30 | 2616712.3954 | 1268885.1027 | 2616695.2063 | 1268896.5616 | 2616693.8543 | 1268897.5134
31 | 2616766.7864 | 1268801.9189 | 2616781.3317 | 1268798.3723
32 | 2616654.4243 | 1268869.1842 | 2616665.149 | 1268862.0281
33 | 2616688.2927 | 1268797.7295 | 2616687.6295 | 1268796.4154
34 | 2616909.7637 | 1268858.4983 | 2616902.0199 | 1268858.743
35 | 2616909.7637 | 1268858.4983 | 2616909.6545 | 1268874.7201
36 | 2616902.0199 | 1268858.743 | 2616900.661 | 1268831.2864 | 2616901.4328 | 1268826.8333
37 | 2616902.0199 | 1268858.743 | 2616891.6121 | 1268859.0742
38 | 2616909.4659 | 1268902.7657 | 2616909.6545 | 1268874.7201
39 | 2616902.8491 | 1268818.6615 | 2616901.4328 | 1268826.8333
40 | 2616891.6121 | 1268859.0742 | 2616875.4022 | 1268859.59 | 2616868.3655 | 1268860.6923
41 | 2616909.4659 | 1268902.7657 | 2616909.3585 | 1268918.7286 | 2616909.4077 | 1268922.3732
42 | 2616949.9729 | 1268793.949 | 2616957.1575 | 1268800.1837
43 | 2616891.101 | 1268737.4484 | 2616899.3598 | 1268750.6548
44 | 2616882.4846 | 1268736.7962 | 2616854.4753 | 1268734.6758
45 | 2616891.101 | 1268737.4484 | 2616882.4846 | 1268736.7962
46 | 2616845.209 | 1268734.4657 | 2616850.046 | 1268734.3405 | 2616854.4753 | 1268734.6758
47 | 2616891.101 | 1268737.4484 | 2616884.4308 | 1268729.2013
48 | 2616840.5606 | 1268734.586 | 2616845.209 | 1268734.4657
49 | 2616840.5606 | 1268734.586 | 2616822.398 | 1268735.0559
50 | 2616822.398 | 1268735.0559 | 2616818.5958 | 1268735.1543
51 | 2616807.0193 | 1268735.4539 | 2616818.5958 | 1268735.1543
52 | 2616687.3119 | 1268795.7861 | 2616687.6295 | 1268796.4154
53 | 2616677.3706 | 1268776.0878 | 2616687.3119 | 1268795.7861
54 | 2616677.3706 | 1268776.0878 | 2616674.227 | 1268769.859
55 | 2616674.2095 | 1268769.8242 | 2616674.227 | 1268769.859
56 | 2616720.1809 | 1268677.363 | 2616724.6338 | 1268675.9553 | 2616736.2183 | 1268673.9676
57 | 2616720.1809 | 1268677.363 | 2616708.1091 | 1268681.1791
58 | 2616736.2183 | 1268673.9676 | 2616741.8943 | 1268672.9936
59 | 2616708.1091 | 1268681.1791 | 2616708.1091 | 1268681.1791 | 2616705.6017 | 1268687.0651
60 | 2616754.137 | 1268670.8929 | 2616741.8943 | 1268672.9936
61 | 2616706.1489 | 1268688.0877 | 2616705.6017 | 1268687.0651 | 2616705.6017 | 1268687.0651
62 | 2616758.6533 | 1268671.0168 | 2616754.2141 | 1268670.8797 | 2616754.137 | 1268670.8929
63 | 2616725.7511 | 1268724.7228 | 2616706.1489 | 1268688.0877
64 | 2616758.6533 | 1268671.0168 | 2616777.4854 | 1268671.5986
65 | 2616726.0194 | 1268725.2242 | 2616725.7511 | 1268724.7228
66 | 2616734.5453 | 1268741.1586 | 2616726.0194 | 1268725.2242
67 | 2616736.8662 | 1268745.4961 | 2616734.5453 | 1268741.1586
68 | 2616739.1593 | 1268749.7818 | 2616736.8662 | 1268745.4961
69 | 2616739.1593 | 1268749.7818 | 2616757.1915 | 1268743.6173 | 2616761.9572 | 1268742.7505
70 | 2616739.1593 | 1268749.7818 | 2616746.882 | 1268764.3558
71 | 2616781.3317 | 1268798.3723 | 2616796.2668 | 1268794.7306 | 2616797.1753 | 1268794.6151
72 | 2616761.9572 | 1268742.7505 | 2616767.9865 | 1268741.654
73 | 2616806.2628 | 1268793.4597 | 2616797.1753 | 1268794.6151
74 | 2616767.9865 | 1268741.654 | 2616769.6775 | 1268741.3465
75 | 2616806.2628 | 1268793.4597 | 2616828.4324 | 1268790.6411
76 | 2616769.6775 | 1268741.3465 | 2616790.0226 | 1268737.6463
77 | 2616661.244 | 1268745.0479 | 2616666.7917 | 1268755.1262 | 2616674.2095 | 1268769.8242
78 | 2616792.4104 | 1268737.2121 | 2616801.2579 | 1268735.603 | 2616807.0193 | 1268735.4539
79 | 2616792.4104 | 1268737.2121 | 2616790.0226 | 1268737.6463
80 | 2616791.6244 | 1268672.2341 | 2616788.6834 | 1268671.9446 | 2616777.4854 | 1268671.5986
81 | 2616652.5306 | 1268870.4478 | 2616654.4243 | 1268869.1842
82 | 2616649.8626 | 1268872.228 | 2616652.5306 | 1268870.4478
83 | 2616649.8626 | 1268872.228 | 2616641.1172 | 1268878.0606
84 | 2616673.3712 | 1268911.9333 | 2616666.2522 | 1268899.9094
85 | 2616673.3712 | 1268911.9333 | 2616647.8785 | 1268930.2857
86 | 2616673.3712 | 1268911.9333 | 2616691.4812 | 1268899.184
87 | 2616691.4812 | 1268899.184 | 2616693.8543 | 1268897.5134
88 | 2616647.8785 | 1268930.2857 | 2616655.3 | 1268945.7287
89 | 2616655.3 | 1268945.7287 | 2616665.4453 | 1268966.8394
90 | 2616781.3916 | 1268845.7316 | 2616791.0576 | 1268840.5594 | 2616802.6353 | 1268840.3579
91 | 2616764.1918 | 1268854.9351 | 2616781.3916 | 1268845.7316
92 | 2616815.2286 | 1268840.1387 | 2616815.2286 | 1268840.1387 | 2616802.6353 | 1268840.3579
93 | 2616815.2286 | 1268840.1387 | 2616821.9938 | 1268845.3282
94 | 2616825.2777 | 1268853.8507 | 2616821.9938 | 1268845.3282 | 2616821.9938 | 1268845.3282
95 | 2616829.9715 | 1268866.0321 | 2616825.2777 | 1268853.8507
96 | 2616713.3716 | 1268960.9857 | 2616716.4846 | 1268958.5321 | 2616724.4988 | 1268951.3899
97 | 2616731.1124 | 1268945.4958 | 2616724.4988 | 1268951.3899
98 | 2616747.5143 | 1268930.8785 | 2616731.1124 | 1268945.4958
99 | 2616774.9334 | 1268906.4603 | 2616761.1585 | 1268918.7189 | 2616747.5143 | 1268930.8785
100 | 2616774.9334 | 1268906.4603 | 2616771.7303 | 1268902.9376
101 | 2616974.576 | 1268815.6972 | 2616970.4322 | 1268811.9694
102 | 2616970.4322 | 1268811.9694 | 2616966.291 | 1268808.244
103 | 2616966.291 | 1268808.244 | 2616962.1006 | 1268804.4744
104 | 2616957.1575 | 1268800.1837 | 2616962.0655 | 1268804.4428 | 2616962.1006 | 1268804.4744
105 | 2616829.9715 | 1268866.0321 | 2616809.771 | 1268875.3592 | 2616806.7406 | 1268877.3555
106 | 2616829.9715 | 1268866.0321 | 2616831.1504 | 1268869.5824
107 | 2616788.7348 | 1268889.2166 | 2616806.7406 | 1268877.3555
108 | 2616831.1504 | 1268869.5824 | 2616835.3474 | 1268868.1101
109 | 2616785.9557 | 1268891.0473 | 2616788.7348 | 1268889.2166
110 | 2616838.7279 | 1268866.9243 | 2616835.3474 | 1268868.1101
111 | 2616838.7279 | 1268866.9243 | 2616853.9995 | 1268862.9427 | 2616868.3655 | 1268860.6923
112 | 2616773.571 | 1268901.2861 | 2616771.7303 | 1268902.9376
113 | 2616773.571 | 1268901.2861 | 2616785.9557 | 1268891.0473
114 | 2616661.244 | 1268745.0479 | 2616648.9353 | 1268741.6331 | 2616626.0632 | 1268750.9756 | 2616601.5737 | 1268773.5366

## bus_geodata
| x | y | coords
0 | 2616870.88 | 1268792.5783
1 | 2616888.2151 | 1268794.0545
2 | 2616865.9427 | 1268792.3529
3 | 2616929.2214 | 1268801.0576
4 | 2616850.5887 | 1268791.6523
5 | 2616921.6184 | 1268786.2477
6 | 2616948.404 | 1268826.9305
7 | 2616845.6403 | 1268791.4264
8 | 2616945.4691 | 1268790.0407
9 | 2616912.8662 | 1268772.2524
10 | 2616843.5672 | 1268791.3318
11 | 2616714.3808 | 1268845.322
12 | 2616723.8545 | 1268860.8873
13 | 2616707.3927 | 1268833.8405
14 | 2616731.0315 | 1268872.679
15 | 2616736.2826 | 1268817.2863
16 | 2616682.7241 | 1268850.3008
17 | 2616700.8802 | 1268821.6053
18 | 2616739.2929 | 1268868.2584
19 | 2616715.8118 | 1268882.8251
20 | 2616751.869 | 1268809.4341
21 | 2616669.6988 | 1268858.9921
22 | 2616690.5059 | 1268802.115
23 | 2616749.4327 | 1268862.8327
24 | 2616712.3954 | 1268885.1027
25 | 2616766.7864 | 1268801.9189
26 | 2616665.149 | 1268862.0281
27 | 2616688.2927 | 1268797.7295
28 | 2616909.7637 | 1268858.4983
29 | 2616902.0199 | 1268858.743
30 | 2616909.6545 | 1268874.7201
31 | 2616901.4328 | 1268826.8333
32 | 2616891.6121 | 1268859.0742
33 | 2616909.4659 | 1268902.7657
34 | 2616949.9729 | 1268793.949
35 | 2616899.3598 | 1268750.6548
36 | 2616882.4846 | 1268736.7962
37 | 2616854.4753 | 1268734.6758
38 | 2616891.101 | 1268737.4484
39 | 2616845.209 | 1268734.4657
40 | 2616884.4308 | 1268729.2013
41 | 2616840.5606 | 1268734.586
42 | 2616822.398 | 1268735.0559
43 | 2616818.5958 | 1268735.1543
44 | 2616687.6295 | 1268796.4154
45 | 2616687.3119 | 1268795.7861
46 | 2616677.3706 | 1268776.0878
47 | 2616674.227 | 1268769.859
48 | 2616720.1809 | 1268677.363
49 | 2616736.2183 | 1268673.9676
50 | 2616708.1091 | 1268681.1791
51 | 2616741.8943 | 1268672.9936
52 | 2616705.6017 | 1268687.0651
53 | 2616754.137 | 1268670.8929
54 | 2616706.1489 | 1268688.0878
55 | 2616758.6533 | 1268671.0168
56 | 2616725.7511 | 1268724.7228
57 | 2616726.0194 | 1268725.2242
58 | 2616734.5453 | 1268741.1586
59 | 2616736.8662 | 1268745.4961
60 | 2616739.1593 | 1268749.7818
61 | 2616746.882 | 1268764.3558
62 | 2616781.3317 | 1268798.3723
63 | 2616761.9572 | 1268742.7505
64 | 2616797.1753 | 1268794.6151
65 | 2616767.9865 | 1268741.654
66 | 2616806.2628 | 1268793.4597
67 | 2616769.6775 | 1268741.3465
68 | 2616674.2095 | 1268769.8242
69 | 2616807.0193 | 1268735.4539
70 | 2616792.4104 | 1268737.2121
71 | 2616790.0226 | 1268737.6463
72 | 2616777.4854 | 1268671.5986
73 | 2616791.6244 | 1268672.2341
74 | 2616654.4243 | 1268869.1842
75 | 2616652.5306 | 1268870.4478
76 | 2616649.8626 | 1268872.228
77 | 2616641.1172 | 1268878.0606
78 | 2616666.2522 | 1268899.9094
79 | 2616673.3712 | 1268911.9333
80 | 2616691.4812 | 1268899.184
81 | 2616693.8543 | 1268897.5134
82 | 2616647.8785 | 1268930.2857
83 | 2616655.3 | 1268945.7287
84 | 2616665.4453 | 1268966.8394
85 | 2616781.3916 | 1268845.7316
86 | 2616802.6353 | 1268840.3579
87 | 2616764.1918 | 1268854.9351
88 | 2616815.2286 | 1268840.1387
89 | 2616821.9938 | 1268845.3282
90 | 2616825.2777 | 1268853.8507
91 | 2616713.3716 | 1268960.9857
92 | 2616724.4988 | 1268951.3899
93 | 2616731.1124 | 1268945.4958
94 | 2616747.5143 | 1268930.8785
95 | 2616774.9334 | 1268906.4603
96 | 2616974.576 | 1268815.6972
97 | 2616970.4322 | 1268811.9694
98 | 2616966.291 | 1268808.244
99 | 2616962.1006 | 1268804.4744
100 | 2616957.1575 | 1268800.1837
101 | 2616828.4324 | 1268790.6411
102 | 2616829.9715 | 1268866.0321
103 | 2616806.7406 | 1268877.3555
104 | 2616831.1504 | 1268869.5824
105 | 2616788.7348 | 1268889.2166
106 | 2616835.3474 | 1268868.1101
107 | 2616838.7279 | 1268866.9243
108 | 2616868.3655 | 1268860.6923
109 | 2616771.7303 | 1268902.9376
110 | 2616773.571 | 1268901.2861
111 | 2616902.8491 | 1268818.6615
112 | 2616601.5737 | 1268773.5366
113 | 2616661.244 | 1268745.0479
114 | 2616909.4077 | 1268922.3732
115 | 2616785.9557 | 1268891.0473
116 | 2616766.7864 | 1268801.9189

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1