## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2770-23_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2770-23_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2770-23_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2770-23_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2770-23_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2770-23_0_5_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_2770-23_0_5_node_104 | 0.4 | n |  | TRUE
7 | bus_LV_2770-23_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2770-23_0_5_node_107 | 0.4 | n |  | TRUE
9 | bus_LV_2770-23_0_5_node_103 | 0.4 | n |  | TRUE
10 | bus_LV_2770-23_0_5_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2770-23_0_5_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2770-23_0_5_node_177 | 0.4 | n |  | TRUE
13 | bus_LV_2770-23_0_5_node_182 | 0.4 | n |  | TRUE
14 | bus_LV_2770-23_0_5_node_176 | 0.4 | n |  | TRUE
15 | bus_LV_2770-23_0_5_node_174 | 0.4 | n |  | TRUE
16 | bus_LV_2770-23_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_2770-23_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_2770-23_0_5_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2770-23_0_5_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_2770-23_0_5_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_2770-23_0_5_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_2770-23_0_5_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_2770-23_0_5_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_2770-23_0_5_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_2770-23_0_5_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_2770-23_0_5_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2770-23_0_5_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_2770-23_0_5_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_2770-23_0_5_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2770-23_0_5_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_2770-23_0_5_node_79 | 0.4 | n |  | TRUE
32 | bus_LV_2770-23_0_5_node_41 | 0.4 | n |  | TRUE
33 | bus_LV_2770-23_0_5_node_80 | 0.4 | n |  | TRUE
34 | bus_LV_2770-23_0_5_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_2770-23_0_5_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_2770-23_0_5_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_2770-23_0_5_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_2770-23_0_5_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_2770-23_0_5_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_2770-23_0_5_node_97 | 0.4 | n |  | TRUE
41 | bus_LV_2770-23_0_5_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_2770-23_0_5_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_2770-23_0_5_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_2770-23_0_5_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_2770-23_0_5_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_2770-23_0_5_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_2770-23_0_5_node_183 | 0.4 | n |  | TRUE
48 | bus_LV_2770-23_0_5_node_184 | 0.4 | n |  | TRUE
49 | bus_LV_2770-23_0_5_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_2770-23_0_5_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_2770-23_0_5_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_2770-23_0_5_node_105 | 0.4 | n |  | TRUE
53 | bus_LV_2770-23_0_5_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_2770-23_0_5_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_2770-23_0_5_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_2770-23_0_5_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_2770-23_0_5_node_77 | 0.4 | n |  | TRUE
58 | bus_LV_2770-23_0_5_node_76 | 0.4 | n |  | TRUE
59 | bus_LV_2770-23_0_5_node_219 | 0.4 | n |  | TRUE
60 | bus_LV_2770-23_0_5_node_78 | 0.4 | n |  | TRUE
61 | bus_LV_2770-23_0_5_node_218 | 0.4 | n |  | TRUE
62 | bus_LV_2770-23_0_5_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_2770-23_0_5_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_2770-23_0_5_node_46 | 0.4 | n |  | TRUE
65 | bus_LV_2770-23_0_5_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_2770-23_0_5_node_48 | 0.4 | n |  | TRUE
67 | bus_LV_2770-23_0_5_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_2770-23_0_5_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_2770-23_0_5_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_2770-23_0_5_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_2770-23_0_5_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_2770-23_0_5_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_2770-23_0_5_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_2770-23_0_5_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_2770-23_0_5_node_67 | 0.4 | n |  | TRUE
76 | bus_LV_2770-23_0_5_node_75 | 0.4 | n |  | TRUE
77 | bus_LV_2770-23_0_5_node_59 | 0.4 | n |  | TRUE
78 | bus_LV_2770-23_0_5_node_57 | 0.4 | n |  | TRUE
79 | bus_LV_2770-23_0_5_node_93 | 0.4 | n |  | TRUE
80 | bus_LV_2770-23_0_5_node_92 | 0.4 | n |  | TRUE
81 | bus_LV_2770-23_0_5_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_2770-23_0_5_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_2770-23_0_5_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_2770-23_0_5_node_60 | 0.4 | n |  | TRUE
85 | bus_LV_2770-23_0_5_node_61 | 0.4 | n |  | TRUE
86 | bus_LV_2770-23_0_5_node_62 | 0.4 | n |  | TRUE
87 | bus_LV_2770-23_0_5_node_63 | 0.4 | n |  | TRUE
88 | bus_LV_2770-23_0_5_node_65 | 0.4 | n |  | TRUE
89 | bus_LV_2770-23_0_5_node_221 | 0.4 | n |  | TRUE
90 | bus_LV_2770-23_0_5_node_222 | 0.4 | n |  | TRUE
91 | bus_LV_2770-23_0_5_node_217 | 0.4 | n |  | TRUE
92 | bus_LV_2770-23_0_5_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_2770-23_0_5_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_2770-23_0_5_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_2770-23_0_5_node_72 | 0.4 | n |  | TRUE
96 | bus_LV_2770-23_0_5_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_2770-23_0_5_node_216 | 0.4 | n |  | TRUE
98 | bus_LV_2770-23_0_5_node_190 | 0.4 | n |  | TRUE
99 | bus_LV_2770-23_0_5_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_2770-23_0_5_node_83 | 0.4 | n |  | TRUE
101 | bus_LV_2770-23_0_5_node_84 | 0.4 | n |  | TRUE
102 | bus_LV_2770-23_0_5_node_81 | 0.4 | n |  | TRUE
103 | bus_LV_2770-23_0_5_node_88 | 0.4 | n |  | TRUE
104 | bus_LV_2770-23_0_5_node_89 | 0.4 | n |  | TRUE
105 | bus_LV_2770-23_0_5_node_86 | 0.4 | n |  | TRUE
106 | bus_LV_2770-23_0_5_node_90 | 0.4 | n |  | TRUE
107 | bus_LV_2770-23_0_5_node_91 | 0.4 | n |  | TRUE
108 | bus_LV_2770-23_0_5_node_85 | 0.4 | n |  | TRUE
109 | bus_LV_2770-23_0_5_node_96 | 0.4 | n |  | TRUE
110 | bus_LV_2770-23_0_5_node_278 | 0.4 | n |  | TRUE
111 | bus_LV_2770-23_0_5_node_94 | 0.4 | n |  | TRUE
112 | bus_LV_2770-23_0_5_node_98 | 0.4 | n |  | TRUE
113 | bus_LV_2770-23_0_5_node_99 | 0.4 | n |  | TRUE
114 | bus_LV_2770-23_0_5_node_100 | 0.4 | n |  | TRUE
115 | bus_LV_2770-23_0_5_node_101 | 0.4 | n |  | TRUE
116 | bus_LV_2770-23_0_5_node_106 | 0.4 | n |  | TRUE
117 | bus_LV_2770-23_0_5_node_268 | 0.4 | n |  | TRUE
118 | bus_LV_2770-23_0_5_node_269 | 0.4 | n |  | TRUE
119 | bus_LV_2770-23_0_5_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_2770-23_0_5_node_109 | 0.4 | n |  | TRUE
121 | bus_LV_2770-23_0_5_node_110 | 0.4 | n |  | TRUE
122 | bus_LV_2770-23_0_5_node_112 | 0.4 | n |  | TRUE
123 | bus_LV_2770-23_0_5_node_121 | 0.4 | n |  | TRUE
124 | bus_LV_2770-23_0_5_node_116 | 0.4 | n |  | TRUE
125 | bus_LV_2770-23_0_5_node_117 | 0.4 | n |  | TRUE
126 | bus_LV_2770-23_0_5_node_122 | 0.4 | n |  | TRUE
127 | bus_LV_2770-23_0_5_node_113 | 0.4 | n |  | TRUE
128 | bus_LV_2770-23_0_5_node_114 | 0.4 | n |  | TRUE
129 | bus_LV_2770-23_0_5_node_115 | 0.4 | n |  | TRUE
130 | bus_LV_2770-23_0_5_node_210 | 0.4 | n |  | TRUE
131 | bus_LV_2770-23_0_5_node_209 | 0.4 | n |  | TRUE
132 | bus_LV_2770-23_0_5_node_118 | 0.4 | n |  | TRUE
133 | bus_LV_2770-23_0_5_node_119 | 0.4 | n |  | TRUE
134 | bus_LV_2770-23_0_5_node_120 | 0.4 | n |  | TRUE
135 | bus_LV_2770-23_0_5_node_124 | 0.4 | n |  | TRUE
136 | bus_LV_2770-23_0_5_node_125 | 0.4 | n |  | TRUE
137 | bus_LV_2770-23_0_5_node_123 | 0.4 | n |  | TRUE
138 | bus_LV_2770-23_0_5_node_128 | 0.4 | n |  | TRUE
139 | bus_LV_2770-23_0_5_node_127 | 0.4 | n |  | TRUE
140 | bus_LV_2770-23_0_5_node_126 | 0.4 | n |  | TRUE
141 | bus_LV_2770-23_0_5_node_131 | 0.4 | n |  | TRUE
142 | bus_LV_2770-23_0_5_node_132 | 0.4 | n |  | TRUE
143 | bus_LV_2770-23_0_5_node_129 | 0.4 | n |  | TRUE
144 | bus_LV_2770-23_0_5_node_130 | 0.4 | n |  | TRUE
145 | bus_LV_2770-23_0_5_node_133 | 0.4 | n |  | TRUE
146 | bus_LV_2770-23_0_5_node_134 | 0.4 | n |  | TRUE
147 | bus_LV_2770-23_0_5_node_157 | 0.4 | n |  | TRUE
148 | bus_LV_2770-23_0_5_node_154 | 0.4 | n |  | TRUE
149 | bus_LV_2770-23_0_5_node_135 | 0.4 | n |  | TRUE
150 | bus_LV_2770-23_0_5_node_136 | 0.4 | n |  | TRUE
151 | bus_LV_2770-23_0_5_node_137 | 0.4 | n |  | TRUE
152 | bus_LV_2770-23_0_5_node_138 | 0.4 | n |  | TRUE
153 | bus_LV_2770-23_0_5_node_141 | 0.4 | n |  | TRUE
154 | bus_LV_2770-23_0_5_node_143 | 0.4 | n |  | TRUE
155 | bus_LV_2770-23_0_5_node_139 | 0.4 | n |  | TRUE
156 | bus_LV_2770-23_0_5_node_140 | 0.4 | n |  | TRUE
157 | bus_LV_2770-23_0_5_node_142 | 0.4 | n |  | TRUE
158 | bus_LV_2770-23_0_5_node_144 | 0.4 | n |  | TRUE
159 | bus_LV_2770-23_0_5_node_151 | 0.4 | n |  | TRUE
160 | bus_LV_2770-23_0_5_node_145 | 0.4 | n |  | TRUE
161 | bus_LV_2770-23_0_5_node_148 | 0.4 | n |  | TRUE
162 | bus_LV_2770-23_0_5_node_146 | 0.4 | n |  | TRUE
163 | bus_LV_2770-23_0_5_node_164 | 0.4 | n |  | TRUE
164 | bus_LV_2770-23_0_5_node_165 | 0.4 | n |  | TRUE
165 | bus_LV_2770-23_0_5_node_147 | 0.4 | n |  | TRUE
166 | bus_LV_2770-23_0_5_node_149 | 0.4 | n |  | TRUE
167 | bus_LV_2770-23_0_5_node_150 | 0.4 | n |  | TRUE
168 | bus_LV_2770-23_0_5_node_152 | 0.4 | n |  | TRUE
169 | bus_LV_2770-23_0_5_node_153 | 0.4 | n |  | TRUE
170 | bus_LV_2770-23_0_5_node_155 | 0.4 | n |  | TRUE
171 | bus_LV_2770-23_0_5_node_156 | 0.4 | n |  | TRUE
172 | bus_LV_2770-23_0_5_node_158 | 0.4 | n |  | TRUE
173 | bus_LV_2770-23_0_5_node_163 | 0.4 | n |  | TRUE
174 | bus_LV_2770-23_0_5_node_223 | 0.4 | n |  | TRUE
175 | bus_LV_2770-23_0_5_node_161 | 0.4 | n |  | TRUE
176 | bus_LV_2770-23_0_5_node_159 | 0.4 | n |  | TRUE
177 | bus_LV_2770-23_0_5_node_160 | 0.4 | n |  | TRUE
178 | bus_LV_2770-23_0_5_node_162 | 0.4 | n |  | TRUE
179 | bus_LV_2770-23_0_5_node_170 | 0.4 | n |  | TRUE
180 | bus_LV_2770-23_0_5_node_171 | 0.4 | n |  | TRUE
181 | bus_LV_2770-23_0_5_node_224 | 0.4 | n |  | TRUE
182 | bus_LV_2770-23_0_5_node_166 | 0.4 | n |  | TRUE
183 | bus_LV_2770-23_0_5_node_167 | 0.4 | n |  | TRUE
184 | bus_LV_2770-23_0_5_node_168 | 0.4 | n |  | TRUE
185 | bus_LV_2770-23_0_5_node_179 | 0.4 | n |  | TRUE
186 | bus_LV_2770-23_0_5_node_169 | 0.4 | n |  | TRUE
187 | bus_LV_2770-23_0_5_node_180 | 0.4 | n |  | TRUE
188 | bus_LV_2770-23_0_5_node_172 | 0.4 | n |  | TRUE
189 | bus_LV_2770-23_0_5_node_173 | 0.4 | n |  | TRUE
190 | bus_LV_2770-23_0_5_node_178 | 0.4 | n |  | TRUE
191 | bus_LV_2770-23_0_5_node_175 | 0.4 | n |  | TRUE
192 | bus_LV_2770-23_0_5_node_237 | 0.4 | n |  | TRUE
193 | bus_LV_2770-23_0_5_node_238 | 0.4 | n |  | TRUE
194 | bus_LV_2770-23_0_5_node_181 | 0.4 | n |  | TRUE
195 | bus_LV_2770-23_0_5_node_189 | 0.4 | n |  | TRUE
196 | bus_LV_2770-23_0_5_node_188 | 0.4 | n |  | TRUE
197 | bus_LV_2770-23_0_5_node_185 | 0.4 | n |  | TRUE
198 | bus_LV_2770-23_0_5_node_186 | 0.4 | n |  | TRUE
199 | bus_LV_2770-23_0_5_node_187 | 0.4 | n |  | TRUE
200 | bus_LV_2770-23_0_5_node_191 | 0.4 | n |  | TRUE
201 | bus_LV_2770-23_0_5_node_194 | 0.4 | n |  | TRUE
202 | bus_LV_2770-23_0_5_node_196 | 0.4 | n |  | TRUE
203 | bus_LV_2770-23_0_5_node_192 | 0.4 | n |  | TRUE
204 | bus_LV_2770-23_0_5_node_193 | 0.4 | n |  | TRUE
205 | bus_LV_2770-23_0_5_node_195 | 0.4 | n |  | TRUE
206 | bus_LV_2770-23_0_5_node_197 | 0.4 | n |  | TRUE
207 | bus_LV_2770-23_0_5_node_198 | 0.4 | n |  | TRUE
208 | bus_LV_2770-23_0_5_node_220 | 0.4 | n |  | TRUE
209 | bus_LV_2770-23_0_5_node_199 | 0.4 | n |  | TRUE
210 | bus_LV_2770-23_0_5_node_200 | 0.4 | n |  | TRUE
211 | bus_LV_2770-23_0_5_node_206 | 0.4 | n |  | TRUE
212 | bus_LV_2770-23_0_5_node_214 | 0.4 | n |  | TRUE
213 | bus_LV_2770-23_0_5_node_204 | 0.4 | n |  | TRUE
214 | bus_LV_2770-23_0_5_node_201 | 0.4 | n |  | TRUE
215 | bus_LV_2770-23_0_5_node_202 | 0.4 | n |  | TRUE
216 | bus_LV_2770-23_0_5_node_203 | 0.4 | n |  | TRUE
217 | bus_LV_2770-23_0_5_node_205 | 0.4 | n |  | TRUE
218 | bus_LV_2770-23_0_5_node_207 | 0.4 | n |  | TRUE
219 | bus_LV_2770-23_0_5_node_208 | 0.4 | n |  | TRUE
220 | bus_LV_2770-23_0_5_node_272 | 0.4 | n |  | TRUE
221 | bus_LV_2770-23_0_5_node_213 | 0.4 | n |  | TRUE
222 | bus_LV_2770-23_0_5_node_211 | 0.4 | n |  | TRUE
223 | bus_LV_2770-23_0_5_node_212 | 0.4 | n |  | TRUE
224 | bus_LV_2770-23_0_5_node_215 | 0.4 | n |  | TRUE
225 | bus_LV_2770-23_0_5_node_225 | 0.4 | n |  | TRUE
226 | bus_LV_2770-23_0_5_node_226 | 0.4 | n |  | TRUE
227 | bus_LV_2770-23_0_5_node_227 | 0.4 | n |  | TRUE
228 | bus_LV_2770-23_0_5_node_277 | 0.4 | n |  | TRUE
229 | bus_LV_2770-23_0_5_node_229 | 0.4 | n |  | TRUE
230 | bus_LV_2770-23_0_5_node_230 | 0.4 | n |  | TRUE
231 | bus_LV_2770-23_0_5_node_233 | 0.4 | n |  | TRUE
232 | bus_LV_2770-23_0_5_node_231 | 0.4 | n |  | TRUE
233 | bus_LV_2770-23_0_5_node_232 | 0.4 | n |  | TRUE
234 | bus_LV_2770-23_0_5_node_234 | 0.4 | n |  | TRUE
235 | bus_LV_2770-23_0_5_node_235 | 0.4 | n |  | TRUE
236 | bus_LV_2770-23_0_5_node_236 | 0.4 | n |  | TRUE
237 | bus_LV_2770-23_0_5_node_275 | 0.4 | n |  | TRUE
238 | bus_LV_2770-23_0_5_node_273 | 0.4 | n |  | TRUE
239 | bus_LV_2770-23_0_5_node_258 | 0.4 | n |  | TRUE
240 | bus_LV_2770-23_0_5_node_262 | 0.4 | n |  | TRUE
241 | bus_LV_2770-23_0_5_node_274 | 0.4 | n |  | TRUE
242 | bus_LV_2770-23_0_5_node_252 | 0.4 | n |  | TRUE
243 | bus_LV_2770-23_0_5_node_260 | 0.4 | n |  | TRUE
244 | bus_LV_2770-23_0_5_node_261 | 0.4 | n |  | TRUE
245 | bus_LV_2770-23_0_5_node_239 | 0.4 | n |  | TRUE
246 | bus_LV_2770-23_0_5_node_240 | 0.4 | n |  | TRUE
247 | bus_LV_2770-23_0_5_node_241 | 0.4 | n |  | TRUE
248 | bus_LV_2770-23_0_5_node_242 | 0.4 | n |  | TRUE
249 | bus_LV_2770-23_0_5_node_243 | 0.4 | n |  | TRUE
250 | bus_LV_2770-23_0_5_node_244 | 0.4 | n |  | TRUE
251 | bus_LV_2770-23_0_5_node_245 | 0.4 | n |  | TRUE
252 | bus_LV_2770-23_0_5_node_246 | 0.4 | n |  | TRUE
253 | bus_LV_2770-23_0_5_node_253 | 0.4 | n |  | TRUE
254 | bus_LV_2770-23_0_5_node_251 | 0.4 | n |  | TRUE
255 | bus_LV_2770-23_0_5_node_270 | 0.4 | n |  | TRUE
256 | bus_LV_2770-23_0_5_node_271 | 0.4 | n |  | TRUE
257 | bus_LV_2770-23_0_5_node_249 | 0.4 | n |  | TRUE
258 | bus_LV_2770-23_0_5_node_247 | 0.4 | n |  | TRUE
259 | bus_LV_2770-23_0_5_node_248 | 0.4 | n |  | TRUE
260 | bus_LV_2770-23_0_5_node_250 | 0.4 | n |  | TRUE
261 | bus_LV_2770-23_0_5_node_257 | 0.4 | n |  | TRUE
262 | bus_LV_2770-23_0_5_node_255 | 0.4 | n |  | TRUE
263 | bus_LV_2770-23_0_5_node_267 | 0.4 | n |  | TRUE
264 | bus_LV_2770-23_0_5_node_254 | 0.4 | n |  | TRUE
265 | bus_LV_2770-23_0_5_node_256 | 0.4 | n |  | TRUE
266 | bus_LV_2770-23_0_5_node_259 | 0.4 | n |  | TRUE
267 | bus_LV_2770-23_0_5_node_265 | 0.4 | n |  | TRUE
268 | bus_LV_2770-23_0_5_node_266 | 0.4 | n |  | TRUE
269 | bus_LV_2770-23_0_5_node_279 | 0.4 | n |  | TRUE
270 | bus_LV_2770-23_0_5_node_264 | 0.4 | n |  | TRUE
271 | bus_MV_575_0_node_30 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2770-23_0_5_load_0 | 0 | 0.0015574 | 0.00039032 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2770-23_0_5_load_1 | 1 | 0.001821 | 0.00045639 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2770-23_0_5_load_2 | 2 | 0.0008102 | 0.00020306 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2770-23_0_5_load_3 | 3 | 0.0015081 | 0.00037796 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2770-23_0_5_load_4 | 4 | 0.0017907 | 0.00044879 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2770-23_0_5_load_7 | 5 | 0.0012674 | 0.00031765 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2770-23_0_5_load_5 | 7 | 0.0022054 | 0.00055274 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2770-23_0_5_load_107 | 8 | 0.0014511 | 0.00036369 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2770-23_0_5_load_6 | 10 | 0.0018572 | 0.00046545 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2770-23_0_5_load_177 | 12 | 0.0028738 | 0.00072025 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2770-23_0_5_load_182 | 13 | 0.0011628 | 0.00029142 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2770-23_0_5_load_176 | 14 | 0.0026075 | 0.0006535 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2770-23_0_5_load_174 | 15 | 0.0018771 | 0.00047046 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2770-23_0_5_load_9 | 16 | 0.0018312 | 0.00045893 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2770-23_0_5_load_10 | 17 | 0.0018086 | 0.00045329 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2770-23_0_5_load_12 | 19 | 0.0036515 | 0.00091515 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2770-23_0_5_load_13 | 20 | 0.0035252 | 0.0008835 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2770-23_0_5_load_14 | 21 | 0.0019004 | 0.00047627 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2770-23_0_5_load_29 | 22 | 0.0020914 | 0.00052417 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2770-23_0_5_load_15 | 23 | 0.0084823 | 0.0021259 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2770-23_0_5_load_32 | 25 | 0.012195 | 0.0030564 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2770-23_0_5_load_16 | 26 | 0.0040106 | 0.0010051 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2770-23_0_5_load_27 | 27 | 0.0018348 | 0.00045985 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2770-23_0_5_load_28 | 28 | 0.0025579 | 0.00064108 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2770-23_0_5_load_79 | 31 | 0.0024096 | 0.0006039 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2770-23_0_5_load_41 | 32 | 0.0031019 | 0.0007774 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2770-23_0_5_load_80 | 33 | 0.0020475 | 0.00051315 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2770-23_0_5_load_18 | 34 | 0.0013115 | 0.0003287 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2770-23_0_5_load_19 | 35 | 0.0027532 | 0.00069003 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2770-23_0_5_load_20 | 36 | 0.0016684 | 0.00041814 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2770-23_0_5_load_21 | 37 | 0.0013154 | 0.00032968 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2770-23_0_5_load_24 | 38 | 0.0028363 | 0.00071085 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2770-23_0_5_load_23 | 39 | 0.0018822 | 0.00047173 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2770-23_0_5_load_97 | 40 | 0.002624 | 0.00065763 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2770-23_0_5_load_37 | 41 | 0.0022615 | 0.00056679 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2770-23_0_5_load_25 | 42 | 0.0014568 | 0.00036512 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2770-23_0_5_load_26 | 43 | 0.001875 | 0.00046992 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2770-23_0_5_load_30 | 44 | 0.001159 | 0.00029048 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2770-23_0_5_load_31 | 45 | 0.0022628 | 0.00056711 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2770-23_0_5_load_35 | 46 | 0.0021549 | 0.00054006 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2770-23_0_5_load_183 | 47 | 0.0021967 | 0.00055054 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2770-23_0_5_load_184 | 48 | 0.0032368 | 0.00081123 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2770-23_0_5_load_33 | 49 | 0.0015335 | 0.00038433 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2770-23_0_5_load_34 | 50 | 0.0021989 | 0.00055111 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2770-23_0_5_load_36 | 51 | 0.00206 | 0.00051629 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2770-23_0_5_load_105 | 52 | 0.0026304 | 0.00065924 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2770-23_0_5_load_38 | 53 | 0.0026764 | 0.00067076 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2770-23_0_5_load_42 | 55 | 0.0030776 | 0.00077132 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2770-23_0_5_load_43 | 56 | 0.0030464 | 0.00076351 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2770-23_0_5_load_77 | 57 | 0.0021663 | 0.00054291 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2770-23_0_5_load_76 | 58 | 0.015345 | 0.0038458 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2770-23_0_5_load_219 | 59 | 0.0011761 | 0.00029475 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2770-23_0_5_load_78 | 60 | 0.0012009 | 0.00030097 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2770-23_0_5_load_218 | 61 | 0.0013944 | 0.00034947 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2770-23_0_5_load_44 | 62 | 0.0050412 | 0.0012634 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2770-23_0_5_load_45 | 63 | 0.0015131 | 0.00037921 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2770-23_0_5_load_47 | 65 | 0.0014546 | 0.00036455 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2770-23_0_5_load_49 | 67 | 0.0037462 | 0.00093888 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2770-23_0_5_load_53 | 69 | 0.0031395 | 0.00078682 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2770-23_0_5_load_50 | 70 | 0.0060311 | 0.0015115 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2770-23_0_5_load_55 | 71 | 0.0022507 | 0.00056408 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2770-23_0_5_load_58 | 72 | 0.0016787 | 0.00042073 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2770-23_0_5_load_51 | 73 | 0.001469 | 0.00036818 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2770-23_0_5_load_52 | 74 | 0.0027504 | 0.00068931 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2770-23_0_5_load_67 | 75 | 0.0025031 | 0.00062735 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2770-23_0_5_load_75 | 76 | 0.0060123 | 0.0015068 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2770-23_0_5_load_59 | 77 | 0.002388 | 0.00059849 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2770-23_0_5_load_57 | 78 | 0.0030709 | 0.00076963 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2770-23_0_5_load_93 | 79 | 0.002011 | 0.00050401 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2770-23_0_5_load_92 | 80 | 0.001771 | 0.00044385 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2770-23_0_5_load_64 | 83 | 0.0015834 | 0.00039683 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2770-23_0_5_load_60 | 84 | 0.0014902 | 0.00037348 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2770-23_0_5_load_61 | 85 | 0.0014185 | 0.0003555 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2770-23_0_5_load_62 | 86 | 0.002661 | 0.00066692 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2770-23_0_5_load_63 | 87 | 0.0019179 | 0.00048067 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2770-23_0_5_load_65 | 88 | 0.0017557 | 0.00044002 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2770-23_0_5_load_221 | 89 | 0.0017024 | 0.00042666 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2770-23_0_5_load_222 | 90 | 0.0012234 | 0.00030662 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2770-23_0_5_load_217 | 91 | 0.0038776 | 0.00097181 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2770-23_0_5_load_73 | 92 | 0.0022241 | 0.00055741 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2770-23_0_5_load_69 | 93 | 0.0013283 | 0.0003329 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2770-23_0_5_load_70 | 94 | 0.0021575 | 0.00054073 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2770-23_0_5_load_72 | 95 | 0.0040525 | 0.0010157 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2770-23_0_5_load_74 | 96 | 0.010658 | 0.0026711 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2770-23_0_5_load_216 | 97 | 0.0013028 | 0.00032651 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2770-23_0_5_load_190 | 98 | 0.0013889 | 0.0003481 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2770-23_0_5_load_83 | 100 | 0.0043846 | 0.0010989 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2770-23_0_5_load_84 | 101 | 0.0019809 | 0.00049646 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2770-23_0_5_load_81 | 102 | 0.0016029 | 0.00040173 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2770-23_0_5_load_86 | 105 | 0.0014035 | 0.00035176 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2770-23_0_5_load_85 | 108 | 0.0022157 | 0.00055531 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2770-23_0_5_load_96 | 109 | 0.0021887 | 0.00054854 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2770-23_0_5_load_278 | 110 | 0.0034823 | 0.00087275 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2770-23_0_5_load_94 | 111 | 0.0013726 | 0.00034401 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2770-23_0_5_load_98 | 112 | 0.001115 | 0.00027945 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2770-23_0_5_load_99 | 113 | 0.0024912 | 0.00062434 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2770-23_0_5_load_100 | 114 | 0.0019577 | 0.00049064 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2770-23_0_5_load_101 | 115 | 0.002519 | 0.00063131 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2770-23_0_5_load_106 | 116 | 0.001637 | 0.00041027 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2770-23_0_5_load_268 | 117 | 0.0031216 | 0.00078235 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2770-23_0_5_load_269 | 118 | 0.0018069 | 0.00045284 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2770-23_0_5_load_108 | 119 | 0.0016657 | 0.00041746 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2770-23_0_5_load_109 | 120 | 0.0021995 | 0.00055125 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2770-23_0_5_load_110 | 121 | 0.0024268 | 0.00060821 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2770-23_0_5_load_112 | 122 | 0.0018461 | 0.00046269 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2770-23_0_5_load_121 | 123 | 0.0020635 | 0.00051717 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2770-23_0_5_load_116 | 124 | 0.0046531 | 0.0011662 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2770-23_0_5_load_117 | 125 | 0.0021535 | 0.00053972 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2770-23_0_5_load_122 | 126 | 0.0017101 | 0.0004286 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2770-23_0_5_load_113 | 127 | 0.002011 | 0.00050401 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2770-23_0_5_load_114 | 128 | 0.0018125 | 0.00045427 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2770-23_0_5_load_115 | 129 | 0.0031773 | 0.00079631 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2770-23_0_5_load_210 | 130 | 0.0020216 | 0.00050666 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2770-23_0_5_load_209 | 131 | 0.0022675 | 0.00056828 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2770-23_0_5_load_118 | 132 | 0.0021492 | 0.00053864 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2770-23_0_5_load_119 | 133 | 0.0011483 | 0.0002878 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2770-23_0_5_load_120 | 134 | 0.0024254 | 0.00060786 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2770-23_0_5_load_124 | 135 | 0.001682 | 0.00042154 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2770-23_0_5_load_125 | 136 | 0.0025229 | 0.00063231 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2770-23_0_5_load_123 | 137 | 0.001826 | 0.00045765 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2770-23_0_5_load_128 | 138 | 0.0018284 | 0.00045825 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2770-23_0_5_load_127 | 139 | 0.0018492 | 0.00046344 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2770-23_0_5_load_126 | 140 | 0.002078 | 0.00052079 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2770-23_0_5_load_131 | 141 | 0.0021529 | 0.00053957 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2770-23_0_5_load_132 | 142 | 0.0024506 | 0.00061418 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2770-23_0_5_load_129 | 143 | 0.0022796 | 0.00057132 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2770-23_0_5_load_130 | 144 | 0.0013934 | 0.00034922 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2770-23_0_5_load_133 | 145 | 0.0024507 | 0.00061419 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2770-23_0_5_load_134 | 146 | 0.0016473 | 0.00041285 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2770-23_0_5_load_154 | 148 | 0.00405 | 0.001015 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2770-23_0_5_load_135 | 149 | 0.0027909 | 0.00069946 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2770-23_0_5_load_136 | 150 | 0.0016254 | 0.00040736 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2770-23_0_5_load_137 | 151 | 0.002625 | 0.00065789 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2770-23_0_5_load_138 | 152 | 0.0018837 | 0.00047211 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2770-23_0_5_load_143 | 154 | 0.0043843 | 0.0010988 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2770-23_0_5_load_139 | 155 | 0.0012951 | 0.00032459 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_2770-23_0_5_load_140 | 156 | 0.0035577 | 0.00089163 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_2770-23_0_5_load_142 | 157 | 0.001862 | 0.00046667 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_2770-23_0_5_load_144 | 158 | 0.0012884 | 0.0003229 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_2770-23_0_5_load_151 | 159 | 0.0035573 | 0.00089153 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_2770-23_0_5_load_145 | 160 | 0.0011942 | 0.0002993 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_2770-23_0_5_load_146 | 162 | 0.0013503 | 0.00033843 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_2770-23_0_5_load_164 | 163 | 0.00195 | 0.00048872 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_2770-23_0_5_load_147 | 165 | 0.0039298 | 0.00098491 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_2770-23_0_5_load_149 | 166 | 0.0024511 | 0.00061429 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_2770-23_0_5_load_152 | 168 | 0.0039929 | 0.0010007 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_2770-23_0_5_load_155 | 170 | 0.0028847 | 0.00072298 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_2770-23_0_5_load_156 | 171 | 0.0016007 | 0.00040116 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_2770-23_0_5_load_158 | 172 | 0.00075866 | 0.00019014 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_2770-23_0_5_load_223 | 174 | 0.0019548 | 0.00048993 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_2770-23_0_5_load_161 | 175 | 0.0062769 | 0.0015731 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_2770-23_0_5_load_159 | 176 | 0.001616 | 0.00040501 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_2770-23_0_5_load_160 | 177 | 0.00077802 | 0.00019499 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_2770-23_0_5_load_162 | 178 | 0.0024802 | 0.0006216 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_2770-23_0_5_load_170 | 179 | 0.0023413 | 0.00058677 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_2770-23_0_5_load_224 | 181 | 0.0014129 | 0.00035412 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_2770-23_0_5_load_166 | 182 | 0.0010345 | 0.00025927 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_2770-23_0_5_load_167 | 183 | 0.0018012 | 0.00045142 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_2770-23_0_5_load_168 | 184 | 0.0014747 | 0.0003696 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_2770-23_0_5_load_179 | 185 | 0.0032279 | 0.000809 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_2770-23_0_5_load_169 | 186 | 0.0017347 | 0.00043475 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_2770-23_0_5_load_180 | 187 | 0.0036253 | 0.00090858 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_2770-23_0_5_load_172 | 188 | 0.001071 | 0.00026842 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_2770-23_0_5_load_173 | 189 | 0.0028715 | 0.00071967 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_2770-23_0_5_load_178 | 190 | 0.0032716 | 0.00081993 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_2770-23_0_5_load_175 | 191 | 0.0016492 | 0.00041333 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_2770-23_0_5_load_237 | 192 | 0.0026025 | 0.00065225 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_2770-23_0_5_load_238 | 193 | 0.0019623 | 0.00049181 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_2770-23_0_5_load_181 | 194 | 0.0013603 | 0.00034091 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_2770-23_0_5_load_189 | 195 | 0.0020488 | 0.00051349 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_2770-23_0_5_load_185 | 197 | 0.00082945 | 0.00020788 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_2770-23_0_5_load_186 | 198 | 0.0027304 | 0.00068431 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_2770-23_0_5_load_187 | 199 | 0.0016146 | 0.00040466 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_2770-23_0_5_load_191 | 200 | 0.0034016 | 0.00085253 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_2770-23_0_5_load_196 | 202 | 0.0015345 | 0.00038459 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_2770-23_0_5_load_192 | 203 | 0.0014038 | 0.00035183 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_2770-23_0_5_load_193 | 204 | 0.001964 | 0.00049222 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_2770-23_0_5_load_197 | 206 | 0.002784 | 0.00069773 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_2770-23_0_5_load_198 | 207 | 0.0016874 | 0.0004229 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_2770-23_0_5_load_220 | 208 | 0.001365 | 0.0003421 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_2770-23_0_5_load_199 | 209 | 0.0018876 | 0.00047308 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_2770-23_0_5_load_200 | 210 | 0.0022916 | 0.00057433 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_2770-23_0_5_load_204 | 213 | 0.0030887 | 0.00077411 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_2770-23_0_5_load_201 | 214 | 0.0021047 | 0.00052748 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_2770-23_0_5_load_202 | 215 | 0.0021404 | 0.00053644 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_2770-23_0_5_load_203 | 216 | 0.0022763 | 0.00057049 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_2770-23_0_5_load_205 | 217 | 0.0018149 | 0.00045486 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_2770-23_0_5_load_207 | 218 | 0.0022098 | 0.00055382 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_2770-23_0_5_load_208 | 219 | 0.0020672 | 0.00051809 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_2770-23_0_5_load_272 | 220 | 0.0020529 | 0.0005145 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_2770-23_0_5_load_211 | 222 | 0.002069 | 0.00051855 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_2770-23_0_5_load_212 | 223 | 0.0022199 | 0.00055636 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_2770-23_0_5_load_215 | 224 | 0.0023581 | 0.00059099 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_2770-23_0_5_load_226 | 226 | 0.0019895 | 0.0004986 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_2770-23_0_5_load_227 | 227 | 0.0043011 | 0.0010779 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_2770-23_0_5_load_277 | 228 | 0.0061841 | 0.0015499 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_2770-23_0_5_load_229 | 229 | 0.0017031 | 0.00042684 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_2770-23_0_5_load_230 | 230 | 0.0025033 | 0.00062738 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_2770-23_0_5_load_233 | 231 | 0.0023786 | 0.00059612 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_2770-23_0_5_load_231 | 232 | 0.001976 | 0.00049523 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_2770-23_0_5_load_232 | 233 | 0.0026701 | 0.00066919 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_2770-23_0_5_load_236 | 236 | 0.0019588 | 0.00049093 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_2770-23_0_5_load_275 | 237 | 0.0022126 | 0.00055453 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_2770-23_0_5_load_273 | 238 | 0.0017672 | 0.00044291 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_2770-23_0_5_load_274 | 241 | 0.001334 | 0.00033432 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_2770-23_0_5_load_252 | 242 | 0.0016825 | 0.00042168 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_2770-23_0_5_load_260 | 243 | 0.0035469 | 0.00088893 | 0 | 0 |  | 1 | TRUE | wye
207 | LV_2770-23_0_5_load_261 | 244 | 0.0011808 | 0.00029595 | 0 | 0 |  | 1 | TRUE | wye
208 | LV_2770-23_0_5_load_239 | 245 | 0.001503 | 0.00037669 | 0 | 0 |  | 1 | TRUE | wye
209 | LV_2770-23_0_5_load_240 | 246 | 0.0015915 | 0.00039888 | 0 | 0 |  | 1 | TRUE | wye
210 | LV_2770-23_0_5_load_241 | 247 | 0.0023017 | 0.00057685 | 0 | 0 |  | 1 | TRUE | wye
211 | LV_2770-23_0_5_load_242 | 248 | 0.0016018 | 0.00040144 | 0 | 0 |  | 1 | TRUE | wye
212 | LV_2770-23_0_5_load_243 | 249 | 0.0015839 | 0.00039696 | 0 | 0 |  | 1 | TRUE | wye
213 | LV_2770-23_0_5_load_246 | 252 | 0.0013913 | 0.0003487 | 0 | 0 |  | 1 | TRUE | wye
214 | LV_2770-23_0_5_load_253 | 253 | 0.0039918 | 0.0010004 | 0 | 0 |  | 1 | TRUE | wye
215 | LV_2770-23_0_5_load_251 | 254 | 0.0014949 | 0.00037466 | 0 | 0 |  | 1 | TRUE | wye
216 | LV_2770-23_0_5_load_270 | 255 | 0.0014153 | 0.00035471 | 0 | 0 |  | 1 | TRUE | wye
217 | LV_2770-23_0_5_load_271 | 256 | 0.0039918 | 0.0010004 | 0 | 0 |  | 1 | TRUE | wye
218 | LV_2770-23_0_5_load_247 | 258 | 0.0015552 | 0.00038976 | 0 | 0 |  | 1 | TRUE | wye
219 | LV_2770-23_0_5_load_248 | 259 | 0.0013598 | 0.00034079 | 0 | 0 |  | 1 | TRUE | wye
220 | LV_2770-23_0_5_load_250 | 260 | 0.0016707 | 0.00041872 | 0 | 0 |  | 1 | TRUE | wye
221 | LV_2770-23_0_5_load_257 | 261 | 0.0015717 | 0.00039391 | 0 | 0 |  | 1 | TRUE | wye
222 | LV_2770-23_0_5_load_255 | 262 | 0.0015374 | 0.00038531 | 0 | 0 |  | 1 | TRUE | wye
223 | LV_2770-23_0_5_load_254 | 264 | 0.0015696 | 0.00039339 | 0 | 0 |  | 1 | TRUE | wye
224 | LV_2770-23_0_5_load_256 | 265 | 0.0020181 | 0.00050579 | 0 | 0 |  | 1 | TRUE | wye
225 | LV_2770-23_0_5_load_259 | 266 | 0.0008299 | 0.00020799 | 0 | 0 |  | 1 | TRUE | wye
226 | LV_2770-23_0_5_load_266 | 268 | 0.0016144 | 0.0004046 | 0 | 0 |  | 1 | TRUE | wye
227 | LV_2770-23_0_5_load_279 | 269 | 0.0011438 | 0.00028665 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 197 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2770-23_0_5_line_0 |  | 0 | 1 | 0.0046842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_2770-23_0_5_line_1 |  | 0 | 2 | 0.0052208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_2770-23_0_5_line_2 |  | 1 | 3 | 0.004429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_2770-23_0_5_line_3 |  | 2 | 4 | 0.0093127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_2770-23_0_5_line_4 |  | 3 | 5 | 0.010167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2770-23_0_5_line_5 |  | 4 | 6 | 0.0065961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2770-23_0_5_line_6 |  | 5 | 7 | 0.0062719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2770-23_0_5_line_7 |  | 6 | 8 | 0.018976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2770-23_0_5_line_8 |  | 6 | 9 | 0.010133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2770-23_0_5_line_9 |  | 7 | 10 | 0.0091923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2770-23_0_5_line_10 |  | 8 | 117 | 0.0022615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2770-23_0_5_line_11 |  | 9 | 52 | 0.025175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2770-23_0_5_line_12 |  | 9 | 51 | 0.025539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2770-23_0_5_line_13 |  | 10 | 11 | 0.010496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2770-23_0_5_line_14 |  | 11 | 12 | 0.023222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2770-23_0_5_line_15 |  | 11 | 13 | 0.025012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2770-23_0_5_line_16 |  | 12 | 14 | 0.024339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2770-23_0_5_line_17 |  | 13 | 15 | 0.0033876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2770-23_0_5_line_18 |  | 14 | 191 | 0.020503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2770-23_0_5_line_19 |  | 15 | 189 | 0.028211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_2770-23_0_5_line_20 |  | 16 | 17 | 0.02035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2770-23_0_5_line_21 |  | 16 | 18 | 0.012232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2770-23_0_5_line_22 |  | 17 | 19 | 0.014038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2770-23_0_5_line_23 |  | 18 | 20 | 0.0055372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2770-23_0_5_line_24 |  | 18 | 21 | 0.014145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2770-23_0_5_line_25 |  | 19 | 22 | 0.0049214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2770-23_0_5_line_26 |  | 20 | 23 | 0.030861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2770-23_0_5_line_27 |  | 21 | 24 | 0.01768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2770-23_0_5_line_28 |  | 22 | 25 | 0.0086051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2770-23_0_5_line_29 |  | 23 | 26 | 0.0003987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2770-23_0_5_line_30 |  | 24 | 27 | 0.010873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2770-23_0_5_line_31 |  | 24 | 28 | 0.019058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2770-23_0_5_line_32 |  | 26 | 29 | 0.018353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2770-23_0_5_line_33 |  | 27 | 40 | 0.040087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2770-23_0_5_line_34 |  | 28 | 41 | 0.010028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2770-23_0_5_line_35 |  | 29 | 30 | 0.007773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2770-23_0_5_line_36 |  | 29 | 31 | 0.011813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2770-23_0_5_line_37 |  | 30 | 32 | 0.015975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2770-23_0_5_line_38 |  | 31 | 33 | 0.011797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2770-23_0_5_line_39 |  | 32 | 57 | 0.017222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2770-23_0_5_line_40 |  | 33 | 102 | 0.0078177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2770-23_0_5_line_41 |  | 34 | 35 | 0.00011601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2770-23_0_5_line_42 |  | 34 | 36 | 0.019527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2770-23_0_5_line_43 |  | 35 | 37 | 0.019271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2770-23_0_5_line_44 |  | 37 | 38 | 0.014806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2770-23_0_5_line_45 |  | 38 | 39 | 0.012972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2770-23_0_5_line_46 |  | 39 | 42 | 0.0045832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2770-23_0_5_line_47 |  | 41 | 46 | 0.0051586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2770-23_0_5_line_48 |  | 42 | 43 | 0.00081351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2770-23_0_5_line_49 |  | 43 | 44 | 0.0041749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2770-23_0_5_line_50 |  | 44 | 45 | 0.025609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2770-23_0_5_line_51 |  | 45 | 47 | 0.00054832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2770-23_0_5_line_52 |  | 46 | 49 | 0.0044788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2770-23_0_5_line_53 |  | 47 | 48 | 0.0013933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2770-23_0_5_line_54 |  | 48 | 197 | 0.016384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2770-23_0_5_line_55 |  | 49 | 50 | 0.012861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2770-23_0_5_line_56 |  | 50 | 51 | 0.00034892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2770-23_0_5_line_57 |  | 52 | 116 | 0.0085924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2770-23_0_5_line_58 |  | 53 | 54 | 0.019112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2770-23_0_5_line_59 |  | 54 | 55 | 0.016459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2770-23_0_5_line_60 |  | 54 | 56 | 0.0069436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2770-23_0_5_line_61 |  | 55 | 58 | 0.0040158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2770-23_0_5_line_62 |  | 56 | 59 | 0.0025049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2770-23_0_5_line_63 |  | 57 | 60 | 0.016118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2770-23_0_5_line_64 |  | 59 | 61 | 0.0046964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2770-23_0_5_line_65 |  | 61 | 91 | 0.0096769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2770-23_0_5_line_66 |  | 62 | 63 | 0.025902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2770-23_0_5_line_67 |  | 62 | 64 | 0.02253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2770-23_0_5_line_68 |  | 63 | 65 | 0.00024846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2770-23_0_5_line_69 |  | 64 | 66 | 0.015288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2770-23_0_5_line_70 |  | 64 | 67 | 0.026053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2770-23_0_5_line_71 |  | 65 | 68 | 0.033098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2770-23_0_5_line_72 |  | 66 | 69 | 0.024576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2770-23_0_5_line_73 |  | 66 | 70 | 0.017611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2770-23_0_5_line_74 |  | 68 | 71 | 0.044751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2770-23_0_5_line_75 |  | 69 | 72 | 0.0074098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2770-23_0_5_line_76 |  | 70 | 73 | 0.00031445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2770-23_0_5_line_77 |  | 71 | 78 | 0.035179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2770-23_0_5_line_78 |  | 72 | 77 | 0.016397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2770-23_0_5_line_79 |  | 73 | 74 | 0.025407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2770-23_0_5_line_80 |  | 74 | 75 | 0.027403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2770-23_0_5_line_81 |  | 75 | 76 | 0.025645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2770-23_0_5_line_82 |  | 76 | 91 | 0.005702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2770-23_0_5_line_83 |  | 77 | 81 | 0.014993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2770-23_0_5_line_84 |  | 78 | 79 | 0.044557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2770-23_0_5_line_85 |  | 79 | 80 | 0.016946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2770-23_0_5_line_86 |  | 80 | 111 | 0.00072552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2770-23_0_5_line_87 |  | 81 | 82 | 0.009846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2770-23_0_5_line_88 |  | 81 | 83 | 0.010337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2770-23_0_5_line_89 |  | 82 | 92 | 0.014337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2770-23_0_5_line_90 |  | 82 | 93 | 0.00799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2770-23_0_5_line_91 |  | 83 | 86 | 0.021992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2770-23_0_5_line_92 |  | 84 | 85 | 0.016231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2770-23_0_5_line_93 |  | 84 | 86 | 0.00070452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2770-23_0_5_line_94 |  | 85 | 87 | 0.0046882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2770-23_0_5_line_95 |  | 87 | 88 | 0.016888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2770-23_0_5_line_96 |  | 88 | 89 | 0.0024689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2770-23_0_5_line_97 |  | 89 | 90 | 0.017492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2770-23_0_5_line_98 |  | 92 | 97 | 0.021598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2770-23_0_5_line_99 |  | 93 | 94 | 0.022339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2770-23_0_5_line_100 |  | 94 | 95 | 0.0016201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2770-23_0_5_line_101 |  | 95 | 96 | 0.010014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2770-23_0_5_line_102 |  | 97 | 98 | 0.005237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2770-23_0_5_line_103 |  | 98 | 196 | 0.023859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2770-23_0_5_line_104 |  | 99 | 100 | 0.019636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2770-23_0_5_line_105 |  | 99 | 101 | 0.018857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2770-23_0_5_line_106 |  | 101 | 106 | 0.02567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2770-23_0_5_line_107 |  | 102 | 103 | 0.0056528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2770-23_0_5_line_108 |  | 103 | 104 | 0.008738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2770-23_0_5_line_109 |  | 103 | 105 | 0.014097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2770-23_0_5_line_110 |  | 104 | 109 | 0.045009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2770-23_0_5_line_111 |  | 105 | 108 | 0.0046545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2770-23_0_5_line_112 |  | 106 | 107 | 0.017516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2770-23_0_5_line_113 |  | 107 | 110 | 0.042212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2770-23_0_5_line_114 |  | 110 | 111 | 0.039694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2770-23_0_5_line_115 |  | 112 | 113 | 0.0049901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2770-23_0_5_line_116 |  | 112 | 114 | 0.0079324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2770-23_0_5_line_117 |  | 113 | 115 | 0.010066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2770-23_0_5_line_118 |  | 115 | 116 | 0.0099597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2770-23_0_5_line_119 |  | 117 | 118 | 0.0029909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2770-23_0_5_line_120 |  | 118 | 255 | 0.021314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2770-23_0_5_line_121 |  | 119 | 120 | 0.010375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2770-23_0_5_line_122 |  | 119 | 121 | 0.014245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2770-23_0_5_line_123 |  | 121 | 122 | 0.015407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2770-23_0_5_line_124 |  | 122 | 123 | 0.0079338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2770-23_0_5_line_125 |  | 123 | 126 | 0.0082677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2770-23_0_5_line_126 |  | 124 | 125 | 0.04344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2770-23_0_5_line_127 |  | 125 | 132 | 0.015609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2770-23_0_5_line_128 |  | 126 | 137 | 0.014655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2770-23_0_5_line_129 |  | 127 | 128 | 0.023666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2770-23_0_5_line_130 |  | 128 | 129 | 0.0029528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2770-23_0_5_line_131 |  | 129 | 130 | 0.013133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2770-23_0_5_line_132 |  | 130 | 131 | 0.012036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2770-23_0_5_line_133 |  | 131 | 219 | 0.0036245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2770-23_0_5_line_134 |  | 132 | 133 | 0.017617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2770-23_0_5_line_135 |  | 133 | 134 | 0.0064226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2770-23_0_5_line_136 |  | 134 | 135 | 0.023518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2770-23_0_5_line_137 |  | 135 | 136 | 0.0079407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2770-23_0_5_line_138 |  | 136 | 140 | 0.021579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2770-23_0_5_line_139 |  | 137 | 138 | 0.00233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2770-23_0_5_line_140 |  | 138 | 139 | 0.00034559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2770-23_0_5_line_141 |  | 139 | 143 | 0.014169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2770-23_0_5_line_142 |  | 140 | 141 | 0.022393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2770-23_0_5_line_143 |  | 141 | 142 | 0.029167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2770-23_0_5_line_144 |  | 142 | 147 | 0.020938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2770-23_0_5_line_145 |  | 143 | 144 | 0.0030482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2770-23_0_5_line_146 |  | 144 | 145 | 0.0024987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2770-23_0_5_line_147 |  | 145 | 146 | 0.021603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2770-23_0_5_line_148 |  | 146 | 149 | 1.2366e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2770-23_0_5_line_149 |  | 147 | 148 | 0.045019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2770-23_0_5_line_150 |  | 148 | 167 | 0.031943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_2770-23_0_5_line_151 |  | 149 | 150 | 0.019843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_2770-23_0_5_line_152 |  | 150 | 151 | 0.0070457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2770-23_0_5_line_153 |  | 151 | 152 | 0.0037875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_2770-23_0_5_line_154 |  | 152 | 153 | 0.0056907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_2770-23_0_5_line_155 |  | 153 | 154 | 0.0193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_2770-23_0_5_line_156 |  | 153 | 155 | 0.016059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_2770-23_0_5_line_157 |  | 154 | 159 | 0.0013726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_2770-23_0_5_line_158 |  | 155 | 156 | 0.024648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_2770-23_0_5_line_159 |  | 156 | 157 | 8.2935e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_2770-23_0_5_line_160 |  | 157 | 158 | 0.00087316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_2770-23_0_5_line_161 |  | 158 | 160 | 0.012125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_2770-23_0_5_line_162 |  | 159 | 161 | 0.020623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_2770-23_0_5_line_163 |  | 160 | 162 | 0.015746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_2770-23_0_5_line_164 |  | 161 | 167 | 0.00248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_2770-23_0_5_line_165 |  | 161 | 165 | 0.016175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_2770-23_0_5_line_166 |  | 162 | 163 | 0.021147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_2770-23_0_5_line_167 |  | 163 | 164 | 0.0054722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_2770-23_0_5_line_168 |  | 164 | 182 | 0.012562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
169 | LV_2770-23_0_5_line_169 |  | 164 | 183 | 0.02132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
170 | LV_2770-23_0_5_line_170 |  | 165 | 166 | 0.0081604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_2770-23_0_5_line_171 |  | 167 | 168 | 0.018654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_2770-23_0_5_line_172 |  | 168 | 169 | 0.017823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_2770-23_0_5_line_173 |  | 169 | 170 | 0.028265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_2770-23_0_5_line_174 |  | 169 | 171 | 0.012875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_2770-23_0_5_line_175 |  | 172 | 173 | 0.018684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_2770-23_0_5_line_176 |  | 173 | 174 | 0.0033632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_2770-23_0_5_line_177 |  | 173 | 175 | 0.030851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_2770-23_0_5_line_178 |  | 174 | 181 | 0.017587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_2770-23_0_5_line_179 |  | 175 | 176 | 0.027021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_2770-23_0_5_line_180 |  | 176 | 177 | 0.017133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_2770-23_0_5_line_181 |  | 177 | 178 | 0.014093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_2770-23_0_5_line_182 |  | 178 | 179 | 0.0082808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_2770-23_0_5_line_183 |  | 179 | 180 | 0.018044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_2770-23_0_5_line_184 |  | 180 | 190 | 0.014752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_2770-23_0_5_line_185 |  | 180 | 191 | 0.022642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_2770-23_0_5_line_186 |  | 181 | 225 | 0.019704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_2770-23_0_5_line_187 |  | 182 | 184 | 0.011313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
188 | LV_2770-23_0_5_line_188 |  | 183 | 185 | 0.006399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
189 | LV_2770-23_0_5_line_189 |  | 184 | 186 | 0.012851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
190 | LV_2770-23_0_5_line_190 |  | 185 | 187 | 0.021361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
191 | LV_2770-23_0_5_line_191 |  | 186 | 188 | 0.0025021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
192 | LV_2770-23_0_5_line_192 |  | 187 | 194 | 0.0016046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
193 | LV_2770-23_0_5_line_193 |  | 188 | 189 | 0.021363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
194 | LV_2770-23_0_5_line_194 |  | 190 | 192 | 0.026141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_2770-23_0_5_line_195 |  | 192 | 193 | 0.020793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_2770-23_0_5_line_196 |  | 194 | 195 | 0.0094116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
197 | LV_2770-23_0_5_line_197 |  | 195 | 196 | 0.030642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
198 | LV_2770-23_0_5_line_198 |  | 196 | 200 | 0.022151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_2770-23_0_5_line_199 |  | 196 | 199 | 0.021962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
200 | LV_2770-23_0_5_line_200 |  | 197 | 198 | 0.0044292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
201 | LV_2770-23_0_5_line_201 |  | 198 | 199 | 0.010821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
202 | LV_2770-23_0_5_line_202 |  | 200 | 201 | 0.016739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_2770-23_0_5_line_203 |  | 201 | 202 | 0.014528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_2770-23_0_5_line_204 |  | 201 | 203 | 0.0067752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_2770-23_0_5_line_205 |  | 202 | 208 | 0.0058783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_2770-23_0_5_line_206 |  | 203 | 204 | 0.0048996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_2770-23_0_5_line_207 |  | 204 | 205 | 0.0064514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_2770-23_0_5_line_208 |  | 205 | 206 | 0.015983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
209 | LV_2770-23_0_5_line_209 |  | 205 | 207 | 0.018535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_2770-23_0_5_line_210 |  | 206 | 209 | 0.016529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
211 | LV_2770-23_0_5_line_211 |  | 209 | 210 | 0.018189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_2770-23_0_5_line_212 |  | 210 | 211 | 0.018112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_2770-23_0_5_line_213 |  | 211 | 212 | 0.005059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_2770-23_0_5_line_214 |  | 211 | 213 | 0.019993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_2770-23_0_5_line_215 |  | 212 | 220 | 0.017538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
216 | LV_2770-23_0_5_line_216 |  | 212 | 221 | 0.020603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
217 | LV_2770-23_0_5_line_217 |  | 213 | 215 | 0.0019001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_2770-23_0_5_line_218 |  | 214 | 215 | 0.027404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_2770-23_0_5_line_219 |  | 214 | 216 | 0.012369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_2770-23_0_5_line_220 |  | 216 | 217 | 0.016214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_2770-23_0_5_line_221 |  | 217 | 218 | 0.0040396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_2770-23_0_5_line_222 |  | 218 | 219 | 0.012206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_2770-23_0_5_line_223 |  | 221 | 224 | 0.018224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_2770-23_0_5_line_224 |  | 221 | 223 | 0.0046154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_2770-23_0_5_line_225 |  | 222 | 223 | 0.015547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
226 | LV_2770-23_0_5_line_226 |  | 225 | 226 | 0.01366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_2770-23_0_5_line_227 |  | 225 | 227 | 0.019174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_2770-23_0_5_line_228 |  | 226 | 228 | 0.10297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_2770-23_0_5_line_229 |  | 227 | 229 | 0.023303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_2770-23_0_5_line_230 |  | 229 | 230 | 0.009848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_2770-23_0_5_line_231 |  | 230 | 231 | 0.003645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_2770-23_0_5_line_232 |  | 231 | 232 | 0.029595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
233 | LV_2770-23_0_5_line_233 |  | 232 | 233 | 0.035703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_2770-23_0_5_line_234 |  | 234 | 235 | 0.009257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
235 | LV_2770-23_0_5_line_235 |  | 234 | 236 | 0.056146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_2770-23_0_5_line_236 |  | 235 | 237 | 0.020345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_2770-23_0_5_line_237 |  | 235 | 238 | 0.0022712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_2770-23_0_5_line_238 |  | 236 | 239 | 0.0073705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_2770-23_0_5_line_239 |  | 236 | 240 | 0.055887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_2770-23_0_5_line_240 |  | 238 | 241 | 0.016556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_2770-23_0_5_line_241 |  | 239 | 242 | 0.014046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_2770-23_0_5_line_242 |  | 240 | 243 | 0.018104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
243 | LV_2770-23_0_5_line_243 |  | 242 | 257 | 0.010612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
244 | LV_2770-23_0_5_line_244 |  | 243 | 244 | 0.047626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
245 | LV_2770-23_0_5_line_245 |  | 245 | 246 | 0.010595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
246 | LV_2770-23_0_5_line_246 |  | 246 | 247 | 0.0046359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
247 | LV_2770-23_0_5_line_247 |  | 247 | 248 | 0.0053839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
248 | LV_2770-23_0_5_line_248 |  | 248 | 249 | 0.010441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
249 | LV_2770-23_0_5_line_249 |  | 249 | 250 | 0.020194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
250 | LV_2770-23_0_5_line_250 |  | 250 | 251 | 0.006777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
251 | LV_2770-23_0_5_line_251 |  | 250 | 252 | 0.010656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
252 | LV_2770-23_0_5_line_252 |  | 251 | 253 | 0.020812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_2770-23_0_5_line_253 |  | 251 | 254 | 0.01588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_2770-23_0_5_line_254 |  | 252 | 255 | 0.0046734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
255 | LV_2770-23_0_5_line_255 |  | 253 | 256 | 0.014394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
256 | LV_2770-23_0_5_line_256 |  | 254 | 257 | 0.017908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
257 | LV_2770-23_0_5_line_257 |  | 256 | 263 | 0.0098901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
258 | LV_2770-23_0_5_line_258 |  | 257 | 258 | 0.019205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
259 | LV_2770-23_0_5_line_259 |  | 258 | 259 | 0.0051696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
260 | LV_2770-23_0_5_line_260 |  | 259 | 260 | 0.011684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
261 | LV_2770-23_0_5_line_261 |  | 260 | 261 | 0.0074183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
262 | LV_2770-23_0_5_line_262 |  | 261 | 262 | 0.0090925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
263 | LV_2770-23_0_5_line_263 |  | 262 | 264 | 0.010466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
264 | LV_2770-23_0_5_line_264 |  | 263 | 267 | 0.017544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
265 | LV_2770-23_0_5_line_265 |  | 263 | 270 | 0.030802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
266 | LV_2770-23_0_5_line_266 |  | 264 | 265 | 0.005087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
267 | LV_2770-23_0_5_line_267 |  | 266 | 267 | 0.0096317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
268 | LV_2770-23_0_5_line_268 |  | 267 | 268 | 0.012714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
269 | LV_2770-23_0_5_line_269 |  | 269 | 270 | 0.020112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2770-23_0_5_trafo_185 | 0.63 MVA 20/0.4 kV | 271 | 197 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2615274.4738 | 1263502.9242 | 2615269.9514 | 1263504.1448
1 | 2615274.4738 | 1263502.9242 | 2615279.5142 | 1263501.5636
2 | 2615265.6754 | 1263505.299 | 2615269.9514 | 1263504.1448
3 | 2615279.5142 | 1263501.5636 | 2615288.5051 | 1263499.1368
4 | 2615265.6754 | 1263505.299 | 2615261.2512 | 1263506.4932 | 2615255.9654 | 1263508.2944
5 | 2615294.8733 | 1263497.4179 | 2615288.5051 | 1263499.1368
6 | 2615255.9654 | 1263508.2944 | 2615250.0287 | 1263510.3174
7 | 2615294.8733 | 1263497.4179 | 2615291.4856 | 1263482.2098 | 2615290.7561 | 1263478.8936
8 | 2615304.9392 | 1263496.0207 | 2615294.8733 | 1263497.4179
9 | 2615241.3277 | 1263513.2824 | 2615250.0287 | 1263510.3174
10 | 2615290.7561 | 1263478.8936 | 2615290.2702 | 1263476.6849
11 | 2615304.9392 | 1263496.0207 | 2615320.0673 | 1263494.2362 | 2615329.9784 | 1263495.017
12 | 2615304.9392 | 1263496.0207 | 2615306.9661 | 1263504.4094 | 2615315.4305 | 1263519.0476
13 | 2615231.3922 | 1263516.668 | 2615241.3277 | 1263513.2824
14 | 2615231.3922 | 1263516.668 | 2615224.2482 | 1263512.38 | 2615209.4384 | 1263510.8388
15 | 2615231.3922 | 1263516.668 | 2615208.007 | 1263525.5412
16 | 2615209.4384 | 1263510.8388 | 2615185.2306 | 1263508.3194
17 | 2615204.8397 | 1263526.743 | 2615208.007 | 1263525.5412
18 | 2615164.8381 | 1263506.1972 | 2615185.2306 | 1263508.3194
19 | 2615178.4632 | 1263536.7512 | 2615204.8397 | 1263526.743
20 | 2615345.8885 | 1263597.6178 | 2615327.8811 | 1263607.0965
21 | 2615356.7121 | 1263591.9204 | 2615345.8885 | 1263597.6178
22 | 2615315.4593 | 1263613.6351 | 2615327.8811 | 1263607.0965
23 | 2615356.7121 | 1263591.9204 | 2615359.362 | 1263596.7823
24 | 2615356.7121 | 1263591.9204 | 2615349.9186 | 1263579.5135
25 | 2615311.1044 | 1263615.9275 | 2615315.4593 | 1263613.6351
26 | 2615374.1312 | 1263623.8798 | 2615359.362 | 1263596.7823
27 | 2615341.4275 | 1263564.0061 | 2615349.9186 | 1263579.5135
28 | 2615303.4898 | 1263619.9357 | 2615311.1044 | 1263615.9275
29 | 2615374.1312 | 1263623.8798 | 2615374.322 | 1263624.2299
30 | 2615341.4275 | 1263564.0061 | 2615345.0474 | 1263559.2455 | 2615349.6511 | 1263557.5903
31 | 2615341.4275 | 1263564.0061 | 2615331.8873 | 1263547.5075
32 | 2615383.1051 | 1263640.3444 | 2615374.322 | 1263624.2299
33 | 2615387.2838 | 1263543.7937 | 2615382.1977 | 1263545.888 | 2615349.6511 | 1263557.5903
34 | 2615326.8674 | 1263538.8262 | 2615331.8873 | 1263547.5075
35 | 2615383.1051 | 1263640.3444 | 2615376.6019 | 1263644.6305
36 | 2615383.1051 | 1263640.3444 | 2615392.9955 | 1263633.8842
37 | 2615376.6019 | 1263644.6305 | 2615386.0003 | 1263657.5477
38 | 2615392.9955 | 1263633.8842 | 2615402.8719 | 1263627.433
39 | 2615386.0003 | 1263657.5477 | 2615396.1328 | 1263671.4736
40 | 2615402.8719 | 1263627.433 | 2615409.4171 | 1263623.1578
41 | 2615293.0811 | 1263585.8447 | 2615292.9753 | 1263585.8924
42 | 2615310.8769 | 1263577.8061 | 2615293.0811 | 1263585.8447
43 | 2615275.4314 | 1263593.8649 | 2615277.5231 | 1263592.8724 | 2615292.9753 | 1263585.8924
44 | 2615275.4314 | 1263593.8649 | 2615262.0554 | 1263600.2123
45 | 2615250.336 | 1263605.7736 | 2615262.0554 | 1263600.2123
46 | 2615246.1953 | 1263607.7385 | 2615250.336 | 1263605.7736
47 | 2615326.8674 | 1263538.8262 | 2615324.2851 | 1263534.3605
48 | 2615246.1953 | 1263607.7385 | 2615245.4604 | 1263608.0873
49 | 2615245.4604 | 1263608.0873 | 2615242.24 | 1263609.6154 | 2615241.6871 | 1263609.874
50 | 2615218.4897 | 1263620.7241 | 2615241.6871 | 1263609.874
51 | 2615218.4897 | 1263620.7241 | 2615217.993 | 1263620.9564
52 | 2615322.0431 | 1263530.4832 | 2615324.2851 | 1263534.3605
53 | 2615217.993 | 1263620.9564 | 2615216.7309 | 1263621.5467
54 | 2615216.7309 | 1263621.5467 | 2615213.9403 | 1263622.852 | 2615202.3101 | 1263629.3105
55 | 2615322.0431 | 1263530.4832 | 2615315.6052 | 1263519.3497
56 | 2615315.6052 | 1263519.3497 | 2615315.4305 | 1263519.0476
57 | 2615329.9784 | 1263495.017 | 2615338.5442 | 1263495.6919
58 | 2615332.7505 | 1263677.8845 | 2615347.4479 | 1263665.6667
59 | 2615332.7505 | 1263677.8845 | 2615342.3297 | 1263691.269
60 | 2615332.7505 | 1263677.8845 | 2615327.4109 | 1263682.3232
61 | 2615344.6669 | 1263694.5346 | 2615342.3297 | 1263691.269
62 | 2615325.4847 | 1263683.9244 | 2615327.4109 | 1263682.3232
63 | 2615396.1328 | 1263671.4736 | 2615405.6157 | 1263684.5067
64 | 2615321.8731 | 1263686.9266 | 2615325.4847 | 1263683.9244
65 | 2615314.4316 | 1263693.1126 | 2615321.8731 | 1263686.9266
66 | 2615237.348 | 1263785.8494 | 2615252.8498 | 1263806.6002
67 | 2615223.8639 | 1263767.7996 | 2615237.348 | 1263785.8494
68 | 2615252.8498 | 1263806.6002 | 2615252.9985 | 1263806.7993
69 | 2615223.8639 | 1263767.7996 | 2615229.6898 | 1263763.2447 | 2615235.9307 | 1263758.3685
70 | 2615223.8639 | 1263767.7996 | 2615203.7502 | 1263784.3591
71 | 2615272.8069 | 1263833.315 | 2615252.9985 | 1263806.7993
72 | 2615235.9307 | 1263758.3685 | 2615220.8083 | 1263738.9963
73 | 2615235.9307 | 1263758.3685 | 2615249.4736 | 1263747.1106
74 | 2615272.8069 | 1263833.315 | 2615307.5965 | 1263805.1663
75 | 2615220.8083 | 1263738.9963 | 2615216.2488 | 1263733.1554
76 | 2615249.7154 | 1263746.9096 | 2615249.4736 | 1263747.1106
77 | 2615307.5965 | 1263805.1663 | 2615342.1517 | 1263811.7612
78 | 2615206.1592 | 1263720.2304 | 2615216.2488 | 1263733.1554
79 | 2615249.7154 | 1263746.9096 | 2615269.2533 | 1263730.6682
80 | 2615290.3259 | 1263713.1511 | 2615269.2533 | 1263730.6682
81 | 2615290.3259 | 1263713.1511 | 2615310.0467 | 1263696.7576
82 | 2615310.0467 | 1263696.7576 | 2615314.4316 | 1263693.1126
83 | 2615196.9334 | 1263708.4119 | 2615206.1592 | 1263720.2304
84 | 2615342.1517 | 1263811.7612 | 2615386.3081 | 1263817.7236
85 | 2615401.0678 | 1263815.2476 | 2615392.2228 | 1263812.7203 | 2615386.3081 | 1263817.7236
86 | 2615401.7654 | 1263815.4469 | 2615401.0678 | 1263815.2476
87 | 2615204.9015 | 1263702.5949 | 2615196.9334 | 1263708.4119
88 | 2615196.9334 | 1263708.4119 | 2615188.6569 | 1263714.604
89 | 2615204.9015 | 1263702.5949 | 2615196.9145 | 1263690.6882
90 | 2615204.9015 | 1263702.5949 | 2615211.3535 | 1263697.8819
91 | 2615188.6569 | 1263714.604 | 2615171.0481 | 1263727.7781
92 | 2615170.484 | 1263728.2002 | 2615157.4875 | 1263737.9236
93 | 2615170.484 | 1263728.2002 | 2615171.0481 | 1263727.7781
94 | 2615153.7336 | 1263740.732 | 2615157.4875 | 1263737.9236
95 | 2615153.7336 | 1263740.732 | 2615140.2112 | 1263750.8489
96 | 2615138.2343 | 1263752.3279 | 2615140.2112 | 1263750.8489
97 | 2615138.2343 | 1263752.3279 | 2615129.2176 | 1263759.0739 | 2615124.6104 | 1263763.2697
98 | 2615196.9145 | 1263690.6882 | 2615184.8828 | 1263672.7516
99 | 2615211.3535 | 1263697.8819 | 2615212.3187 | 1263697.1769 | 2615229.4758 | 1263684.8199
100 | 2615230.7904 | 1263683.8731 | 2615229.4758 | 1263684.8199
101 | 2615238.9161 | 1263678.0207 | 2615230.7904 | 1263683.8731
102 | 2615181.9654 | 1263668.4025 | 2615184.8828 | 1263672.7516
103 | 2615170.1181 | 1263647.9572 | 2615171.1464 | 1263652.2739 | 2615181.9654 | 1263668.4025
104 | 2615435.4382 | 1263725.4945 | 2615419.9898 | 1263737.6739
105 | 2615435.4382 | 1263725.4945 | 2615446.533 | 1263740.742
106 | 2615461.6364 | 1263761.4986 | 2615446.533 | 1263740.742
107 | 2615414.1498 | 1263620.0665 | 2615409.4171 | 1263623.1578
108 | 2615414.1498 | 1263620.0665 | 2615421.4829 | 1263615.2822
109 | 2615414.1498 | 1263620.0665 | 2615421.6196 | 1263632.0219
110 | 2615421.4829 | 1263615.2822 | 2615401.5851 | 1263574.9099
111 | 2615424.0859 | 1263635.9693 | 2615421.6196 | 1263632.0219
112 | 2615461.6364 | 1263761.4986 | 2615471.9474 | 1263775.6797
113 | 2615439.3121 | 1263802.5689 | 2615471.9474 | 1263775.6797
114 | 2615439.3121 | 1263802.5689 | 2615401.7654 | 1263815.4469
115 | 2615358.5085 | 1263497.2647 | 2615363.4832 | 1263497.6566
116 | 2615371.391 | 1263498.2796 | 2615363.4832 | 1263497.6566
117 | 2615358.5085 | 1263497.2647 | 2615348.4731 | 1263496.4741
118 | 2615348.4731 | 1263496.4741 | 2615338.5442 | 1263495.6919
119 | 2615290.2702 | 1263476.6849 | 2615289.6277 | 1263473.7638
120 | 2615285.0488 | 1263452.9478 | 2615289.6277 | 1263473.7638
121 | 2614933.9969 | 1263701.7109 | 2614926.7704 | 1263709.1553
122 | 2614933.9969 | 1263701.7109 | 2614942.8945 | 1263692.545 | 2614943.9916 | 1263691.566
123 | 2614955.4872 | 1263681.3077 | 2614943.9916 | 1263691.566
124 | 2614955.4872 | 1263681.3077 | 2614961.4067 | 1263676.0253
125 | 2614967.5754 | 1263670.5206 | 2614961.4067 | 1263676.0253
126 | 2614882.0898 | 1263716.1018 | 2614878.8278 | 1263709.3624 | 2614877.0599 | 1263702.5978 | 2614875.869 | 1263696.9687 | 2614875.172 | 1263689.5618 | 2614877.4525 | 1263678.1708 | 2614878.6902 | 1263674.2085
127 | 2614878.6902 | 1263674.2085 | 2614880.9298 | 1263667.0385 | 2614885.1442 | 1263660.1243
128 | 2614967.5754 | 1263670.5206 | 2614978.3796 | 1263660.8793 | 2614978.5092 | 1263660.7631
129 | 2614992.5578 | 1263724.3863 | 2614975.6519 | 1263740.9472
130 | 2614994.7106 | 1263722.3661 | 2614993.4801 | 1263723.4828 | 2614992.5578 | 1263724.3863
131 | 2614994.7106 | 1263722.3661 | 2615004.4359 | 1263713.5411
132 | 2615013.3489 | 1263705.4532 | 2615004.4359 | 1263713.5411
133 | 2615013.3489 | 1263705.4532 | 2615016.033 | 1263703.0175
134 | 2614894.3134 | 1263645.0816 | 2614885.1442 | 1263660.1243
135 | 2614894.3134 | 1263645.0816 | 2614897.6562 | 1263639.5974
136 | 2614897.6562 | 1263639.5974 | 2614899.0044 | 1263637.3856 | 2614911.1471 | 1263620.3413
137 | 2614911.1471 | 1263620.3413 | 2614915.7546 | 1263613.874
138 | 2614915.7546 | 1263613.874 | 2614928.2757 | 1263596.2985
139 | 2614980.2447 | 1263659.2084 | 2614978.5092 | 1263660.7631
140 | 2614980.5021 | 1263658.9778 | 2614980.2447 | 1263659.2084
141 | 2614991.0554 | 1263649.5234 | 2614980.5021 | 1263658.9778
142 | 2614941.7652 | 1263578.4685 | 2614938.5715 | 1263581.8467 | 2614928.2757 | 1263596.2985
143 | 2614961.8026 | 1263557.2735 | 2614941.7652 | 1263578.4685
144 | 2614976.1866 | 1263542.0585 | 2614961.8026 | 1263557.2735
145 | 2614991.0554 | 1263649.5234 | 2614993.3258 | 1263647.4895
146 | 2614995.1868 | 1263645.8222 | 2614993.3258 | 1263647.4895
147 | 2615012.0655 | 1263632.3704 | 2615000.9044 | 1263640.7 | 2614995.1868 | 1263645.8222
148 | 2615012.0754 | 1263632.363 | 2615012.0655 | 1263632.3704
149 | 2614976.1866 | 1263542.0585 | 2614993.8164 | 1263557.6137 | 2615013.1173 | 1263548.1241
150 | 2615027.9659 | 1263574.9342 | 2615014.3127 | 1263547.5363 | 2615013.1173 | 1263548.1241
151 | 2615012.0754 | 1263632.363 | 2615015.6337 | 1263629.7074 | 2615028.1437 | 1263620.7218 | 2615028.1437 | 1263620.7218
152 | 2615034.4875 | 1263617.6562 | 2615028.1437 | 1263620.7218
153 | 2615037.8977 | 1263616.0083 | 2615034.4875 | 1263617.6562
154 | 2615043.0215 | 1263613.5323 | 2615037.8977 | 1263616.0083
155 | 2615043.0215 | 1263613.5323 | 2615034.9421 | 1263596.0051
156 | 2615043.0215 | 1263613.5323 | 2615057.4738 | 1263606.5314
157 | 2615034.3674 | 1263594.7586 | 2615034.9421 | 1263596.0051
158 | 2615057.4738 | 1263606.5314 | 2615064.2338 | 1263603.2567 | 2615079.8949 | 1263596.2995
159 | 2615079.9707 | 1263596.2659 | 2615079.8949 | 1263596.2995
160 | 2615080.7687 | 1263595.9114 | 2615079.9707 | 1263596.2659
161 | 2615091.7725 | 1263590.8268 | 2615088.573 | 1263592.4444 | 2615080.7687 | 1263595.9114
162 | 2615025.7338 | 1263576.0293 | 2615034.3674 | 1263594.7586
163 | 2615105.8243 | 1263583.7222 | 2615091.7725 | 1263590.8268
164 | 2615025.7338 | 1263576.0293 | 2615027.9659 | 1263574.9342
165 | 2615025.7338 | 1263576.0293 | 2615011.278 | 1263583.287
166 | 2615105.8243 | 1263583.7222 | 2615112.5768 | 1263580.3082 | 2615122.9655 | 1263571.5614
167 | 2615127.1515 | 1263568.0369 | 2615122.9655 | 1263571.5614
168 | 2615127.1515 | 1263568.0369 | 2615136.8565 | 1263560.0614
169 | 2615127.1515 | 1263568.0369 | 2615137.2471 | 1263586.8153
170 | 2615003.9852 | 1263586.9485 | 2615011.278 | 1263583.287
171 | 2615027.9659 | 1263574.9342 | 2615044.6948 | 1263566.6808
172 | 2615060.6788 | 1263558.7949 | 2615044.6948 | 1263566.6808
173 | 2615060.6788 | 1263558.7949 | 2615048.7116 | 1263533.1879
174 | 2615072.2542 | 1263553.087 | 2615060.6788 | 1263558.7949
175 | 2615028.5359 | 1263486.6859 | 2615015.7001 | 1263500.263
176 | 2615028.5359 | 1263486.6859 | 2615030.2036 | 1263483.7654
177 | 2615028.5359 | 1263486.6859 | 2615045.4306 | 1263492.1547 | 2615055.7503 | 1263494.5937 | 2615058.2258 | 1263494.8585
178 | 2615030.2036 | 1263483.7654 | 2615033.2717 | 1263478.3922 | 2615036.2581 | 1263470.9169 | 2615038.2674 | 1263468.2367
179 | 2615058.2258 | 1263494.8585 | 2615085.0934 | 1263497.7324
180 | 2615085.0934 | 1263497.7324 | 2615102.129 | 1263499.5546
181 | 2615116.1425 | 1263501.0536 | 2615102.129 | 1263499.5546
182 | 2615124.3764 | 1263501.9344 | 2615116.1425 | 1263501.0536
183 | 2615142.3182 | 1263503.8535 | 2615124.3764 | 1263501.9344
184 | 2615142.3182 | 1263503.8535 | 2615144.2569 | 1263499.7001 | 2615148.2828 | 1263495.1739 | 2615152.0301 | 1263493.485
185 | 2615142.3182 | 1263503.8535 | 2615164.8381 | 1263506.1972
186 | 2615056.2696 | 1263462.1059 | 2615054.0775 | 1263462.2338 | 2615045.2012 | 1263463.8235 | 2615039.9687 | 1263465.9673 | 2615038.2674 | 1263468.2367
187 | 2615136.8565 | 1263560.0614 | 2615144.3218 | 1263553.9265 | 2615145.7367 | 1263553.0766
188 | 2615140.2772 | 1263592.4514 | 2615137.2471 | 1263586.8153
189 | 2615156.7528 | 1263546.4593 | 2615145.7367 | 1263553.0766
190 | 2615140.2772 | 1263592.4514 | 2615150.3921 | 1263611.2656
191 | 2615156.7528 | 1263546.4593 | 2615158.8977 | 1263545.1709
192 | 2615151.1519 | 1263612.679 | 2615150.3921 | 1263611.2656
193 | 2615178.4632 | 1263536.7512 | 2615163.3985 | 1263542.4673 | 2615158.8977 | 1263545.1709
194 | 2615152.0301 | 1263493.485 | 2615175.8629 | 1263482.744
195 | 2615194.8199 | 1263474.2005 | 2615175.8629 | 1263482.744
196 | 2615155.6085 | 1263620.9685 | 2615151.1519 | 1263612.679
197 | 2615170.1181 | 1263647.9572 | 2615155.6085 | 1263620.9685
198 | 2615170.1181 | 1263647.9572 | 2615151.1676 | 1263659.4257
199 | 2615170.1181 | 1263647.9572 | 2615182.3309 | 1263640.4054 | 2615188.9776 | 1263636.7143
200 | 2615202.3101 | 1263629.3105 | 2615198.4379 | 1263631.4608
201 | 2615188.9776 | 1263636.7143 | 2615198.4379 | 1263631.4608
202 | 2615137.7386 | 1263669.2892 | 2615143.4984 | 1263664.067 | 2615151.1676 | 1263659.4257
203 | 2615137.7386 | 1263669.2892 | 2615146.4488 | 1263680.916
204 | 2615137.7386 | 1263669.2892 | 2615132.719 | 1263673.8397
205 | 2615149.9732 | 1263685.6206 | 2615146.4488 | 1263680.916
206 | 2615132.719 | 1263673.8397 | 2615129.0889 | 1263677.1304
207 | 2615124.3092 | 1263681.4634 | 2615129.0889 | 1263677.1304
208 | 2615124.3092 | 1263681.4634 | 2615112.4691 | 1263692.1996
209 | 2615124.3092 | 1263681.4634 | 2615135.117 | 1263696.5212
210 | 2615112.4691 | 1263692.1996 | 2615100.2242 | 1263703.3029
211 | 2615100.2242 | 1263703.3029 | 2615086.7497 | 1263715.5212
212 | 2615073.332 | 1263727.6879 | 2615086.7497 | 1263715.5212
213 | 2615073.332 | 1263727.6879 | 2615069.7606 | 1263731.2813
214 | 2615073.332 | 1263727.6879 | 2615063.9203 | 1263710.0483
215 | 2615069.7606 | 1263731.2813 | 2615079.8097 | 1263745.6545
216 | 2615069.7606 | 1263731.2813 | 2615055.2331 | 1263745.9323
217 | 2615063.0258 | 1263708.3719 | 2615063.9203 | 1263710.0483
218 | 2615050.1256 | 1263684.1946 | 2615063.0258 | 1263708.3719
219 | 2615050.1256 | 1263684.1946 | 2615049.6231 | 1263683.2526 | 2615047.1886 | 1263680.9782 | 2615045.0235 | 1263679.4495 | 2615042.3561 | 1263679.9542 | 2615040.0709 | 1263681.2048
220 | 2615040.0709 | 1263681.2048 | 2615040.0709 | 1263681.2048 | 2615028.0634 | 1263692.1008
221 | 2615025.0719 | 1263694.8154 | 2615028.0634 | 1263692.1008
222 | 2615025.0719 | 1263694.8154 | 2615016.033 | 1263703.0175
223 | 2615055.2331 | 1263745.9323 | 2615065.2378 | 1263761.1643
224 | 2615055.2331 | 1263745.9323 | 2615051.9838 | 1263749.2102
225 | 2615041.0388 | 1263760.2516 | 2615051.9838 | 1263749.2102
226 | 2615056.2696 | 1263462.1059 | 2615054.2214 | 1263448.6002
227 | 2615056.2696 | 1263462.1059 | 2615071.1545 | 1263461.2098 | 2615075.3814 | 1263460.6615
228 | 2615054.2214 | 1263448.6002 | 2615054.2378 | 1263345.6317
229 | 2615075.3814 | 1263460.6615 | 2615084.9421 | 1263459.4213 | 2615097.161 | 1263455.4719 | 2615097.8858 | 1263455.0875
230 | 2615106.586 | 1263450.4735 | 2615097.8858 | 1263455.0875
231 | 2615106.586 | 1263450.4735 | 2615109.8062 | 1263448.7657
232 | 2615135.4191 | 1263434.0619 | 2615128.6455 | 1263437.0059 | 2615110.035 | 1263448.6444 | 2615109.8062 | 1263448.7657
233 | 2615135.4191 | 1263434.0619 | 2615148.7624 | 1263428.2623 | 2615168.7238 | 1263421.2596
234 | 2615207.4503 | 1263381.0465 | 2615212.6819 | 1263373.3991
235 | 2615207.4503 | 1263381.0465 | 2615211.9803 | 1263382.6592 | 2615216.1233 | 1263382.4697 | 2615226.9319 | 1263379.3731 | 2615239.1626 | 1263376.7915 | 2615251.6882 | 1263376.7237 | 2615262.5514 | 1263377.8476
236 | 2615212.6819 | 1263373.3991 | 2615232.4135 | 1263368.2128
237 | 2615212.6819 | 1263373.3991 | 2615213.2792 | 1263372.5333 | 2615213.9664 | 1263371.526
238 | 2615269.2188 | 1263380.9828 | 2615262.5989 | 1263377.8525 | 2615262.5514 | 1263377.8476
239 | 2615262.5514 | 1263377.8476 | 2615272.6146 | 1263322.8737
240 | 2615213.9664 | 1263371.526 | 2615223.2965 | 1263357.8489
241 | 2615269.2188 | 1263380.9828 | 2615274.1919 | 1263394.1188
242 | 2615272.6146 | 1263322.8737 | 2615285.3706 | 1263324.0518 | 2615290.5091 | 1263325.3243
243 | 2615277.9491 | 1263404.0433 | 2615274.1919 | 1263394.1188
244 | 2615290.5091 | 1263325.3243 | 2615298.4827 | 1263327.2989 | 2615308.248 | 1263331.5937 | 2615319.4962 | 1263336.237 | 2615329.5434 | 1263342.167 | 2615333.3934 | 1263345.2118
245 | 2615234.1509 | 1263456.9086 | 2615243.8568 | 1263452.6598
246 | 2615243.8568 | 1263452.6598 | 2615248.1036 | 1263450.8007
247 | 2615253.0456 | 1263448.6662 | 2615252.6025 | 1263448.8312 | 2615248.1036 | 1263450.8007
248 | 2615253.0456 | 1263448.6662 | 2615262.8306 | 1263445.0229
249 | 2615281.7556 | 1263437.9765 | 2615262.8306 | 1263445.0229
250 | 2615281.7556 | 1263437.9765 | 2615288.2082 | 1263435.8472
251 | 2615281.7556 | 1263437.9765 | 2615284.0448 | 1263448.3836
252 | 2615288.2082 | 1263435.8472 | 2615307.9719 | 1263429.3249
253 | 2615288.2082 | 1263435.8472 | 2615287.4932 | 1263432.721 | 2615286.1447 | 1263427.0247 | 2615284.2414 | 1263420.4766
254 | 2615285.0488 | 1263452.9478 | 2615284.0448 | 1263448.3836
255 | 2615321.6406 | 1263424.814 | 2615307.9719 | 1263429.3249
256 | 2615277.9491 | 1263404.0433 | 2615280.0901 | 1263406.1948 | 2615284.2414 | 1263420.4766
257 | 2615331.0326 | 1263421.7146 | 2615321.6406 | 1263424.814
258 | 2615277.9491 | 1263404.0433 | 2615260.4505 | 1263411.9563
259 | 2615260.4505 | 1263411.9563 | 2615258.977 | 1263412.6227 | 2615255.4433 | 1263412.9869
260 | 2615243.8191 | 1263414.1672 | 2615244.452 | 1263414.1197 | 2615255.4433 | 1263412.9869
261 | 2615236.4215 | 1263414.7217 | 2615243.8191 | 1263414.1672
262 | 2615228.1285 | 1263418.4498 | 2615236.4215 | 1263414.7217 | 2615236.4215 | 1263414.7217
263 | 2615218.5832 | 1263422.7409 | 2615228.1285 | 1263418.4498
264 | 2615331.0326 | 1263421.7146 | 2615316.6126 | 1263411.6593
265 | 2615331.0326 | 1263421.7146 | 2615353.1204 | 1263414.0775 | 2615359.7499 | 1263410.5478
266 | 2615213.9435 | 1263424.8266 | 2615218.5832 | 1263422.7409
267 | 2615316.6126 | 1263411.6593 | 2615308.7132 | 1263406.1484
268 | 2615304.0886 | 1263414.0509 | 2615316.6126 | 1263411.6593
269 | 2615359.7499 | 1263410.5478 | 2615355.0726 | 1263404.7761 | 2615342.9141 | 1263408.5362

## bus_geodata
| x | y | coords
0 | 2615274.4738 | 1263502.9242
1 | 2615269.9514 | 1263504.1448
2 | 2615279.5142 | 1263501.5636
3 | 2615265.6754 | 1263505.299
4 | 2615288.5051 | 1263499.1368
5 | 2615255.9654 | 1263508.2944
6 | 2615294.8733 | 1263497.4179
7 | 2615250.0287 | 1263510.3174
8 | 2615290.7561 | 1263478.8936
9 | 2615304.9392 | 1263496.0207
10 | 2615241.3277 | 1263513.2824
11 | 2615231.3922 | 1263516.668
12 | 2615209.4384 | 1263510.8388
13 | 2615208.007 | 1263525.5412
14 | 2615185.2306 | 1263508.3194
15 | 2615204.8397 | 1263526.743
16 | 2615345.8885 | 1263597.6178
17 | 2615327.8811 | 1263607.0965
18 | 2615356.7121 | 1263591.9204
19 | 2615315.4593 | 1263613.6351
20 | 2615359.362 | 1263596.7823
21 | 2615349.9186 | 1263579.5135
22 | 2615311.1044 | 1263615.9275
23 | 2615374.1312 | 1263623.8798
24 | 2615341.4275 | 1263564.0061
25 | 2615303.4898 | 1263619.9357
26 | 2615374.322 | 1263624.2299
27 | 2615349.6511 | 1263557.5903
28 | 2615331.8873 | 1263547.5075
29 | 2615383.1051 | 1263640.3444
30 | 2615376.6019 | 1263644.6305
31 | 2615392.9955 | 1263633.8842
32 | 2615386.0003 | 1263657.5477
33 | 2615402.8719 | 1263627.433
34 | 2615293.0811 | 1263585.8447
35 | 2615292.9753 | 1263585.8924
36 | 2615310.8769 | 1263577.8061
37 | 2615275.4314 | 1263593.8649
38 | 2615262.0554 | 1263600.2123
39 | 2615250.336 | 1263605.7736
40 | 2615387.2838 | 1263543.7937
41 | 2615326.8674 | 1263538.8262
42 | 2615246.1953 | 1263607.7385
43 | 2615245.4604 | 1263608.0873
44 | 2615241.6871 | 1263609.874
45 | 2615218.4897 | 1263620.7241
46 | 2615324.2851 | 1263534.3605
47 | 2615217.993 | 1263620.9564
48 | 2615216.7309 | 1263621.5467
49 | 2615322.0431 | 1263530.4832
50 | 2615315.6052 | 1263519.3497
51 | 2615315.4305 | 1263519.0476
52 | 2615329.9784 | 1263495.017
53 | 2615347.4479 | 1263665.6667
54 | 2615332.7505 | 1263677.8845
55 | 2615342.3297 | 1263691.269
56 | 2615327.4109 | 1263682.3232
57 | 2615396.1328 | 1263671.4736
58 | 2615344.6669 | 1263694.5346
59 | 2615325.4847 | 1263683.9244
60 | 2615405.6157 | 1263684.5067
61 | 2615321.8731 | 1263686.9266
62 | 2615237.348 | 1263785.8494
63 | 2615252.8498 | 1263806.6002
64 | 2615223.8639 | 1263767.7996
65 | 2615252.9985 | 1263806.7993
66 | 2615235.9307 | 1263758.3685
67 | 2615203.7502 | 1263784.3591
68 | 2615272.8069 | 1263833.315
69 | 2615220.8083 | 1263738.9963
70 | 2615249.4736 | 1263747.1106
71 | 2615307.5965 | 1263805.1663
72 | 2615216.2488 | 1263733.1554
73 | 2615249.7154 | 1263746.9096
74 | 2615269.2533 | 1263730.6682
75 | 2615290.3259 | 1263713.1511
76 | 2615310.0467 | 1263696.7576
77 | 2615206.1592 | 1263720.2304
78 | 2615342.1517 | 1263811.7612
79 | 2615386.3081 | 1263817.7236
80 | 2615401.0678 | 1263815.2476
81 | 2615196.9334 | 1263708.4119
82 | 2615204.9015 | 1263702.5949
83 | 2615188.6569 | 1263714.604
84 | 2615170.484 | 1263728.2002
85 | 2615157.4875 | 1263737.9236
86 | 2615171.0481 | 1263727.7781
87 | 2615153.7336 | 1263740.732
88 | 2615140.2112 | 1263750.8489
89 | 2615138.2343 | 1263752.3279
90 | 2615124.6104 | 1263763.2697
91 | 2615314.4316 | 1263693.1126
92 | 2615196.9145 | 1263690.6882
93 | 2615211.3535 | 1263697.8819
94 | 2615229.4758 | 1263684.8199
95 | 2615230.7904 | 1263683.8731
96 | 2615238.9161 | 1263678.0207
97 | 2615184.8828 | 1263672.7516
98 | 2615181.9654 | 1263668.4025
99 | 2615435.4382 | 1263725.4945
100 | 2615419.9898 | 1263737.6739
101 | 2615446.533 | 1263740.742
102 | 2615409.4171 | 1263623.1578
103 | 2615414.1498 | 1263620.0665
104 | 2615421.4829 | 1263615.2822
105 | 2615421.6196 | 1263632.0219
106 | 2615461.6364 | 1263761.4986
107 | 2615471.9474 | 1263775.6797
108 | 2615424.0859 | 1263635.9693
109 | 2615401.5851 | 1263574.9099
110 | 2615439.3121 | 1263802.5689
111 | 2615401.7654 | 1263815.4469
112 | 2615363.4832 | 1263497.6566
113 | 2615358.5085 | 1263497.2647
114 | 2615371.391 | 1263498.2796
115 | 2615348.4731 | 1263496.4741
116 | 2615338.5442 | 1263495.6919
117 | 2615290.2702 | 1263476.6849
118 | 2615289.6277 | 1263473.7638
119 | 2614933.9969 | 1263701.7109
120 | 2614926.7704 | 1263709.1553
121 | 2614943.9916 | 1263691.566
122 | 2614955.4872 | 1263681.3077
123 | 2614961.4067 | 1263676.0253
124 | 2614882.0898 | 1263716.1018
125 | 2614878.6902 | 1263674.2085
126 | 2614967.5754 | 1263670.5206
127 | 2614975.6519 | 1263740.9472
128 | 2614992.5578 | 1263724.3863
129 | 2614994.7106 | 1263722.3661
130 | 2615004.4359 | 1263713.5411
131 | 2615013.3489 | 1263705.4532
132 | 2614885.1442 | 1263660.1243
133 | 2614894.3134 | 1263645.0816
134 | 2614897.6562 | 1263639.5974
135 | 2614911.1471 | 1263620.3413
136 | 2614915.7546 | 1263613.874
137 | 2614978.5092 | 1263660.7631
138 | 2614980.2447 | 1263659.2084
139 | 2614980.5021 | 1263658.9778
140 | 2614928.2757 | 1263596.2985
141 | 2614941.7652 | 1263578.4685
142 | 2614961.8026 | 1263557.2735
143 | 2614991.0554 | 1263649.5234
144 | 2614993.3258 | 1263647.4895
145 | 2614995.1868 | 1263645.8222
146 | 2615012.0655 | 1263632.3704
147 | 2614976.1866 | 1263542.0585
148 | 2615013.1173 | 1263548.1241
149 | 2615012.0754 | 1263632.363
150 | 2615028.1437 | 1263620.7218
151 | 2615034.4875 | 1263617.6562
152 | 2615037.8977 | 1263616.0083
153 | 2615043.0215 | 1263613.5323
154 | 2615034.9421 | 1263596.0051
155 | 2615057.4738 | 1263606.5314
156 | 2615079.8949 | 1263596.2995
157 | 2615079.9707 | 1263596.2659
158 | 2615080.7687 | 1263595.9114
159 | 2615034.3674 | 1263594.7586
160 | 2615091.7725 | 1263590.8268
161 | 2615025.7338 | 1263576.0293
162 | 2615105.8243 | 1263583.7222
163 | 2615122.9655 | 1263571.5614
164 | 2615127.1515 | 1263568.0369
165 | 2615011.278 | 1263583.287
166 | 2615003.9852 | 1263586.9485
167 | 2615027.9659 | 1263574.9342
168 | 2615044.6948 | 1263566.6808
169 | 2615060.6788 | 1263558.7949
170 | 2615048.7116 | 1263533.1879
171 | 2615072.2542 | 1263553.087
172 | 2615015.7001 | 1263500.263
173 | 2615028.5359 | 1263486.6859
174 | 2615030.2036 | 1263483.7654
175 | 2615058.2258 | 1263494.8585
176 | 2615085.0934 | 1263497.7324
177 | 2615102.129 | 1263499.5546
178 | 2615116.1425 | 1263501.0536
179 | 2615124.3764 | 1263501.9344
180 | 2615142.3182 | 1263503.8535
181 | 2615038.2674 | 1263468.2367
182 | 2615136.8565 | 1263560.0614
183 | 2615137.2471 | 1263586.8153
184 | 2615145.7367 | 1263553.0766
185 | 2615140.2772 | 1263592.4514
186 | 2615156.7528 | 1263546.4593
187 | 2615150.3921 | 1263611.2656
188 | 2615158.8977 | 1263545.1709
189 | 2615178.4632 | 1263536.7512
190 | 2615152.0301 | 1263493.485
191 | 2615164.8381 | 1263506.1972
192 | 2615175.8629 | 1263482.744
193 | 2615194.8199 | 1263474.2005
194 | 2615151.1519 | 1263612.679
195 | 2615155.6085 | 1263620.9685
196 | 2615170.1181 | 1263647.9572
197 | 2615202.3101 | 1263629.3105
198 | 2615198.4379 | 1263631.4608
199 | 2615188.9776 | 1263636.7143
200 | 2615151.1676 | 1263659.4257
201 | 2615137.7386 | 1263669.2892
202 | 2615146.4488 | 1263680.916
203 | 2615132.719 | 1263673.8397
204 | 2615129.0889 | 1263677.1304
205 | 2615124.3092 | 1263681.4634
206 | 2615112.4691 | 1263692.1996
207 | 2615135.117 | 1263696.5212
208 | 2615149.9732 | 1263685.6206
209 | 2615100.2242 | 1263703.3029
210 | 2615086.7497 | 1263715.5212
211 | 2615073.332 | 1263727.6879
212 | 2615069.7606 | 1263731.2813
213 | 2615063.9203 | 1263710.0483
214 | 2615050.1256 | 1263684.1946
215 | 2615063.0258 | 1263708.3719
216 | 2615040.0709 | 1263681.2048
217 | 2615028.0634 | 1263692.1008
218 | 2615025.0719 | 1263694.8154
219 | 2615016.033 | 1263703.0175
220 | 2615079.8097 | 1263745.6545
221 | 2615055.2331 | 1263745.9323
222 | 2615041.0388 | 1263760.2516
223 | 2615051.9838 | 1263749.2102
224 | 2615065.2378 | 1263761.1643
225 | 2615056.2696 | 1263462.1059
226 | 2615054.2214 | 1263448.6002
227 | 2615075.3814 | 1263460.6615
228 | 2615054.2378 | 1263345.6317
229 | 2615097.8858 | 1263455.0875
230 | 2615106.586 | 1263450.4735
231 | 2615109.8062 | 1263448.7657
232 | 2615135.4191 | 1263434.0619
233 | 2615168.7238 | 1263421.2596
234 | 2615207.4503 | 1263381.0465
235 | 2615212.6819 | 1263373.3991
236 | 2615262.5514 | 1263377.8476
237 | 2615232.4135 | 1263368.2128
238 | 2615213.9664 | 1263371.526
239 | 2615269.2188 | 1263380.9828
240 | 2615272.6146 | 1263322.8737
241 | 2615223.2965 | 1263357.8489
242 | 2615274.1919 | 1263394.1188
243 | 2615290.5091 | 1263325.3243
244 | 2615333.3934 | 1263345.2118
245 | 2615234.1509 | 1263456.9086
246 | 2615243.8568 | 1263452.6598
247 | 2615248.1036 | 1263450.8007
248 | 2615253.0456 | 1263448.6662
249 | 2615262.8306 | 1263445.0229
250 | 2615281.7556 | 1263437.9765
251 | 2615288.2082 | 1263435.8472
252 | 2615284.0448 | 1263448.3836
253 | 2615307.9719 | 1263429.3249
254 | 2615284.2414 | 1263420.4766
255 | 2615285.0488 | 1263452.9478
256 | 2615321.6406 | 1263424.814
257 | 2615277.9491 | 1263404.0433
258 | 2615260.4505 | 1263411.9563
259 | 2615255.4433 | 1263412.9869
260 | 2615243.8191 | 1263414.1672
261 | 2615236.4215 | 1263414.7217
262 | 2615228.1285 | 1263418.4498
263 | 2615331.0326 | 1263421.7146
264 | 2615218.5832 | 1263422.7409
265 | 2615213.9435 | 1263424.8266
266 | 2615308.7132 | 1263406.1484
267 | 2615316.6126 | 1263411.6593
268 | 2615304.0886 | 1263414.0509
269 | 2615342.9141 | 1263408.5362
270 | 2615359.7499 | 1263410.5478
271 | 2615202.3101 | 1263629.3105

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1