## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2770-27_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2770-27_0_6_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2770-27_0_6_node_247 | 0.4 | n |  | TRUE
3 | bus_LV_2770-27_0_6_node_171 | 0.4 | n |  | TRUE
4 | bus_LV_2770-27_0_6_node_246 | 0.4 | n |  | TRUE
5 | bus_LV_2770-27_0_6_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_2770-27_0_6_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2770-27_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2770-27_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2770-27_0_6_node_135 | 0.4 | n |  | TRUE
10 | bus_LV_2770-27_0_6_node_136 | 0.4 | n |  | TRUE
11 | bus_LV_2770-27_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2770-27_0_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2770-27_0_6_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2770-27_0_6_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2770-27_0_6_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2770-27_0_6_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2770-27_0_6_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_2770-27_0_6_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2770-27_0_6_node_214 | 0.4 | n |  | TRUE
20 | bus_LV_2770-27_0_6_node_205 | 0.4 | n |  | TRUE
21 | bus_LV_2770-27_0_6_node_213 | 0.4 | n |  | TRUE
22 | bus_LV_2770-27_0_6_node_96 | 0.4 | n |  | TRUE
23 | bus_LV_2770-27_0_6_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_2770-27_0_6_node_215 | 0.4 | n |  | TRUE
25 | bus_LV_2770-27_0_6_node_202 | 0.4 | n |  | TRUE
26 | bus_LV_2770-27_0_6_node_212 | 0.4 | n |  | TRUE
27 | bus_LV_2770-27_0_6_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2770-27_0_6_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_2770-27_0_6_node_97 | 0.4 | n |  | TRUE
30 | bus_LV_2770-27_0_6_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2770-27_0_6_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_2770-27_0_6_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_2770-27_0_6_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_2770-27_0_6_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_2770-27_0_6_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_2770-27_0_6_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_2770-27_0_6_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_2770-27_0_6_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_2770-27_0_6_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_2770-27_0_6_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_2770-27_0_6_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_2770-27_0_6_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_2770-27_0_6_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_2770-27_0_6_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_2770-27_0_6_node_90 | 0.4 | n |  | TRUE
46 | bus_LV_2770-27_0_6_node_91 | 0.4 | n |  | TRUE
47 | bus_LV_2770-27_0_6_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_2770-27_0_6_node_102 | 0.4 | n |  | TRUE
49 | bus_LV_2770-27_0_6_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_2770-27_0_6_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_2770-27_0_6_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_2770-27_0_6_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_2770-27_0_6_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_2770-27_0_6_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_2770-27_0_6_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_2770-27_0_6_node_41 | 0.4 | n |  | TRUE
57 | bus_LV_2770-27_0_6_node_42 | 0.4 | n |  | TRUE
58 | bus_LV_2770-27_0_6_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_2770-27_0_6_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_2770-27_0_6_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_2770-27_0_6_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_2770-27_0_6_node_47 | 0.4 | n |  | TRUE
63 | bus_LV_2770-27_0_6_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_2770-27_0_6_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_2770-27_0_6_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_2770-27_0_6_node_55 | 0.4 | n |  | TRUE
67 | bus_LV_2770-27_0_6_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_2770-27_0_6_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_2770-27_0_6_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_2770-27_0_6_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_2770-27_0_6_node_53 | 0.4 | n |  | TRUE
72 | bus_LV_2770-27_0_6_node_56 | 0.4 | n |  | TRUE
73 | bus_LV_2770-27_0_6_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_2770-27_0_6_node_70 | 0.4 | n |  | TRUE
75 | bus_LV_2770-27_0_6_node_71 | 0.4 | n |  | TRUE
76 | bus_LV_2770-27_0_6_node_89 | 0.4 | n |  | TRUE
77 | bus_LV_2770-27_0_6_node_105 | 0.4 | n |  | TRUE
78 | bus_LV_2770-27_0_6_node_86 | 0.4 | n |  | TRUE
79 | bus_LV_2770-27_0_6_node_82 | 0.4 | n |  | TRUE
80 | bus_LV_2770-27_0_6_node_62 | 0.4 | n |  | TRUE
81 | bus_LV_2770-27_0_6_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_2770-27_0_6_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_2770-27_0_6_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_2770-27_0_6_node_66 | 0.4 | n |  | TRUE
85 | bus_LV_2770-27_0_6_node_69 | 0.4 | n |  | TRUE
86 | bus_LV_2770-27_0_6_node_67 | 0.4 | n |  | TRUE
87 | bus_LV_2770-27_0_6_node_76 | 0.4 | n |  | TRUE
88 | bus_LV_2770-27_0_6_node_77 | 0.4 | n |  | TRUE
89 | bus_LV_2770-27_0_6_node_95 | 0.4 | n |  | TRUE
90 | bus_LV_2770-27_0_6_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_2770-27_0_6_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_2770-27_0_6_node_84 | 0.4 | n |  | TRUE
93 | bus_LV_2770-27_0_6_node_94 | 0.4 | n |  | TRUE
94 | bus_LV_2770-27_0_6_node_72 | 0.4 | n |  | TRUE
95 | bus_LV_2770-27_0_6_node_73 | 0.4 | n |  | TRUE
96 | bus_LV_2770-27_0_6_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_2770-27_0_6_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_2770-27_0_6_node_80 | 0.4 | n |  | TRUE
99 | bus_LV_2770-27_0_6_node_81 | 0.4 | n |  | TRUE
100 | bus_LV_2770-27_0_6_node_79 | 0.4 | n |  | TRUE
101 | bus_LV_2770-27_0_6_node_83 | 0.4 | n |  | TRUE
102 | bus_LV_2770-27_0_6_node_87 | 0.4 | n |  | TRUE
103 | bus_LV_2770-27_0_6_node_88 | 0.4 | n |  | TRUE
104 | bus_LV_2770-27_0_6_node_85 | 0.4 | n |  | TRUE
105 | bus_LV_2770-27_0_6_node_125 | 0.4 | n |  | TRUE
106 | bus_LV_2770-27_0_6_node_254 | 0.4 | n |  | TRUE
107 | bus_LV_2770-27_0_6_node_137 | 0.4 | n |  | TRUE
108 | bus_LV_2770-27_0_6_node_141 | 0.4 | n |  | TRUE
109 | bus_LV_2770-27_0_6_node_121 | 0.4 | n |  | TRUE
110 | bus_LV_2770-27_0_6_node_122 | 0.4 | n |  | TRUE
111 | bus_LV_2770-27_0_6_node_127 | 0.4 | n |  | TRUE
112 | bus_LV_2770-27_0_6_node_128 | 0.4 | n |  | TRUE
113 | bus_LV_2770-27_0_6_node_123 | 0.4 | n |  | TRUE
114 | bus_LV_2770-27_0_6_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_2770-27_0_6_node_92 | 0.4 | n |  | TRUE
116 | bus_LV_2770-27_0_6_node_93 | 0.4 | n |  | TRUE
117 | bus_LV_2770-27_0_6_node_98 | 0.4 | n |  | TRUE
118 | bus_LV_2770-27_0_6_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_2770-27_0_6_node_100 | 0.4 | n |  | TRUE
120 | bus_LV_2770-27_0_6_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_2770-27_0_6_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_2770-27_0_6_node_107 | 0.4 | n |  | TRUE
123 | bus_LV_2770-27_0_6_node_103 | 0.4 | n |  | TRUE
124 | bus_LV_2770-27_0_6_node_108 | 0.4 | n |  | TRUE
125 | bus_LV_2770-27_0_6_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_2770-27_0_6_node_184 | 0.4 | n |  | TRUE
127 | bus_LV_2770-27_0_6_node_185 | 0.4 | n |  | TRUE
128 | bus_LV_2770-27_0_6_node_110 | 0.4 | n |  | TRUE
129 | bus_LV_2770-27_0_6_node_111 | 0.4 | n |  | TRUE
130 | bus_LV_2770-27_0_6_node_112 | 0.4 | n |  | TRUE
131 | bus_LV_2770-27_0_6_node_113 | 0.4 | n |  | TRUE
132 | bus_LV_2770-27_0_6_node_116 | 0.4 | n |  | TRUE
133 | bus_LV_2770-27_0_6_node_253 | 0.4 | n |  | TRUE
134 | bus_LV_2770-27_0_6_node_163 | 0.4 | n |  | TRUE
135 | bus_LV_2770-27_0_6_node_114 | 0.4 | n |  | TRUE
136 | bus_LV_2770-27_0_6_node_115 | 0.4 | n |  | TRUE
137 | bus_LV_2770-27_0_6_node_117 | 0.4 | n |  | TRUE
138 | bus_LV_2770-27_0_6_node_118 | 0.4 | n |  | TRUE
139 | bus_LV_2770-27_0_6_node_164 | 0.4 | n |  | TRUE
140 | bus_LV_2770-27_0_6_node_151 | 0.4 | n |  | TRUE
141 | bus_LV_2770-27_0_6_node_119 | 0.4 | n |  | TRUE
142 | bus_LV_2770-27_0_6_node_120 | 0.4 | n |  | TRUE
143 | bus_LV_2770-27_0_6_node_158 | 0.4 | n |  | TRUE
144 | bus_LV_2770-27_0_6_node_133 | 0.4 | n |  | TRUE
145 | bus_LV_2770-27_0_6_node_134 | 0.4 | n |  | TRUE
146 | bus_LV_2770-27_0_6_node_124 | 0.4 | n |  | TRUE
147 | bus_LV_2770-27_0_6_node_126 | 0.4 | n |  | TRUE
148 | bus_LV_2770-27_0_6_node_129 | 0.4 | n |  | TRUE
149 | bus_LV_2770-27_0_6_node_154 | 0.4 | n |  | TRUE
150 | bus_LV_2770-27_0_6_node_130 | 0.4 | n |  | TRUE
151 | bus_LV_2770-27_0_6_node_153 | 0.4 | n |  | TRUE
152 | bus_LV_2770-27_0_6_node_131 | 0.4 | n |  | TRUE
153 | bus_LV_2770-27_0_6_node_132 | 0.4 | n |  | TRUE
154 | bus_LV_2770-27_0_6_node_146 | 0.4 | n |  | TRUE
155 | bus_LV_2770-27_0_6_node_142 | 0.4 | n |  | TRUE
156 | bus_LV_2770-27_0_6_node_145 | 0.4 | n |  | TRUE
157 | bus_LV_2770-27_0_6_node_139 | 0.4 | n |  | TRUE
158 | bus_LV_2770-27_0_6_node_138 | 0.4 | n |  | TRUE
159 | bus_LV_2770-27_0_6_node_144 | 0.4 | n |  | TRUE
160 | bus_LV_2770-27_0_6_node_147 | 0.4 | n |  | TRUE
161 | bus_LV_2770-27_0_6_node_149 | 0.4 | n |  | TRUE
162 | bus_LV_2770-27_0_6_node_148 | 0.4 | n |  | TRUE
163 | bus_LV_2770-27_0_6_node_150 | 0.4 | n |  | TRUE
164 | bus_LV_2770-27_0_6_node_161 | 0.4 | n |  | TRUE
165 | bus_LV_2770-27_0_6_node_160 | 0.4 | n |  | TRUE
166 | bus_LV_2770-27_0_6_node_162 | 0.4 | n |  | TRUE
167 | bus_LV_2770-27_0_6_node_155 | 0.4 | n |  | TRUE
168 | bus_LV_2770-27_0_6_node_159 | 0.4 | n |  | TRUE
169 | bus_LV_2770-27_0_6_node_233 | 0.4 | n |  | TRUE
170 | bus_LV_2770-27_0_6_node_168 | 0.4 | n |  | TRUE
171 | bus_LV_2770-27_0_6_node_167 | 0.4 | n |  | TRUE
172 | bus_LV_2770-27_0_6_node_156 | 0.4 | n |  | TRUE
173 | bus_LV_2770-27_0_6_node_157 | 0.4 | n |  | TRUE
174 | bus_LV_2770-27_0_6_node_165 | 0.4 | n |  | TRUE
175 | bus_LV_2770-27_0_6_node_166 | 0.4 | n |  | TRUE
176 | bus_LV_2770-27_0_6_node_178 | 0.4 | n |  | TRUE
177 | bus_LV_2770-27_0_6_node_179 | 0.4 | n |  | TRUE
178 | bus_LV_2770-27_0_6_node_169 | 0.4 | n |  | TRUE
179 | bus_LV_2770-27_0_6_node_170 | 0.4 | n |  | TRUE
180 | bus_LV_2770-27_0_6_node_172 | 0.4 | n |  | TRUE
181 | bus_LV_2770-27_0_6_node_173 | 0.4 | n |  | TRUE
182 | bus_LV_2770-27_0_6_node_176 | 0.4 | n |  | TRUE
183 | bus_LV_2770-27_0_6_node_231 | 0.4 | n |  | TRUE
184 | bus_LV_2770-27_0_6_node_174 | 0.4 | n |  | TRUE
185 | bus_LV_2770-27_0_6_node_175 | 0.4 | n |  | TRUE
186 | bus_LV_2770-27_0_6_node_177 | 0.4 | n |  | TRUE
187 | bus_LV_2770-27_0_6_node_180 | 0.4 | n |  | TRUE
188 | bus_LV_2770-27_0_6_node_181 | 0.4 | n |  | TRUE
189 | bus_LV_2770-27_0_6_node_226 | 0.4 | n |  | TRUE
190 | bus_LV_2770-27_0_6_node_228 | 0.4 | n |  | TRUE
191 | bus_LV_2770-27_0_6_node_224 | 0.4 | n |  | TRUE
192 | bus_LV_2770-27_0_6_node_182 | 0.4 | n |  | TRUE
193 | bus_LV_2770-27_0_6_node_183 | 0.4 | n |  | TRUE
194 | bus_LV_2770-27_0_6_node_196 | 0.4 | n |  | TRUE
195 | bus_LV_2770-27_0_6_node_195 | 0.4 | n |  | TRUE
196 | bus_LV_2770-27_0_6_node_186 | 0.4 | n |  | TRUE
197 | bus_LV_2770-27_0_6_node_187 | 0.4 | n |  | TRUE
198 | bus_LV_2770-27_0_6_node_188 | 0.4 | n |  | TRUE
199 | bus_LV_2770-27_0_6_node_210 | 0.4 | n |  | TRUE
200 | bus_LV_2770-27_0_6_node_211 | 0.4 | n |  | TRUE
201 | bus_LV_2770-27_0_6_node_189 | 0.4 | n |  | TRUE
202 | bus_LV_2770-27_0_6_node_192 | 0.4 | n |  | TRUE
203 | bus_LV_2770-27_0_6_node_190 | 0.4 | n |  | TRUE
204 | bus_LV_2770-27_0_6_node_191 | 0.4 | n |  | TRUE
205 | bus_LV_2770-27_0_6_node_193 | 0.4 | n |  | TRUE
206 | bus_LV_2770-27_0_6_node_194 | 0.4 | n |  | TRUE
207 | bus_LV_2770-27_0_6_node_200 | 0.4 | n |  | TRUE
208 | bus_LV_2770-27_0_6_node_207 | 0.4 | n |  | TRUE
209 | bus_LV_2770-27_0_6_node_208 | 0.4 | n |  | TRUE
210 | bus_LV_2770-27_0_6_node_206 | 0.4 | n |  | TRUE
211 | bus_LV_2770-27_0_6_node_197 | 0.4 | n |  | TRUE
212 | bus_LV_2770-27_0_6_node_198 | 0.4 | n |  | TRUE
213 | bus_LV_2770-27_0_6_node_199 | 0.4 | n |  | TRUE
214 | bus_LV_2770-27_0_6_node_225 | 0.4 | n |  | TRUE
215 | bus_LV_2770-27_0_6_node_201 | 0.4 | n |  | TRUE
216 | bus_LV_2770-27_0_6_node_203 | 0.4 | n |  | TRUE
217 | bus_LV_2770-27_0_6_node_204 | 0.4 | n |  | TRUE
218 | bus_LV_2770-27_0_6_node_209 | 0.4 | n |  | TRUE
219 | bus_LV_2770-27_0_6_node_219 | 0.4 | n |  | TRUE
220 | bus_LV_2770-27_0_6_node_221 | 0.4 | n |  | TRUE
221 | bus_LV_2770-27_0_6_node_220 | 0.4 | n |  | TRUE
222 | bus_LV_2770-27_0_6_node_218 | 0.4 | n |  | TRUE
223 | bus_LV_2770-27_0_6_node_216 | 0.4 | n |  | TRUE
224 | bus_LV_2770-27_0_6_node_217 | 0.4 | n |  | TRUE
225 | bus_LV_2770-27_0_6_node_235 | 0.4 | n |  | TRUE
226 | bus_LV_2770-27_0_6_node_244 | 0.4 | n |  | TRUE
227 | bus_LV_2770-27_0_6_node_243 | 0.4 | n |  | TRUE
228 | bus_LV_2770-27_0_6_node_232 | 0.4 | n |  | TRUE
229 | bus_LV_2770-27_0_6_node_229 | 0.4 | n |  | TRUE
230 | bus_LV_2770-27_0_6_node_230 | 0.4 | n |  | TRUE
231 | bus_LV_2770-27_0_6_node_234 | 0.4 | n |  | TRUE
232 | bus_LV_2770-27_0_6_node_237 | 0.4 | n |  | TRUE
233 | bus_LV_2770-27_0_6_node_236 | 0.4 | n |  | TRUE
234 | bus_LV_2770-27_0_6_node_238 | 0.4 | n |  | TRUE
235 | bus_LV_2770-27_0_6_node_239 | 0.4 | n |  | TRUE
236 | bus_LV_2770-27_0_6_node_240 | 0.4 | n |  | TRUE
237 | bus_LV_2770-27_0_6_node_241 | 0.4 | n |  | TRUE
238 | bus_LV_2770-27_0_6_node_242 | 0.4 | n |  | TRUE
239 | bus_LV_2770-27_0_6_node_245 | 0.4 | n |  | TRUE
240 | bus_LV_2770-27_0_6_node_252 | 0.4 | n |  | TRUE
241 | bus_LV_2770-27_0_6_node_251 | 0.4 | n |  | TRUE
242 | bus_LV_2770-27_0_6_node_248 | 0.4 | n |  | TRUE
243 | bus_LV_2770-27_0_6_node_249 | 0.4 | n |  | TRUE
244 | bus_MV_575_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2770-27_0_6_load_0 | 0 | 0.000606 | 0.00015188 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2770-27_0_6_load_246 | 4 | 0.0014149 | 0.00035461 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2770-27_0_6_load_3 | 5 | 0.00080933 | 0.00020284 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2770-27_0_6_load_4 | 6 | 0.0032055 | 0.00080338 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2770-27_0_6_load_5 | 7 | 0.0018622 | 0.00046671 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2770-27_0_6_load_6 | 8 | 0.0013589 | 0.00034058 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2770-27_0_6_load_135 | 9 | 0.0015418 | 0.00038642 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2770-27_0_6_load_136 | 10 | 0.0011723 | 0.00029381 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2770-27_0_6_load_8 | 11 | 0.0034272 | 0.00085894 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2770-27_0_6_load_9 | 12 | 0.002046 | 0.00051276 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2770-27_0_6_load_10 | 13 | 0.0014596 | 0.00036581 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2770-27_0_6_load_11 | 14 | 0.002357 | 0.00059073 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2770-27_0_6_load_12 | 15 | 0.0028631 | 0.00071756 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2770-27_0_6_load_16 | 17 | 0.0016148 | 0.00040471 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2770-27_0_6_load_214 | 19 | 0.0021701 | 0.00054387 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2770-27_0_6_load_205 | 20 | 0.0017376 | 0.00043547 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2770-27_0_6_load_213 | 21 | 0.0016274 | 0.00040786 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2770-27_0_6_load_96 | 22 | 0.00068635 | 0.00017202 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2770-27_0_6_load_215 | 24 | 0.0017368 | 0.00043528 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2770-27_0_6_load_212 | 26 | 0.0017413 | 0.00043641 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2770-27_0_6_load_19 | 27 | 0.0029728 | 0.00074505 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2770-27_0_6_load_17 | 28 | 0.0024219 | 0.000607 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2770-27_0_6_load_97 | 29 | 0.0052098 | 0.0013057 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2770-27_0_6_load_18 | 30 | 0.0025837 | 0.00064753 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2770-27_0_6_load_20 | 31 | 0.0022253 | 0.00055771 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2770-27_0_6_load_21 | 32 | 0.0039162 | 0.00098149 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2770-27_0_6_load_22 | 33 | 0.0019833 | 0.00049707 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2770-27_0_6_load_23 | 34 | 0.0017069 | 0.00042779 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2770-27_0_6_load_32 | 36 | 0.0018495 | 0.00046353 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2770-27_0_6_load_33 | 37 | 0.00096551 | 0.00024198 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2770-27_0_6_load_24 | 38 | 0.0034834 | 0.00087302 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2770-27_0_6_load_25 | 39 | 0.0017184 | 0.00043068 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2770-27_0_6_load_26 | 40 | 0.0033383 | 0.00083666 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2770-27_0_6_load_27 | 41 | 0.0034626 | 0.00086781 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2770-27_0_6_load_28 | 42 | 0.00037062 | 9.2885e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2770-27_0_6_load_29 | 43 | 0.0059785 | 0.0014984 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2770-27_0_6_load_30 | 44 | 0.00179 | 0.00044863 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2770-27_0_6_load_90 | 45 | 0.0012399 | 0.00031074 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2770-27_0_6_load_91 | 46 | 0.0030671 | 0.0007687 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2770-27_0_6_load_102 | 48 | 0.00086397 | 0.00021653 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2770-27_0_6_load_35 | 49 | 0.0027772 | 0.00069604 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2770-27_0_6_load_36 | 50 | 0.0029469 | 0.00073857 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2770-27_0_6_load_48 | 51 | 0.0020847 | 0.00052246 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2770-27_0_6_load_37 | 52 | 0.00087847 | 0.00022017 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2770-27_0_6_load_38 | 53 | 0.0015059 | 0.00037741 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2770-27_0_6_load_39 | 54 | 0.003238 | 0.00081152 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2770-27_0_6_load_41 | 56 | 0.0029034 | 0.00072766 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2770-27_0_6_load_42 | 57 | 0.0015261 | 0.00038248 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2770-27_0_6_load_43 | 58 | 0.003156 | 0.00079096 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2770-27_0_6_load_44 | 59 | 0.0029435 | 0.0007377 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2770-27_0_6_load_46 | 61 | 0.00096548 | 0.00024197 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2770-27_0_6_load_47 | 62 | 0.0036222 | 0.0009078 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2770-27_0_6_load_51 | 65 | 0.003033 | 0.00076014 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2770-27_0_6_load_54 | 67 | 0.0062138 | 0.0015573 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2770-27_0_6_load_52 | 68 | 0.0041438 | 0.0010385 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2770-27_0_6_load_58 | 69 | 0.0049608 | 0.0012433 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2770-27_0_6_load_57 | 70 | 0.0030764 | 0.00077102 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2770-27_0_6_load_53 | 71 | 0.0061844 | 0.00155 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2770-27_0_6_load_56 | 72 | 0.0036461 | 0.00091381 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2770-27_0_6_load_60 | 73 | 0.0025961 | 0.00065065 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2770-27_0_6_load_70 | 74 | 0.00051665 | 0.00012948 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2770-27_0_6_load_71 | 75 | 0.0020193 | 0.00050609 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2770-27_0_6_load_89 | 76 | 0.003745 | 0.00093859 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2770-27_0_6_load_105 | 77 | 0.0011372 | 0.000285 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2770-27_0_6_load_86 | 78 | 0.0034451 | 0.00086343 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2770-27_0_6_load_62 | 80 | 0.00090388 | 0.00022653 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2770-27_0_6_load_63 | 81 | 0.0036189 | 0.00090699 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2770-27_0_6_load_64 | 82 | 0.0041136 | 0.001031 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2770-27_0_6_load_69 | 85 | 0.0027876 | 0.00069863 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2770-27_0_6_load_67 | 86 | 0.0028776 | 0.00072119 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2770-27_0_6_load_76 | 87 | 0.0034632 | 0.00086795 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2770-27_0_6_load_77 | 88 | 0.001008 | 0.00025264 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2770-27_0_6_load_95 | 89 | 0.0029781 | 0.00074637 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2770-27_0_6_load_68 | 90 | 0.002347 | 0.00058821 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2770-27_0_6_load_78 | 91 | 0.0031533 | 0.0007903 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2770-27_0_6_load_84 | 92 | 0.0013127 | 0.000329 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2770-27_0_6_load_94 | 93 | 0.0029657 | 0.00074327 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2770-27_0_6_load_72 | 94 | 0.0015712 | 0.00039378 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2770-27_0_6_load_73 | 95 | 0.0018264 | 0.00045773 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2770-27_0_6_load_74 | 96 | 0.0015073 | 0.00037777 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2770-27_0_6_load_75 | 97 | 0.00075296 | 0.00018871 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2770-27_0_6_load_81 | 99 | 0.00097723 | 0.00024492 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2770-27_0_6_load_79 | 100 | 0.0007506 | 0.00018812 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2770-27_0_6_load_87 | 102 | 0.0013872 | 0.00034768 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2770-27_0_6_load_88 | 103 | 0.002869 | 0.00071905 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2770-27_0_6_load_254 | 106 | 0.0043378 | 0.0010871 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2770-27_0_6_load_141 | 108 | 0.0050236 | 0.001259 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2770-27_0_6_load_121 | 109 | 0.0022255 | 0.00055776 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2770-27_0_6_load_122 | 110 | 0.0017347 | 0.00043476 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2770-27_0_6_load_127 | 111 | 0.0013279 | 0.00033281 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2770-27_0_6_load_128 | 112 | 0.0012915 | 0.00032369 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2770-27_0_6_load_123 | 113 | 0.0015489 | 0.0003882 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2770-27_0_6_load_104 | 114 | 0.0029594 | 0.00074169 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2770-27_0_6_load_92 | 115 | 0.0069582 | 0.0017439 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2770-27_0_6_load_93 | 116 | 0.0035292 | 0.0008845 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2770-27_0_6_load_98 | 117 | 0.0018067 | 0.0004528 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2770-27_0_6_load_99 | 118 | 0.0015424 | 0.00038655 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2770-27_0_6_load_100 | 119 | 0.0035723 | 0.00089532 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2770-27_0_6_load_106 | 121 | 0.0023302 | 0.00058401 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2770-27_0_6_load_107 | 122 | 0.0016282 | 0.00040807 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2770-27_0_6_load_103 | 123 | 0.0056767 | 0.0014227 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2770-27_0_6_load_108 | 124 | 0.0021086 | 0.00052846 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2770-27_0_6_load_109 | 125 | 0.0023897 | 0.00059891 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2770-27_0_6_load_184 | 126 | 0.0018352 | 0.00045996 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2770-27_0_6_load_185 | 127 | 0.0020623 | 0.00051687 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2770-27_0_6_load_110 | 128 | 0.004008 | 0.0010045 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2770-27_0_6_load_111 | 129 | 0.0027133 | 0.00068002 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2770-27_0_6_load_113 | 131 | 0.0090142 | 0.0022592 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2770-27_0_6_load_253 | 133 | 0.0022638 | 0.00056736 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2770-27_0_6_load_114 | 135 | 0.0013054 | 0.00032717 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2770-27_0_6_load_115 | 136 | 0.002628 | 0.00065864 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2770-27_0_6_load_117 | 137 | 0.0016759 | 0.00042002 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2770-27_0_6_load_118 | 138 | 0.0026286 | 0.00065878 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2770-27_0_6_load_164 | 139 | 0.0023633 | 0.00059229 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2770-27_0_6_load_119 | 141 | 0.001948 | 0.0004882 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2770-27_0_6_load_120 | 142 | 0.0015636 | 0.00039187 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2770-27_0_6_load_158 | 143 | 0.002869 | 0.00071905 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2770-27_0_6_load_133 | 144 | 0.0015551 | 0.00038976 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2770-27_0_6_load_124 | 146 | 0.0014011 | 0.00035116 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2770-27_0_6_load_126 | 147 | 0.0020894 | 0.00052366 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2770-27_0_6_load_129 | 148 | 0.0014379 | 0.00036037 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2770-27_0_6_load_154 | 149 | 0.0018822 | 0.00047172 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2770-27_0_6_load_131 | 152 | 0.0014113 | 0.00035369 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2770-27_0_6_load_132 | 153 | 0.0019773 | 0.00049556 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2770-27_0_6_load_146 | 154 | 0.0015514 | 0.00038881 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2770-27_0_6_load_142 | 155 | 0.0067209 | 0.0016844 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2770-27_0_6_load_145 | 156 | 0.0021524 | 0.00053945 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2770-27_0_6_load_139 | 157 | 0.0010435 | 0.00026152 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2770-27_0_6_load_138 | 158 | 0.0021984 | 0.00055097 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2770-27_0_6_load_144 | 159 | 0.0015248 | 0.00038216 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2770-27_0_6_load_147 | 160 | 0.0017795 | 0.00044599 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2770-27_0_6_load_161 | 164 | 0.00133 | 0.00033333 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2770-27_0_6_load_160 | 165 | 0.0013308 | 0.00033354 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2770-27_0_6_load_162 | 166 | 0.0019546 | 0.00048987 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2770-27_0_6_load_155 | 167 | 0.0018218 | 0.00045658 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2770-27_0_6_load_159 | 168 | 0.0010539 | 0.00026414 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_2770-27_0_6_load_233 | 169 | 0.004528 | 0.0011348 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_2770-27_0_6_load_168 | 170 | 0.0023737 | 0.00059491 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_2770-27_0_6_load_167 | 171 | 0.0030502 | 0.00076445 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_2770-27_0_6_load_156 | 172 | 0.0015615 | 0.00039134 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_2770-27_0_6_load_157 | 173 | 0.0015898 | 0.00039844 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_2770-27_0_6_load_165 | 174 | 0.0025385 | 0.00063621 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_2770-27_0_6_load_166 | 175 | 0.0023128 | 0.00057965 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_2770-27_0_6_load_178 | 176 | 0.0020183 | 0.00050582 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_2770-27_0_6_load_179 | 177 | 0.0034235 | 0.00085801 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_2770-27_0_6_load_169 | 178 | 0.0022928 | 0.00057464 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_2770-27_0_6_load_172 | 180 | 0.0029126 | 0.00072998 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_2770-27_0_6_load_173 | 181 | 0.0013033 | 0.00032665 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_2770-27_0_6_load_176 | 182 | 0.0012989 | 0.00032554 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_2770-27_0_6_load_174 | 184 | 0.0033049 | 0.00082829 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_2770-27_0_6_load_175 | 185 | 0.0048519 | 0.001216 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_2770-27_0_6_load_177 | 186 | 0.0018817 | 0.00047159 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_2770-27_0_6_load_180 | 187 | 0.0024698 | 0.000619 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_2770-27_0_6_load_181 | 188 | 0.0023567 | 0.00059064 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_2770-27_0_6_load_228 | 190 | 0.00070167 | 0.00017586 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_2770-27_0_6_load_182 | 192 | 0.0011156 | 0.00027959 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_2770-27_0_6_load_183 | 193 | 0.0022639 | 0.00056739 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_2770-27_0_6_load_196 | 194 | 0.0018146 | 0.00045479 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_2770-27_0_6_load_195 | 195 | 0.003863 | 0.00096816 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_2770-27_0_6_load_187 | 197 | 0.0014877 | 0.00037285 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_2770-27_0_6_load_188 | 198 | 0.0010737 | 0.0002691 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_2770-27_0_6_load_210 | 199 | 0.0017379 | 0.00043556 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_2770-27_0_6_load_211 | 200 | 0.0016038 | 0.00040194 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_2770-27_0_6_load_190 | 203 | 0.0033745 | 0.00084573 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_2770-27_0_6_load_191 | 204 | 0.0025006 | 0.00062671 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_2770-27_0_6_load_194 | 206 | 0.0032072 | 0.00080379 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_2770-27_0_6_load_200 | 207 | 0.0021765 | 0.00054549 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_2770-27_0_6_load_206 | 210 | 0.0024978 | 0.000626 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_2770-27_0_6_load_197 | 211 | 0.0016847 | 0.00042222 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_2770-27_0_6_load_198 | 212 | 0.001312 | 0.00032882 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_2770-27_0_6_load_199 | 213 | 0.0034472 | 0.00086394 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_2770-27_0_6_load_225 | 214 | 0.003305 | 0.00082831 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_2770-27_0_6_load_201 | 215 | 0.0017099 | 0.00042855 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_2770-27_0_6_load_203 | 216 | 0.0021717 | 0.00054427 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_2770-27_0_6_load_209 | 218 | 0.0013432 | 0.00033665 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_2770-27_0_6_load_219 | 219 | 0.0012932 | 0.00032411 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_2770-27_0_6_load_221 | 220 | 0.0017237 | 0.000432 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_2770-27_0_6_load_220 | 221 | 0.001344 | 0.00033683 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_2770-27_0_6_load_218 | 222 | 0.0017384 | 0.0004357 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_2770-27_0_6_load_216 | 223 | 0.0017383 | 0.00043565 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_2770-27_0_6_load_217 | 224 | 0.0017381 | 0.00043561 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_2770-27_0_6_load_235 | 225 | 0.0015914 | 0.00039884 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_2770-27_0_6_load_244 | 226 | 0.0026683 | 0.00066874 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_2770-27_0_6_load_243 | 227 | 0.003791 | 0.00095011 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_2770-27_0_6_load_232 | 228 | 0.00078257 | 0.00019613 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_2770-27_0_6_load_229 | 229 | 0.0020929 | 0.00052452 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_2770-27_0_6_load_230 | 230 | 0.0020926 | 0.00052445 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_2770-27_0_6_load_234 | 231 | 0.0025758 | 0.00064555 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_2770-27_0_6_load_237 | 232 | 0.0013101 | 0.00032834 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_2770-27_0_6_load_236 | 233 | 0.003675 | 0.00092103 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_2770-27_0_6_load_238 | 234 | 0.0010327 | 0.00025881 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_2770-27_0_6_load_239 | 235 | 0.0014589 | 0.00036563 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_2770-27_0_6_load_241 | 237 | 0.0024313 | 0.00060935 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_2770-27_0_6_load_252 | 240 | 0.0038174 | 0.00095673 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_2770-27_0_6_load_248 | 242 | 0.0011264 | 0.00028231 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_2770-27_0_6_load_249 | 243 | 0.00068907 | 0.0001727 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 77 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2770-27_0_6_line_0 |  | 0 | 1 | 0.036779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2770-27_0_6_line_1 |  | 1 | 2 | 0.1175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2770-27_0_6_line_2 |  | 2 | 3 | 0.068824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2770-27_0_6_line_3 |  | 2 | 4 | 0.0082347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2770-27_0_6_line_4 |  | 3 | 169 | 0.079214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2770-27_0_6_line_5 |  | 5 | 6 | 0.0028882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2770-27_0_6_line_6 |  | 5 | 7 | 0.024875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2770-27_0_6_line_7 |  | 6 | 8 | 0.018964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2770-27_0_6_line_8 |  | 8 | 9 | 0.0071843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2770-27_0_6_line_9 |  | 9 | 10 | 0.01806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2770-27_0_6_line_10 |  | 10 | 107 | 0.037558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2770-27_0_6_line_11 |  | 11 | 12 | 0.011511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_2770-27_0_6_line_12 |  | 11 | 13 | 0.0099826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_2770-27_0_6_line_13 |  | 12 | 14 | 0.0096895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_2770-27_0_6_line_14 |  | 13 | 15 | 0.0084166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_2770-27_0_6_line_15 |  | 13 | 16 | 0.032414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_2770-27_0_6_line_16 |  | 14 | 17 | 0.0098587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_2770-27_0_6_line_17 |  | 15 | 18 | 0.050053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2770-27_0_6_line_18 |  | 16 | 19 | 0.011631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2770-27_0_6_line_19 |  | 16 | 20 | 0.009641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_2770-27_0_6_line_20 |  | 16 | 21 | 0.009889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2770-27_0_6_line_21 |  | 17 | 22 | 0.0036169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_2770-27_0_6_line_22 |  | 18 | 23 | 0.024516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2770-27_0_6_line_23 |  | 19 | 24 | 0.001264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2770-27_0_6_line_24 |  | 20 | 25 | 0.0093369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_2770-27_0_6_line_25 |  | 21 | 26 | 0.0096606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2770-27_0_6_line_26 |  | 22 | 29 | 0.015945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_2770-27_0_6_line_27 |  | 23 | 27 | 0.049605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_2770-27_0_6_line_28 |  | 24 | 223 | 0.011107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2770-27_0_6_line_29 |  | 25 | 217 | 0.001601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_2770-27_0_6_line_30 |  | 25 | 215 | 0.028486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2770-27_0_6_line_31 |  | 26 | 200 | 0.0026202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2770-27_0_6_line_32 |  | 27 | 28 | 0.0084688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2770-27_0_6_line_33 |  | 28 | 30 | 0.008028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2770-27_0_6_line_34 |  | 29 | 117 | 0.018354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_2770-27_0_6_line_35 |  | 30 | 31 | 0.0070566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2770-27_0_6_line_36 |  | 31 | 32 | 0.0094705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2770-27_0_6_line_37 |  | 32 | 33 | 0.033578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2770-27_0_6_line_38 |  | 33 | 34 | 0.008747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2770-27_0_6_line_39 |  | 34 | 35 | 0.017808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2770-27_0_6_line_40 |  | 35 | 36 | 0.014252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2770-27_0_6_line_41 |  | 35 | 37 | 0.00079286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2770-27_0_6_line_42 |  | 36 | 47 | 0.015283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2770-27_0_6_line_43 |  | 37 | 48 | 0.00059108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2770-27_0_6_line_44 |  | 38 | 39 | 0.0035094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2770-27_0_6_line_45 |  | 38 | 40 | 0.026405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2770-27_0_6_line_46 |  | 39 | 41 | 0.010062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2770-27_0_6_line_47 |  | 40 | 42 | 0.010429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2770-27_0_6_line_48 |  | 40 | 43 | 0.04082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2770-27_0_6_line_49 |  | 41 | 44 | 0.0061107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2770-27_0_6_line_50 |  | 43 | 45 | 0.018629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2770-27_0_6_line_51 |  | 45 | 46 | 0.0046085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2770-27_0_6_line_52 |  | 46 | 115 | 0.020658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2770-27_0_6_line_53 |  | 47 | 49 | 0.011203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2770-27_0_6_line_54 |  | 47 | 50 | 0.0087663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2770-27_0_6_line_55 |  | 48 | 51 | 0.02567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2770-27_0_6_line_56 |  | 50 | 52 | 0.0044166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2770-27_0_6_line_57 |  | 51 | 60 | 0.021109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2770-27_0_6_line_58 |  | 53 | 54 | 0.0011725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2770-27_0_6_line_59 |  | 53 | 55 | 0.018288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2770-27_0_6_line_60 |  | 55 | 56 | 0.024875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2770-27_0_6_line_61 |  | 55 | 57 | 0.0088502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2770-27_0_6_line_62 |  | 56 | 58 | 0.015216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2770-27_0_6_line_63 |  | 57 | 59 | 0.008269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2770-27_0_6_line_64 |  | 59 | 60 | 0.015265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2770-27_0_6_line_65 |  | 60 | 61 | 0.041311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2770-27_0_6_line_66 |  | 60 | 62 | 0.025135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2770-27_0_6_line_67 |  | 62 | 63 | 0.018576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2770-27_0_6_line_68 |  | 63 | 64 | 0.024622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2770-27_0_6_line_69 |  | 63 | 65 | 0.022693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2770-27_0_6_line_70 |  | 64 | 66 | 0.023666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2770-27_0_6_line_71 |  | 64 | 67 | 0.022729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2770-27_0_6_line_72 |  | 65 | 68 | 0.021658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2770-27_0_6_line_73 |  | 66 | 69 | 0.039349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2770-27_0_6_line_74 |  | 66 | 70 | 0.033536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2770-27_0_6_line_75 |  | 67 | 71 | 0.032472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2770-27_0_6_line_76 |  | 70 | 72 | 0.025815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2770-27_0_6_line_77 |  | 73 | 74 | 0.018519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2770-27_0_6_line_78 |  | 74 | 75 | 0.00077837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2770-27_0_6_line_79 |  | 75 | 94 | 0.00039602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2770-27_0_6_line_80 |  | 76 | 77 | 0.049395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2770-27_0_6_line_81 |  | 77 | 114 | 0.049651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_2770-27_0_6_line_82 |  | 78 | 79 | 0.064475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2770-27_0_6_line_83 |  | 79 | 102 | 0.019858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2770-27_0_6_line_84 |  | 79 | 103 | 0.026662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_2770-27_0_6_line_85 |  | 79 | 98 | 0.047603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_2770-27_0_6_line_86 |  | 80 | 81 | 0.00011595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_2770-27_0_6_line_87 |  | 80 | 82 | 0.040824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_2770-27_0_6_line_88 |  | 81 | 83 | 0.0577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_2770-27_0_6_line_89 |  | 82 | 84 | 0.049977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_2770-27_0_6_line_90 |  | 83 | 85 | 0.038888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
91 | LV_2770-27_0_6_line_91 |  | 83 | 86 | 0.0058484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2770-27_0_6_line_92 |  | 84 | 87 | 0.009626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_2770-27_0_6_line_93 |  | 84 | 88 | 0.046579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2770-27_0_6_line_94 |  | 85 | 89 | 0.019117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2770-27_0_6_line_95 |  | 86 | 90 | 0.011618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2770-27_0_6_line_96 |  | 87 | 91 | 0.01769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_2770-27_0_6_line_97 |  | 88 | 92 | 0.021888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2770-27_0_6_line_98 |  | 89 | 93 | 0.034041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2770-27_0_6_line_99 |  | 91 | 100 | 0.02844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_2770-27_0_6_line_100 |  | 92 | 101 | 0.026123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2770-27_0_6_line_101 |  | 93 | 116 | 0.028672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2770-27_0_6_line_102 |  | 94 | 95 | 0.021269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2770-27_0_6_line_103 |  | 95 | 96 | 0.003883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2770-27_0_6_line_104 |  | 96 | 97 | 0.01243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2770-27_0_6_line_105 |  | 97 | 98 | 0.026872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2770-27_0_6_line_106 |  | 98 | 99 | 0.011781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_2770-27_0_6_line_107 |  | 99 | 100 | 0.0042711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_2770-27_0_6_line_108 |  | 101 | 104 | 0.079146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2770-27_0_6_line_109 |  | 103 | 105 | 0.020987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_2770-27_0_6_line_110 |  | 104 | 106 | 0.024077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2770-27_0_6_line_111 |  | 104 | 107 | 0.039266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2770-27_0_6_line_112 |  | 105 | 111 | 0.030385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2770-27_0_6_line_113 |  | 105 | 112 | 0.026054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_2770-27_0_6_line_114 |  | 105 | 113 | 0.01059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2770-27_0_6_line_115 |  | 107 | 108 | 0.044962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2770-27_0_6_line_116 |  | 108 | 157 | 0.0033411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2770-27_0_6_line_117 |  | 109 | 110 | 0.02265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2770-27_0_6_line_118 |  | 110 | 144 | 0.043667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2770-27_0_6_line_119 |  | 111 | 149 | 0.013257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2770-27_0_6_line_120 |  | 112 | 143 | 0.016301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
121 | LV_2770-27_0_6_line_121 |  | 113 | 146 | 0.019954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2770-27_0_6_line_122 |  | 114 | 123 | 0.018257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_2770-27_0_6_line_123 |  | 115 | 116 | 0.049111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2770-27_0_6_line_124 |  | 117 | 118 | 0.0083921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
125 | LV_2770-27_0_6_line_125 |  | 118 | 119 | 0.012365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
126 | LV_2770-27_0_6_line_126 |  | 119 | 120 | 0.019344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
127 | LV_2770-27_0_6_line_127 |  | 120 | 121 | 0.031098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_2770-27_0_6_line_128 |  | 120 | 122 | 0.020133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2770-27_0_6_line_129 |  | 120 | 123 | 0.020887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_2770-27_0_6_line_130 |  | 121 | 124 | 0.0060567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
131 | LV_2770-27_0_6_line_131 |  | 124 | 125 | 0.017136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_2770-27_0_6_line_132 |  | 125 | 128 | 0.032037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
133 | LV_2770-27_0_6_line_133 |  | 126 | 127 | 0.0094455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2770-27_0_6_line_134 |  | 127 | 199 | 0.011952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2770-27_0_6_line_135 |  | 128 | 129 | 0.0038432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
136 | LV_2770-27_0_6_line_136 |  | 129 | 130 | 0.0059252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
137 | LV_2770-27_0_6_line_137 |  | 130 | 131 | 0.043052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
138 | LV_2770-27_0_6_line_138 |  | 131 | 135 | 0.046991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
139 | LV_2770-27_0_6_line_139 |  | 132 | 133 | 0.016955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2770-27_0_6_line_140 |  | 132 | 134 | 0.038689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2770-27_0_6_line_141 |  | 134 | 139 | 0.0097539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2770-27_0_6_line_142 |  | 134 | 140 | 0.005266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2770-27_0_6_line_143 |  | 135 | 136 | 0.021333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
144 | LV_2770-27_0_6_line_144 |  | 136 | 137 | 0.0087479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
145 | LV_2770-27_0_6_line_145 |  | 137 | 138 | 0.012271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
146 | LV_2770-27_0_6_line_146 |  | 138 | 141 | 0.026254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
147 | LV_2770-27_0_6_line_147 |  | 139 | 174 | 0.036643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2770-27_0_6_line_148 |  | 140 | 166 | 0.012053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2770-27_0_6_line_149 |  | 140 | 162 | 0.023253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2770-27_0_6_line_150 |  | 141 | 142 | 0.017094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
151 | LV_2770-27_0_6_line_151 |  | 142 | 143 | 0.0050096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
152 | LV_2770-27_0_6_line_152 |  | 144 | 145 | 0.012886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2770-27_0_6_line_153 |  | 145 | 155 | 0.040416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_2770-27_0_6_line_154 |  | 145 | 152 | 0.02642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_2770-27_0_6_line_155 |  | 146 | 147 | 0.0038742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_2770-27_0_6_line_156 |  | 147 | 148 | 0.01053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_2770-27_0_6_line_157 |  | 148 | 150 | 0.026049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_2770-27_0_6_line_158 |  | 149 | 151 | 0.024188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_2770-27_0_6_line_159 |  | 150 | 152 | 0.03761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_2770-27_0_6_line_160 |  | 150 | 153 | 0.010181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_2770-27_0_6_line_161 |  | 151 | 167 | 0.024338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_2770-27_0_6_line_162 |  | 151 | 161 | 0.034544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_2770-27_0_6_line_163 |  | 153 | 154 | 0.0012385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_2770-27_0_6_line_164 |  | 154 | 156 | 0.024393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_2770-27_0_6_line_165 |  | 156 | 159 | 0.0017473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_2770-27_0_6_line_166 |  | 157 | 158 | 0.033005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_2770-27_0_6_line_167 |  | 160 | 161 | 0.015757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_2770-27_0_6_line_168 |  | 162 | 163 | 0.004516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_2770-27_0_6_line_169 |  | 163 | 164 | 0.026865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_2770-27_0_6_line_170 |  | 163 | 165 | 0.039317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_2770-27_0_6_line_171 |  | 165 | 168 | 0.0076966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_2770-27_0_6_line_172 |  | 167 | 172 | 0.01474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_2770-27_0_6_line_173 |  | 168 | 173 | 0.014501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_2770-27_0_6_line_174 |  | 169 | 183 | 0.013855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_2770-27_0_6_line_175 |  | 170 | 171 | 0.029108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_2770-27_0_6_line_176 |  | 171 | 178 | 0.03018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_2770-27_0_6_line_177 |  | 172 | 173 | 0.0046749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_2770-27_0_6_line_178 |  | 174 | 175 | 0.024233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_2770-27_0_6_line_179 |  | 176 | 177 | 0.026606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_2770-27_0_6_line_180 |  | 177 | 192 | 0.024589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_2770-27_0_6_line_181 |  | 178 | 179 | 0.015441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_2770-27_0_6_line_182 |  | 179 | 180 | 0.026099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_2770-27_0_6_line_183 |  | 179 | 181 | 0.012186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_2770-27_0_6_line_184 |  | 181 | 182 | 0.037407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_2770-27_0_6_line_185 |  | 182 | 186 | 0.016206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_2770-27_0_6_line_186 |  | 183 | 231 | 0.0086825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_2770-27_0_6_line_187 |  | 183 | 229 | 0.039936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_2770-27_0_6_line_188 |  | 184 | 185 | 0.0058532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_2770-27_0_6_line_189 |  | 185 | 187 | 0.024242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_2770-27_0_6_line_190 |  | 186 | 189 | 0.034016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_2770-27_0_6_line_191 |  | 187 | 188 | 0.0077183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_2770-27_0_6_line_192 |  | 188 | 194 | 0.0090835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_2770-27_0_6_line_193 |  | 189 | 190 | 0.0078764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_2770-27_0_6_line_194 |  | 189 | 191 | 0.004846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_2770-27_0_6_line_195 |  | 190 | 225 | 0.029536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_2770-27_0_6_line_196 |  | 191 | 214 | 0.038035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_2770-27_0_6_line_197 |  | 191 | 213 | 0.016114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_2770-27_0_6_line_198 |  | 192 | 193 | 0.013245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_2770-27_0_6_line_199 |  | 193 | 196 | 0.011279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_2770-27_0_6_line_200 |  | 194 | 195 | 0.022612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_2770-27_0_6_line_201 |  | 195 | 205 | 0.007937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_2770-27_0_6_line_202 |  | 196 | 197 | 0.0089612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
203 | LV_2770-27_0_6_line_203 |  | 196 | 198 | 0.017943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
204 | LV_2770-27_0_6_line_204 |  | 197 | 201 | 0.029272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
205 | LV_2770-27_0_6_line_205 |  | 198 | 202 | 0.034616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
206 | LV_2770-27_0_6_line_206 |  | 199 | 200 | 0.0092377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_2770-27_0_6_line_207 |  | 201 | 203 | 0.01993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_2770-27_0_6_line_208 |  | 201 | 204 | 0.018904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
209 | LV_2770-27_0_6_line_209 |  | 202 | 205 | 0.007245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_2770-27_0_6_line_210 |  | 202 | 206 | 0.017336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
211 | LV_2770-27_0_6_line_211 |  | 203 | 207 | 0.010932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_2770-27_0_6_line_212 |  | 204 | 208 | 0.0078517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
213 | LV_2770-27_0_6_line_213 |  | 205 | 211 | 0.019906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_2770-27_0_6_line_214 |  | 208 | 209 | 0.013698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_2770-27_0_6_line_215 |  | 208 | 210 | 0.0217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
216 | LV_2770-27_0_6_line_216 |  | 209 | 220 | 0.015917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
217 | LV_2770-27_0_6_line_217 |  | 209 | 221 | 0.0030075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_2770-27_0_6_line_218 |  | 210 | 217 | 0.024065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
219 | LV_2770-27_0_6_line_219 |  | 211 | 212 | 0.0011447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_2770-27_0_6_line_220 |  | 212 | 213 | 0.041977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_2770-27_0_6_line_221 |  | 215 | 216 | 0.018066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_2770-27_0_6_line_222 |  | 217 | 218 | 0.019989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_2770-27_0_6_line_223 |  | 218 | 219 | 0.0021458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_2770-27_0_6_line_224 |  | 219 | 222 | 0.011186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_2770-27_0_6_line_225 |  | 223 | 224 | 0.00031149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
226 | LV_2770-27_0_6_line_226 |  | 225 | 228 | 0.021641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_2770-27_0_6_line_227 |  | 226 | 227 | 0.033496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_2770-27_0_6_line_228 |  | 227 | 239 | 0.020733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_2770-27_0_6_line_229 |  | 228 | 230 | 0.011086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_2770-27_0_6_line_230 |  | 229 | 230 | 0.039492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_2770-27_0_6_line_231 |  | 231 | 232 | 0.03367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_2770-27_0_6_line_232 |  | 232 | 233 | 0.0021818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
233 | LV_2770-27_0_6_line_233 |  | 233 | 234 | 0.018182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_2770-27_0_6_line_234 |  | 234 | 235 | 0.0049785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
235 | LV_2770-27_0_6_line_235 |  | 235 | 236 | 0.036291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_2770-27_0_6_line_236 |  | 236 | 237 | 0.032498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_2770-27_0_6_line_237 |  | 236 | 238 | 0.004626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_2770-27_0_6_line_238 |  | 238 | 239 | 0.002999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_2770-27_0_6_line_239 |  | 238 | 240 | 0.037853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_2770-27_0_6_line_240 |  | 240 | 241 | 0.070329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_2770-27_0_6_line_241 |  | 241 | 243 | 0.035866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_2770-27_0_6_line_242 |  | 242 | 243 | 0.048602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2770-27_0_6_trafo_105 | 0.63 MVA 20/0.4 kV | 244 | 77 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2616112.524 | 1262849.0678 | 2616111.2175 | 1262847.5188 | 2616088.8292 | 1262820.9385
1 | 2616041.9616 | 1262943.0191 | 2616112.524 | 1262849.0678
2 | 2615992.0295 | 1262931.8545 | 2616019.2609 | 1262914.4381 | 2616041.9616 | 1262943.0191
3 | 2616041.9616 | 1262943.0191 | 2616035.2586 | 1262947.8024
4 | 2615992.0295 | 1262931.8545 | 2615983.9433 | 1262944.5081 | 2615978.4558 | 1262957.1687 | 2615973.5594 | 1262974.0782 | 2615972.4075 | 1262987.8846 | 2615971.7388 | 1263006.8131
5 | 2615848.6548 | 1262644.8042 | 2615846.3368 | 1262646.5271
6 | 2615848.6548 | 1262644.8042 | 2615868.6194 | 1262629.9654
7 | 2615846.3368 | 1262646.5271 | 2615831.1162 | 1262657.8399
8 | 2615825.2994 | 1262662.0562 | 2615830.4968 | 1262658.3002 | 2615831.1162 | 1262657.8399
9 | 2615810.6616 | 1262672.6343 | 2615825.2994 | 1262662.0562
10 | 2615779.977 | 1262694.2793 | 2615787.636 | 1262689.274 | 2615810.6616 | 1262672.6343
11 | 2615679.9415 | 1263225.438 | 2615683.3286 | 1263214.4365 | 2615683.3286 | 1263214.4365
12 | 2615677.3764 | 1263235.0794 | 2615678.6563 | 1263229.6123 | 2615679.9415 | 1263225.438
13 | 2615683.3286 | 1263214.4365 | 2615686.7309 | 1263205.364
14 | 2615677.3764 | 1263235.0794 | 2615675.4553 | 1263243.2737
15 | 2615706.5863 | 1263234.7897 | 2615681.6851 | 1263232.1109 | 2615680.8012 | 1263235.9335 | 2615677.3764 | 1263235.0794
16 | 2615686.7309 | 1263205.364 | 2615688.244 | 1263201.3293 | 2615690.4893 | 1263196.2542
17 | 2615664.0301 | 1263292.0056 | 2615675.4553 | 1263243.2737
18 | 2615706.5863 | 1263234.7897 | 2615705.9835 | 1263237.7235 | 2615706.8871 | 1263246.3121
19 | 2615706.5863 | 1263234.7897 | 2615716.0943 | 1263236.3852
20 | 2615706.5863 | 1263234.7897 | 2615708.4402 | 1263225.8551 | 2615708.6334 | 1263225.1159
21 | 2615690.4893 | 1263196.2542 | 2615691.9526 | 1263192.9465
22 | 2615664.0301 | 1263292.0056 | 2615660.7494 | 1263290.785 | 2615640.9823 | 1263283.4611
23 | 2615706.8871 | 1263246.3121 | 2615707.0193 | 1263247.5691
24 | 2615725.3025 | 1263237.9303 | 2615716.0943 | 1263236.3852
25 | 2615711.0761 | 1263215.7692 | 2615708.6334 | 1263225.1159
26 | 2615691.9526 | 1263192.9465 | 2615698.4038 | 1263178.3646
27 | 2615640.9823 | 1263283.4611 | 2615637.4019 | 1263281.6505 | 2615633.2554 | 1263277.4144 | 2615630.9416 | 1263272.2826 | 2615627.4651 | 1263251.0143 | 2615627.0447 | 1263238.5361
28 | 2615707.0193 | 1263247.5691 | 2615707.4309 | 1263251.4812 | 2615707.7799 | 1263258.6458
29 | 2615725.3025 | 1263237.9303 | 2615724.9218 | 1263239.4859
30 | 2615725.3025 | 1263237.9303 | 2615731.6812 | 1263210.1676
31 | 2615711.0761 | 1263215.7692 | 2615711.7387 | 1263213.2341
32 | 2615627.0447 | 1263238.5361 | 2615626.7596 | 1263230.0721
33 | 2615626.7596 | 1263230.0721 | 2615626.4893 | 1263222.0487
34 | 2615705.8296 | 1263161.58 | 2615698.4038 | 1263178.3646
35 | 2615626.3358 | 1263214.9978 | 2615626.2775 | 1263215.7647 | 2615626.4893 | 1263222.0487
36 | 2615626.3358 | 1263214.9978 | 2615627.0536 | 1263205.5546
37 | 2615629.5985 | 1263172.0732 | 2615627.0536 | 1263205.5546
38 | 2615630.2614 | 1263163.3514 | 2615629.5985 | 1263172.0732
39 | 2615636.2439 | 1263146.6211 | 2615630.3426 | 1263162.283 | 2615630.2614 | 1263163.3514
40 | 2615636.2439 | 1263146.6211 | 2615622.1843 | 1263144.2878
41 | 2615636.5232 | 1263145.8791 | 2615636.2439 | 1263146.6211
42 | 2615607.1073 | 1263141.7856 | 2615622.1843 | 1263144.2878
43 | 2615636.7314 | 1263145.3259 | 2615636.5232 | 1263145.8791
44 | 2615559.401 | 1263192.6732 | 2615559.5369 | 1263189.1664
45 | 2615533.0028 | 1263192.0814 | 2615559.401 | 1263192.6732 | 2615559.401 | 1263192.6732
46 | 2615559.5369 | 1263189.1664 | 2615559.9266 | 1263179.1121
47 | 2615533.0028 | 1263192.0814 | 2615532.7193 | 1263202.5069
48 | 2615533.0028 | 1263192.0814 | 2615533.7612 | 1263164.1753 | 2615533.8094 | 1263151.2718
49 | 2615560.1632 | 1263173.006 | 2615559.9266 | 1263179.1121
50 | 2615533.8094 | 1263151.2718 | 2615533.8788 | 1263132.6429
51 | 2615533.896 | 1263128.0344 | 2615533.8788 | 1263132.6429
52 | 2615533.896 | 1263128.0344 | 2615533.9383 | 1263116.6764 | 2615535.5031 | 1263107.5093
53 | 2615607.1073 | 1263141.7856 | 2615604.992 | 1263152.7876
54 | 2615607.1073 | 1263141.7856 | 2615608.4575 | 1263133.1239
55 | 2615636.7314 | 1263145.3259 | 2615645.7752 | 1263121.3017
56 | 2615608.4575 | 1263133.1239 | 2615609.1377 | 1263128.76
57 | 2615653.2121 | 1263101.5459 | 2615645.7752 | 1263121.3017
58 | 2615605.2595 | 1263088.2559 | 2615604.1315 | 1263087.9359
59 | 2615622.3181 | 1263091.8357 | 2615621.6374 | 1263092.9013 | 2615605.2595 | 1263088.2559
60 | 2615622.3181 | 1263091.8357 | 2615629.1629 | 1263072.5849 | 2615624.9461 | 1263071.1838
61 | 2615622.3181 | 1263091.8357 | 2615630.7612 | 1263094.4894
62 | 2615610.5065 | 1263066.386 | 2615624.9461 | 1263071.1838
63 | 2615630.7612 | 1263094.4894 | 2615638.6497 | 1263096.9688
64 | 2615653.2121 | 1263101.5459 | 2615638.6497 | 1263096.9688
65 | 2615653.2121 | 1263101.5459 | 2615662.5177 | 1263108.8422 | 2615671.8694 | 1263118.6069 | 2615673.8354 | 1263124.2715 | 2615674.0726 | 1263134.2791
66 | 2615653.2121 | 1263101.5459 | 2615657.2779 | 1263090.7492 | 2615662.8148 | 1263078.3296
67 | 2615670.3786 | 1263061.3636 | 2615662.8148 | 1263078.3296
68 | 2615670.3786 | 1263061.3636 | 2615680.4032 | 1263038.8635
69 | 2615670.3786 | 1263061.3636 | 2615649.2875 | 1263052.9901
70 | 2615680.4032 | 1263038.8635 | 2615688.3289 | 1263021.0833 | 2615689.605 | 1263017.0728
71 | 2615680.4032 | 1263038.8635 | 2615659.2966 | 1263030.4293
72 | 2615649.2875 | 1263052.9901 | 2615629.1583 | 1263044.9985
73 | 2615689.605 | 1263017.0728 | 2615692.8103 | 1263006.9854 | 2615699.692 | 1262979.0557
74 | 2615689.605 | 1263017.0728 | 2615679.1835 | 1263012.998 | 2615680.7282 | 1263007.0758 | 2615678.9598 | 1263006.4373 | 2615677.2604 | 1263011.0694 | 2615668.4944 | 1263007.6442
75 | 2615629.1427 | 1263018.3799 | 2615659.2966 | 1263030.4293
76 | 2615644.5658 | 1262997.9676 | 2615652.7078 | 1263001.4758 | 2615668.4944 | 1263007.6442
77 | 2615715.2523 | 1262915.7606 | 2615719.603 | 1262897.7598
78 | 2615719.603 | 1262897.7598 | 2615719.7858 | 1262897.0032
79 | 2615719.7858 | 1262897.0032 | 2615719.8789 | 1262896.6183
80 | 2615748.6029 | 1262992.5517 | 2615748.1203 | 1263001.1501 | 2615746.7753 | 1263011.2424 | 2615743.063 | 1263025.0309 | 2615738.0458 | 1263040.5629
81 | 2615722.7841 | 1263087.8099 | 2615738.0458 | 1263040.5629
82 | 2615780.5044 | 1262835.8335 | 2615767.5899 | 1262896.7967 | 2615767.1557 | 1262898.9114
83 | 2615780.5044 | 1262835.8335 | 2615784.7021 | 1262820.9233 | 2615786.3888 | 1262816.8937
84 | 2615780.5044 | 1262835.8335 | 2615807.1342 | 1262837.1488
85 | 2615780.5044 | 1262835.8335 | 2615732.8147 | 1262833.5276
86 | 2615637.9471 | 1262914.7884 | 2615638.0306 | 1262914.708
87 | 2615638.0306 | 1262914.708 | 2615644.6302 | 1262908.3571 | 2615648.0892 | 1262902.0286 | 2615651.1507 | 1262892.2077 | 2615652.5482 | 1262878.111
88 | 2615601.8616 | 1262954.0315 | 2615609.6226 | 1262930.1022 | 2615613.6783 | 1262925.9989 | 2615619.457 | 1262922.6229 | 2615637.9471 | 1262914.7884
89 | 2615661.0919 | 1262830.0245 | 2615653.7418 | 1262843.6923 | 2615653.2555 | 1262870.9764 | 2615652.5482 | 1262878.111
90 | 2615601.8616 | 1262954.0315 | 2615599.1957 | 1262962.4081 | 2615599.0137 | 1262962.8746 | 2615588.4043 | 1262990.5049
91 | 2615601.8616 | 1262954.0315 | 2615607.12 | 1262956.5916 | 2615607.12 | 1262956.5916
92 | 2615661.0919 | 1262830.0245 | 2615670.7065 | 1262830.4941
93 | 2615661.0919 | 1262830.0245 | 2615666.1257 | 1262820.6758 | 2615692.2073 | 1262795.9176
94 | 2615579.4696 | 1263007.1495 | 2615584.3079 | 1263001.1734 | 2615588.4043 | 1262990.5049
95 | 2615607.12 | 1262956.5916 | 2615607.2636 | 1262962.118 | 2615605.6818 | 1262967.9983
96 | 2615670.7065 | 1262830.4941 | 2615688.3759 | 1262831.3571
97 | 2615692.2073 | 1262795.9176 | 2615697.0793 | 1262791.2929 | 2615707.0521 | 1262785.7266 | 2615710.6802 | 1262784.7802
98 | 2615559.0021 | 1263034.2164 | 2615561.2673 | 1263029.6325 | 2615579.4696 | 1263007.1495
99 | 2615716.7818 | 1262832.7445 | 2615688.3759 | 1262831.3571
100 | 2615736.484 | 1262782.0686 | 2615720.1753 | 1262782.3034 | 2615710.6802 | 1262784.7802
101 | 2615546.2996 | 1263059.9215 | 2615559.0021 | 1263034.2164
102 | 2615719.8789 | 1262896.6183 | 2615724.8756 | 1262875.9446
103 | 2615724.8756 | 1262875.9446 | 2615725.7879 | 1262872.1703
104 | 2615728.5964 | 1262860.0662 | 2615728.3718 | 1262861.4795 | 2615725.7879 | 1262872.1703
105 | 2615732.8147 | 1262833.5276 | 2615728.5964 | 1262860.0662
106 | 2615732.8147 | 1262833.5276 | 2615721.0478 | 1262832.9529
107 | 2615716.7818 | 1262832.7445 | 2615721.0478 | 1262832.9529
108 | 2615736.484 | 1262782.0686 | 2615740.6721 | 1262782.0798 | 2615758.8507 | 1262732.9275 | 2615765.4058 | 1262720.9367 | 2615774.2779 | 1262721.4273
109 | 2615828.0961 | 1262838.1841 | 2615807.1342 | 1262837.1488
110 | 2615774.2779 | 1262721.4273 | 2615792.3461 | 1262705.4532
111 | 2615779.977 | 1262694.2793 | 2615765.4058 | 1262720.9367 | 2615774.2779 | 1262721.4273
112 | 2615828.0961 | 1262838.1841 | 2615858.4166 | 1262840.1663
113 | 2615828.0961 | 1262838.1841 | 2615821.6006 | 1262863.4153
114 | 2615828.0961 | 1262838.1841 | 2615831.6733 | 1262828.2166
115 | 2615779.977 | 1262694.2793 | 2615785.867 | 1262680.3521 | 2615796.2825 | 1262655.7295 | 2615797.5924 | 1262652.9139
116 | 2615799.0017 | 1262649.8846 | 2615797.5924 | 1262652.9139
117 | 2615827.3812 | 1262761.15 | 2615829.6862 | 1262758.8338 | 2615844.4202 | 1262747.4875 | 2615845.0725 | 1262747.049
118 | 2615845.0725 | 1262747.049 | 2615859.1654 | 1262737.5756 | 2615884.036 | 1262727.9023
119 | 2615869.5312 | 1262847.392 | 2615858.4166 | 1262840.1663 | 2615858.4166 | 1262840.1663
120 | 2615821.6006 | 1262863.4153 | 2615817.5367 | 1262879.2011
121 | 2615831.6733 | 1262828.2166 | 2615837.7796 | 1262811.2025 | 2615838.4397 | 1262809.4446
122 | 2615719.9472 | 1263105.7549 | 2615720.1617 | 1263100.1552 | 2615721.5248 | 1263091.7086 | 2615722.7841 | 1263087.8099
123 | 2615535.5031 | 1263107.5093 | 2615542.2151 | 1263068.1869 | 2615546.2996 | 1263059.9215
124 | 2615705.8296 | 1263161.58 | 2615709.2249 | 1263153.9054
125 | 2615714.2276 | 1263142.5976 | 2615709.2249 | 1263153.9054
126 | 2615724.2131 | 1263126.0727 | 2615720.8097 | 1263131.3451 | 2615715.7045 | 1263139.2592 | 2615714.2276 | 1263142.5976
127 | 2615724.2131 | 1263126.0727 | 2615735.761 | 1263114.2729 | 2615745.903 | 1263103.7875
128 | 2615724.2131 | 1263126.0727 | 2615726.8669 | 1263133.6516 | 2615729.4705 | 1263143.1317 | 2615729.2325 | 1263145.3908
129 | 2615724.2131 | 1263126.0727 | 2615721.0543 | 1263115.7683 | 2615719.8542 | 1263108.1821 | 2615719.9472 | 1263105.7549
130 | 2615750.297 | 1263099.6203 | 2615746.4559 | 1263103.2159 | 2615745.903 | 1263103.7875
131 | 2615750.297 | 1263099.6203 | 2615762.8069 | 1263087.9101
132 | 2615762.8069 | 1263087.9101 | 2615784.0144 | 1263068.0581 | 2615786.1155 | 1263065.9335
133 | 2615719.4848 | 1263183.5949 | 2615717.0964 | 1263192.7334
134 | 2615714.0744 | 1263204.2966 | 2615717.0964 | 1263192.7334
135 | 2615788.8178 | 1263063.2009 | 2615788.8178 | 1263063.2009 | 2615786.1155 | 1263065.9335
136 | 2615790.9416 | 1263057.6694 | 2615788.8178 | 1263063.2009
137 | 2615790.9416 | 1263057.6694 | 2615792.8857 | 1263040.396 | 2615795.5842 | 1263014.8689
138 | 2615800.5241 | 1262968.1383 | 2615795.5842 | 1263014.8689
139 | 2615821.5824 | 1263004.103 | 2615819.2558 | 1263012.258 | 2615822.24 | 1263020.1936
140 | 2615843.1535 | 1262987.6937 | 2615830.8947 | 1263008.8644 | 2615822.24 | 1263020.1936
141 | 2615843.1535 | 1262987.6937 | 2615847.6612 | 1262992.0643 | 2615847.0283 | 1262995.4814
142 | 2615843.1535 | 1262987.6937 | 2615845.9223 | 1262983.2091
143 | 2615800.5241 | 1262968.1383 | 2615802.2507 | 1262951.8044 | 2615802.8812 | 1262946.9373
144 | 2615804.0051 | 1262938.2619 | 2615802.8812 | 1262946.9373
145 | 2615804.0051 | 1262938.2619 | 2615804.9116 | 1262931.2641 | 2615806.1579 | 1262926.2003
146 | 2615812.3465 | 1262900.6861 | 2615810.105 | 1262910.1634 | 2615806.1579 | 1262926.2003
147 | 2615847.0283 | 1262995.4814 | 2615846.9963 | 1262995.6539 | 2615834.8686 | 1263015.6797 | 2615830.4267 | 1263027.9567
148 | 2615845.9223 | 1262983.2091 | 2615843.6843 | 1262980.7459 | 2615840.4927 | 1262974.2996 | 2615840.8797 | 1262972.818
149 | 2615858.3054 | 1262963.5064 | 2615850.7412 | 1262975.4055 | 2615845.9223 | 1262983.2091
150 | 2615816.2878 | 1262884.0526 | 2615816.1996 | 1262884.3952 | 2615812.3465 | 1262900.6861
151 | 2615816.2878 | 1262884.0526 | 2615817.5367 | 1262879.2011
152 | 2615896.046 | 1262723.2311 | 2615884.036 | 1262727.9023
153 | 2615896.046 | 1262723.2311 | 2615931.1437 | 1262703.192
154 | 2615896.046 | 1262723.2311 | 2615879.131 | 1262743.5262
155 | 2615839.8017 | 1262805.8177 | 2615838.4397 | 1262809.4446
156 | 2615839.8017 | 1262805.8177 | 2615843.5035 | 1262795.9602
157 | 2615856.0949 | 1262773.1697 | 2615850.4954 | 1262782.6612 | 2615843.6819 | 1262795.4852 | 2615843.5035 | 1262795.9602
158 | 2615889.8102 | 1262860.5754 | 2615869.5312 | 1262847.392
159 | 2615856.0949 | 1262773.1697 | 2615859.5151 | 1262767.3637 | 2615871.3953 | 1262752.8077 | 2615879.131 | 1262743.5262
160 | 2615856.0949 | 1262773.1697 | 2615864.9549 | 1262778.1857
161 | 2615889.8102 | 1262860.5754 | 2615881.108 | 1262872.6271 | 2615876.802 | 1262881.0652
162 | 2615889.8102 | 1262860.5754 | 2615892.3514 | 1262856.7018 | 2615917.837 | 1262872.3586
163 | 2615864.9549 | 1262778.1857 | 2615864.9549 | 1262778.1857 | 2615865.6402 | 1262777.1541
164 | 2615883.8733 | 1262778.3829 | 2615875.3252 | 1262773.3323 | 2615870.1137 | 1262770.1161 | 2615867.6095 | 1262774.19 | 2615865.6402 | 1262777.1541
165 | 2615885.3777 | 1262779.2718 | 2615883.8733 | 1262778.3829
166 | 2615799.0017 | 1262649.8846 | 2615812.9234 | 1262619.9595
167 | 2615917.837 | 1262872.3586 | 2615910.9355 | 1262881.4352 | 2615908.5729 | 1262885.0931
168 | 2615858.3054 | 1262963.5064 | 2615858.4304 | 1262958.9925
169 | 2615858.4304 | 1262958.9925 | 2615841.8231 | 1262955.6014 | 2615839.5835 | 1262953.7275 | 2615840.2299 | 1262946.7623
170 | 2615858.4304 | 1262958.9925 | 2615858.8959 | 1262942.6603 | 2615861.3725 | 1262923.5316 | 2615862.4045 | 1262919.9889
171 | 2615864.5573 | 1262912.5995 | 2615862.4045 | 1262919.9889
172 | 2615876.802 | 1262881.0652 | 2615871.9684 | 1262890.5372 | 2615870.5953 | 1262894.4067
173 | 2615869.0319 | 1262898.8124 | 2615866.4735 | 1262906.022 | 2615864.5573 | 1262912.5995
174 | 2615971.2496 | 1263020.6596 | 2615971.7388 | 1263006.8131
175 | 2615910.0737 | 1263014.8863 | 2615919.0822 | 1262987.2071
176 | 2615910.0737 | 1263014.8863 | 2615909.2983 | 1263017.2687 | 2615903.8155 | 1263044.3951
177 | 2615869.0319 | 1262898.8124 | 2615870.5953 | 1262894.4067
178 | 2615830.4267 | 1263027.9567 | 2615822.1819 | 1263050.7444
179 | 2615803.9018 | 1263104.6786 | 2615795.5472 | 1263129.9389
180 | 2615795.5472 | 1263129.9389 | 2615787.8261 | 1263153.2838
181 | 2615900.7564 | 1263059.5304 | 2615903.8155 | 1263044.3951
182 | 2615900.7564 | 1263059.5304 | 2615885.6602 | 1263057.3218 | 2615875.1067 | 1263054.8363
183 | 2615900.7564 | 1263059.5304 | 2615899.7911 | 1263071.678
184 | 2615899.7911 | 1263071.678 | 2615899.5559 | 1263074.6376 | 2615899.7197 | 1263089.4038 | 2615899.6847 | 1263102.4905 | 2615900.7031 | 1263108.9955
185 | 2615903.3415 | 1263124.9757 | 2615903.0615 | 1263124.0588 | 2615900.7031 | 1263108.9955
186 | 2615971.2496 | 1263020.6596 | 2615970.9703 | 1263029.3376
187 | 2615971.2496 | 1263020.6596 | 2615958.843 | 1263040.6177 | 2615951.6369 | 1263055.3902
188 | 2615849.6004 | 1263106.457 | 2615849.7144 | 1263106.0259 | 2615852.1172 | 1263101.1819
189 | 2615849.6004 | 1263106.457 | 2615843.4029 | 1263129.893
190 | 2615913.2757 | 1263157.5092 | 2615903.3415 | 1263124.9757
191 | 2615843.4029 | 1263129.893 | 2615841.4297 | 1263137.3548
192 | 2615839.1074 | 1263146.1364 | 2615841.4297 | 1263137.3548
193 | 2615913.2757 | 1263157.5092 | 2615915.519 | 1263149.959
194 | 2615913.2757 | 1263157.5092 | 2615911.2829 | 1263161.9291
195 | 2615922.4512 | 1263121.2559 | 2615921.2386 | 1263126.1201 | 2615916.7417 | 1263145.8438 | 2615915.519 | 1263149.959
196 | 2615911.2829 | 1263161.9291 | 2615895.6344 | 1263196.5964
197 | 2615911.2829 | 1263161.9291 | 2615895.4318 | 1263164.8252
198 | 2615783.667 | 1263165.8587 | 2615787.8261 | 1263153.2838
199 | 2615780.1254 | 1263176.5669 | 2615783.667 | 1263165.8587
200 | 2615834.9058 | 1263168.3542 | 2615839.1074 | 1263146.1364 | 2615839.1074 | 1263146.1364
201 | 2615833.431 | 1263176.153 | 2615834.9058 | 1263168.3542
202 | 2615780.1254 | 1263176.5669 | 2615777.3123 | 1263185.0751
203 | 2615780.1254 | 1263176.5669 | 2615797.9208 | 1263178.8652
204 | 2615772.6975 | 1263213.8728 | 2615773.2759 | 1263208.782 | 2615775.2734 | 1263191.2419 | 2615777.3123 | 1263185.0751
205 | 2615832.2519 | 1263183.2992 | 2615797.9208 | 1263178.8652
206 | 2615714.0744 | 1263204.2966 | 2615711.7387 | 1263213.2341
207 | 2615772.6975 | 1263213.8728 | 2615782.9553 | 1263214.167 | 2615790.0864 | 1263214.8419 | 2615792.5845 | 1263215.0317
208 | 2615772.6975 | 1263213.8728 | 2615770.571 | 1263232.657
209 | 2615833.431 | 1263176.153 | 2615832.7511 | 1263179.7314 | 2615832.2519 | 1263183.2992
210 | 2615832.2519 | 1263183.2992 | 2615829.8396 | 1263200.467
211 | 2615800.8951 | 1263220.3968 | 2615799.7189 | 1263218.0253 | 2615797.2177 | 1263215.3835 | 2615792.5845 | 1263215.0317
212 | 2615770.6759 | 1263240.4969 | 2615770.4375 | 1263233.8361 | 2615770.571 | 1263232.657
213 | 2615833.431 | 1263176.153 | 2615853.0128 | 1263172.5753
214 | 2615771.1668 | 1263254.1854 | 2615770.6759 | 1263240.4969
215 | 2615770.6759 | 1263240.4969 | 2615748.981 | 1263240.0175
216 | 2615771.1668 | 1263254.1854 | 2615787.0839 | 1263254.2912
217 | 2615771.1668 | 1263254.1854 | 2615771.2745 | 1263257.191
218 | 2615724.9218 | 1263239.4859 | 2615748.981 | 1263240.0175
219 | 2615853.0128 | 1263172.5753 | 2615854.1388 | 1263172.3696
220 | 2615854.1388 | 1263172.3696 | 2615895.4318 | 1263164.8252
221 | 2615735.7266 | 1263192.56 | 2615731.6812 | 1263210.1676
222 | 2615724.9218 | 1263239.4859 | 2615724.7695 | 1263240.1082 | 2615726.0619 | 1263259.4134
223 | 2615726.2052 | 1263261.5544 | 2615726.0619 | 1263259.4134
224 | 2615727.0053 | 1263272.7079 | 2615726.9285 | 1263272.3583 | 2615726.2052 | 1263261.5544
225 | 2615707.795 | 1263258.9569 | 2615707.7799 | 1263258.6458
226 | 2615929.4096 | 1263100.808 | 2615924.2994 | 1263113.842 | 2615922.4512 | 1263121.2559
227 | 2615977.8792 | 1263132.2294 | 2615960.5534 | 1263135.5877 | 2615961.9707 | 1263151.3715
228 | 2615998.2337 | 1263128.2841 | 2615977.8792 | 1263132.2294
229 | 2615934.1229 | 1263090.785 | 2615930.6094 | 1263097.7479 | 2615929.4096 | 1263100.808
230 | 2615951.6369 | 1263055.3902 | 2615941.5744 | 1263076.0179 | 2615934.1229 | 1263090.785
231 | 2615979.0067 | 1263061.7589 | 2615974.7831 | 1263048.3104 | 2615970.7811 | 1263035.2128 | 2615970.9703 | 1263029.3376
232 | 2615979.6604 | 1263063.8405 | 2615979.0067 | 1263061.7589
233 | 2615979.6604 | 1263063.8405 | 2615985.1082 | 1263081.1872
234 | 2615986.5998 | 1263085.937 | 2615985.1082 | 1263081.1872
235 | 2615996.2199 | 1263120.9292 | 2615987.001 | 1263087.2145 | 2615986.5998 | 1263085.937
236 | 2615996.2199 | 1263120.9292 | 2616010.6002 | 1263117.599 | 2616016.135 | 1263115.2901 | 2616016.4884 | 1263109.954 | 2616015.0441 | 1263103.668
237 | 2615997.4431 | 1263125.3911 | 2615996.2199 | 1263120.9292
238 | 2615997.4431 | 1263125.3911 | 2615998.2337 | 1263128.2841
239 | 2615997.4431 | 1263125.3911 | 2616034.3268 | 1263116.88
240 | 2616086.6972 | 1263126.055 | 2616044.4449 | 1263136.0586 | 2616040.1167 | 1263115.5439 | 2616034.3268 | 1263116.88
241 | 2616086.6972 | 1263126.055 | 2616080.8922 | 1263090.6616
242 | 2616075.5921 | 1263042.4816 | 2616075.716 | 1263059.1014 | 2616080.8922 | 1263090.6616

## bus_geodata
| x | y | coords
0 | 2616088.8292 | 1262820.9385
1 | 2616112.524 | 1262849.0678
2 | 2616041.9616 | 1262943.0191
3 | 2615992.0295 | 1262931.8545
4 | 2616035.2586 | 1262947.8024
5 | 2615848.6548 | 1262644.8042
6 | 2615846.3368 | 1262646.5271
7 | 2615868.6194 | 1262629.9654
8 | 2615831.1162 | 1262657.8399
9 | 2615825.2994 | 1262662.0562
10 | 2615810.6616 | 1262672.6343
11 | 2615679.9415 | 1263225.438
12 | 2615683.3286 | 1263214.4365
13 | 2615677.3764 | 1263235.0794
14 | 2615686.7309 | 1263205.364
15 | 2615675.4553 | 1263243.2737
16 | 2615706.5863 | 1263234.7897
17 | 2615690.4893 | 1263196.2542
18 | 2615664.0301 | 1263292.0056
19 | 2615706.8871 | 1263246.3121
20 | 2615716.0943 | 1263236.3852
21 | 2615708.6334 | 1263225.1159
22 | 2615691.9526 | 1263192.9465
23 | 2615640.9823 | 1263283.4611
24 | 2615707.0193 | 1263247.5691
25 | 2615725.3025 | 1263237.9303
26 | 2615711.0761 | 1263215.7692
27 | 2615627.0447 | 1263238.5361
28 | 2615626.7596 | 1263230.0721
29 | 2615698.4038 | 1263178.3646
30 | 2615626.4893 | 1263222.0487
31 | 2615626.3358 | 1263214.9978
32 | 2615627.0536 | 1263205.5546
33 | 2615629.5985 | 1263172.0732
34 | 2615630.2614 | 1263163.3514
35 | 2615636.2439 | 1263146.6211
36 | 2615622.1843 | 1263144.2878
37 | 2615636.5232 | 1263145.8791
38 | 2615559.401 | 1263192.6732
39 | 2615559.5369 | 1263189.1664
40 | 2615533.0028 | 1263192.0814
41 | 2615559.9266 | 1263179.1121
42 | 2615532.7193 | 1263202.5069
43 | 2615533.8094 | 1263151.2718
44 | 2615560.1632 | 1263173.006
45 | 2615533.8788 | 1263132.6429
46 | 2615533.896 | 1263128.0344
47 | 2615607.1073 | 1263141.7856
48 | 2615636.7314 | 1263145.3259
49 | 2615604.992 | 1263152.7876
50 | 2615608.4575 | 1263133.1239
51 | 2615645.7752 | 1263121.3017
52 | 2615609.1377 | 1263128.76
53 | 2615605.2595 | 1263088.2559
54 | 2615604.1315 | 1263087.9359
55 | 2615622.3181 | 1263091.8357
56 | 2615624.9461 | 1263071.1838
57 | 2615630.7612 | 1263094.4894
58 | 2615610.5065 | 1263066.386
59 | 2615638.6497 | 1263096.9688
60 | 2615653.2121 | 1263101.5459
61 | 2615674.0726 | 1263134.2791
62 | 2615662.8148 | 1263078.3296
63 | 2615670.3786 | 1263061.3636
64 | 2615680.4032 | 1263038.8635
65 | 2615649.2875 | 1263052.9901
66 | 2615689.605 | 1263017.0728
67 | 2615659.2966 | 1263030.4293
68 | 2615629.1583 | 1263044.9985
69 | 2615699.692 | 1262979.0557
70 | 2615668.4944 | 1263007.6442
71 | 2615629.1427 | 1263018.3799
72 | 2615644.5658 | 1262997.9676
73 | 2615715.2523 | 1262915.7606
74 | 2615719.603 | 1262897.7598
75 | 2615719.7858 | 1262897.0032
76 | 2615748.6029 | 1262992.5517
77 | 2615738.0458 | 1263040.5629
78 | 2615767.1557 | 1262898.9114
79 | 2615780.5044 | 1262835.8335
80 | 2615638.0306 | 1262914.708
81 | 2615637.9471 | 1262914.7884
82 | 2615652.5482 | 1262878.111
83 | 2615601.8616 | 1262954.0315
84 | 2615661.0919 | 1262830.0245
85 | 2615588.4043 | 1262990.5049
86 | 2615607.12 | 1262956.5916
87 | 2615670.7065 | 1262830.4941
88 | 2615692.2073 | 1262795.9176
89 | 2615579.4696 | 1263007.1495
90 | 2615605.6818 | 1262967.9983
91 | 2615688.3759 | 1262831.3571
92 | 2615710.6802 | 1262784.7802
93 | 2615559.0021 | 1263034.2164
94 | 2615719.8789 | 1262896.6183
95 | 2615724.8756 | 1262875.9446
96 | 2615725.7879 | 1262872.1703
97 | 2615728.5964 | 1262860.0662
98 | 2615732.8147 | 1262833.5276
99 | 2615721.0478 | 1262832.9529
100 | 2615716.7818 | 1262832.7445
101 | 2615736.484 | 1262782.0686
102 | 2615786.3888 | 1262816.8937
103 | 2615807.1342 | 1262837.1488
104 | 2615774.2779 | 1262721.4273
105 | 2615828.0961 | 1262838.1841
106 | 2615792.3461 | 1262705.4532
107 | 2615779.977 | 1262694.2793
108 | 2615797.5924 | 1262652.9139
109 | 2615827.3812 | 1262761.15
110 | 2615845.0725 | 1262747.049
111 | 2615858.4166 | 1262840.1663
112 | 2615821.6006 | 1262863.4153
113 | 2615831.6733 | 1262828.2166
114 | 2615722.7841 | 1263087.8099
115 | 2615535.5031 | 1263107.5093
116 | 2615546.2996 | 1263059.9215
117 | 2615705.8296 | 1263161.58
118 | 2615709.2249 | 1263153.9054
119 | 2615714.2276 | 1263142.5976
120 | 2615724.2131 | 1263126.0727
121 | 2615745.903 | 1263103.7875
122 | 2615729.2325 | 1263145.3908
123 | 2615719.9472 | 1263105.7549
124 | 2615750.297 | 1263099.6203
125 | 2615762.8069 | 1263087.9101
126 | 2615719.4848 | 1263183.5949
127 | 2615717.0964 | 1263192.7334
128 | 2615786.1155 | 1263065.9335
129 | 2615788.8178 | 1263063.2009
130 | 2615790.9416 | 1263057.6694
131 | 2615795.5842 | 1263014.8689
132 | 2615822.24 | 1263020.1936
133 | 2615821.5824 | 1263004.103
134 | 2615843.1535 | 1262987.6937
135 | 2615800.5241 | 1262968.1383
136 | 2615802.8812 | 1262946.9373
137 | 2615804.0051 | 1262938.2619
138 | 2615806.1579 | 1262926.2003
139 | 2615847.0283 | 1262995.4814
140 | 2615845.9223 | 1262983.2091
141 | 2615812.3465 | 1262900.6861
142 | 2615816.2878 | 1262884.0526
143 | 2615817.5367 | 1262879.2011
144 | 2615884.036 | 1262727.9023
145 | 2615896.046 | 1262723.2311
146 | 2615838.4397 | 1262809.4446
147 | 2615839.8017 | 1262805.8177
148 | 2615843.5035 | 1262795.9602
149 | 2615869.5312 | 1262847.392
150 | 2615856.0949 | 1262773.1697
151 | 2615889.8102 | 1262860.5754
152 | 2615879.131 | 1262743.5262
153 | 2615864.9549 | 1262778.1857
154 | 2615865.6402 | 1262777.1541
155 | 2615931.1437 | 1262703.192
156 | 2615883.8733 | 1262778.3829
157 | 2615799.0017 | 1262649.8846
158 | 2615812.9234 | 1262619.9595
159 | 2615885.3777 | 1262779.2718
160 | 2615908.5729 | 1262885.0931
161 | 2615917.837 | 1262872.3586
162 | 2615858.3054 | 1262963.5064
163 | 2615858.4304 | 1262958.9925
164 | 2615840.2299 | 1262946.7623
165 | 2615862.4045 | 1262919.9889
166 | 2615840.8797 | 1262972.818
167 | 2615876.802 | 1262881.0652
168 | 2615864.5573 | 1262912.5995
169 | 2615971.7388 | 1263006.8131
170 | 2615919.0822 | 1262987.2071
171 | 2615910.0737 | 1263014.8863
172 | 2615870.5953 | 1262894.4067
173 | 2615869.0319 | 1262898.8124
174 | 2615830.4267 | 1263027.9567
175 | 2615822.1819 | 1263050.7444
176 | 2615803.9018 | 1263104.6786
177 | 2615795.5472 | 1263129.9389
178 | 2615903.8155 | 1263044.3951
179 | 2615900.7564 | 1263059.5304
180 | 2615875.1067 | 1263054.8363
181 | 2615899.7911 | 1263071.678
182 | 2615900.7031 | 1263108.9955
183 | 2615971.2496 | 1263020.6596
184 | 2615852.1172 | 1263101.1819
185 | 2615849.6004 | 1263106.457
186 | 2615903.3415 | 1263124.9757
187 | 2615843.4029 | 1263129.893
188 | 2615841.4297 | 1263137.3548
189 | 2615913.2757 | 1263157.5092
190 | 2615915.519 | 1263149.959
191 | 2615911.2829 | 1263161.9291
192 | 2615787.8261 | 1263153.2838
193 | 2615783.667 | 1263165.8587
194 | 2615839.1074 | 1263146.1364
195 | 2615834.9058 | 1263168.3542
196 | 2615780.1254 | 1263176.5669
197 | 2615777.3123 | 1263185.0751
198 | 2615797.9208 | 1263178.8652
199 | 2615714.0744 | 1263204.2966
200 | 2615711.7387 | 1263213.2341
201 | 2615772.6975 | 1263213.8728
202 | 2615832.2519 | 1263183.2992
203 | 2615792.5845 | 1263215.0317
204 | 2615770.571 | 1263232.657
205 | 2615833.431 | 1263176.153
206 | 2615829.8396 | 1263200.467
207 | 2615800.8951 | 1263220.3967
208 | 2615770.6759 | 1263240.4969
209 | 2615771.1668 | 1263254.1854
210 | 2615748.981 | 1263240.0175
211 | 2615853.0128 | 1263172.5753
212 | 2615854.1388 | 1263172.3696
213 | 2615895.4318 | 1263164.8252
214 | 2615895.6344 | 1263196.5964
215 | 2615731.6812 | 1263210.1676
216 | 2615735.7266 | 1263192.56
217 | 2615724.9218 | 1263239.4859
218 | 2615726.0619 | 1263259.4134
219 | 2615726.2052 | 1263261.5544
220 | 2615787.0839 | 1263254.2912
221 | 2615771.2745 | 1263257.191
222 | 2615727.0053 | 1263272.7079
223 | 2615707.7799 | 1263258.6458
224 | 2615707.795 | 1263258.9569
225 | 2615922.4512 | 1263121.2559
226 | 2615961.9707 | 1263151.3715
227 | 2615977.8792 | 1263132.2294
228 | 2615929.4096 | 1263100.808
229 | 2615951.6369 | 1263055.3902
230 | 2615934.1229 | 1263090.785
231 | 2615970.9703 | 1263029.3376
232 | 2615979.0067 | 1263061.7589
233 | 2615979.6604 | 1263063.8405
234 | 2615985.1082 | 1263081.1872
235 | 2615986.5998 | 1263085.937
236 | 2615996.2199 | 1263120.9292
237 | 2616015.0441 | 1263103.668
238 | 2615997.4431 | 1263125.3911
239 | 2615998.2337 | 1263128.2841
240 | 2616034.3268 | 1263116.88
241 | 2616086.6972 | 1263126.055
242 | 2616075.5921 | 1263042.4816
243 | 2616080.8922 | 1263090.6616
244 | 2615748.6974 | 1262990.8668

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1