## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2771-18_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2771-18_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2771-18_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2771-18_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2771-18_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2771-18_0_5_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_2771-18_0_5_node_45 | 0.4 | n |  | TRUE
7 | bus_LV_2771-18_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2771-18_0_5_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_2771-18_0_5_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_2771-18_0_5_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_2771-18_0_5_node_97 | 0.4 | n |  | TRUE
12 | bus_LV_2771-18_0_5_node_98 | 0.4 | n |  | TRUE
13 | bus_LV_2771-18_0_5_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_2771-18_0_5_node_49 | 0.4 | n |  | TRUE
15 | bus_LV_2771-18_0_5_node_96 | 0.4 | n |  | TRUE
16 | bus_LV_2771-18_0_5_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2771-18_0_5_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2771-18_0_5_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2771-18_0_5_node_6 | 0.4 | n |  | TRUE
20 | bus_LV_2771-18_0_5_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_2771-18_0_5_node_7 | 0.4 | n |  | TRUE
22 | bus_LV_2771-18_0_5_node_8 | 0.4 | n |  | TRUE
23 | bus_LV_2771-18_0_5_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_2771-18_0_5_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_2771-18_0_5_node_91 | 0.4 | n |  | TRUE
26 | bus_LV_2771-18_0_5_node_59 | 0.4 | n |  | TRUE
27 | bus_LV_2771-18_0_5_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_2771-18_0_5_node_114 | 0.4 | n |  | TRUE
29 | bus_LV_2771-18_0_5_node_61 | 0.4 | n |  | TRUE
30 | bus_LV_2771-18_0_5_node_57 | 0.4 | n |  | TRUE
31 | bus_LV_2771-18_0_5_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_2771-18_0_5_node_90 | 0.4 | n |  | TRUE
33 | bus_LV_2771-18_0_5_node_107 | 0.4 | n |  | TRUE
34 | bus_LV_2771-18_0_5_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_2771-18_0_5_node_99 | 0.4 | n |  | TRUE
36 | bus_LV_2771-18_0_5_node_100 | 0.4 | n |  | TRUE
37 | bus_LV_2771-18_0_5_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_2771-18_0_5_node_18 | 0.4 | n |  | TRUE
39 | bus_LV_2771-18_0_5_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_2771-18_0_5_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_2771-18_0_5_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_2771-18_0_5_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_2771-18_0_5_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_2771-18_0_5_node_108 | 0.4 | n |  | TRUE
45 | bus_LV_2771-18_0_5_node_77 | 0.4 | n |  | TRUE
46 | bus_LV_2771-18_0_5_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_2771-18_0_5_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_2771-18_0_5_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_2771-18_0_5_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_2771-18_0_5_node_79 | 0.4 | n |  | TRUE
51 | bus_LV_2771-18_0_5_node_76 | 0.4 | n |  | TRUE
52 | bus_LV_2771-18_0_5_node_110 | 0.4 | n |  | TRUE
53 | bus_LV_2771-18_0_5_node_111 | 0.4 | n |  | TRUE
54 | bus_LV_2771-18_0_5_node_109 | 0.4 | n |  | TRUE
55 | bus_LV_2771-18_0_5_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_2771-18_0_5_node_24 | 0.4 | n |  | TRUE
57 | bus_LV_2771-18_0_5_node_25 | 0.4 | n |  | TRUE
58 | bus_LV_2771-18_0_5_node_112 | 0.4 | n |  | TRUE
59 | bus_LV_2771-18_0_5_node_84 | 0.4 | n |  | TRUE
60 | bus_LV_2771-18_0_5_node_113 | 0.4 | n |  | TRUE
61 | bus_LV_2771-18_0_5_node_31 | 0.4 | n |  | TRUE
62 | bus_LV_2771-18_0_5_node_32 | 0.4 | n |  | TRUE
63 | bus_LV_2771-18_0_5_node_33 | 0.4 | n |  | TRUE
64 | bus_LV_2771-18_0_5_node_89 | 0.4 | n |  | TRUE
65 | bus_LV_2771-18_0_5_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_2771-18_0_5_node_87 | 0.4 | n |  | TRUE
67 | bus_LV_2771-18_0_5_node_43 | 0.4 | n |  | TRUE
68 | bus_LV_2771-18_0_5_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_2771-18_0_5_node_92 | 0.4 | n |  | TRUE
70 | bus_LV_2771-18_0_5_node_93 | 0.4 | n |  | TRUE
71 | bus_LV_2771-18_0_5_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_2771-18_0_5_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_2771-18_0_5_node_41 | 0.4 | n |  | TRUE
74 | bus_LV_2771-18_0_5_node_48 | 0.4 | n |  | TRUE
75 | bus_LV_2771-18_0_5_node_50 | 0.4 | n |  | TRUE
76 | bus_LV_2771-18_0_5_node_52 | 0.4 | n |  | TRUE
77 | bus_LV_2771-18_0_5_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_2771-18_0_5_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_2771-18_0_5_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_2771-18_0_5_node_63 | 0.4 | n |  | TRUE
81 | bus_LV_2771-18_0_5_node_58 | 0.4 | n |  | TRUE
82 | bus_LV_2771-18_0_5_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_2771-18_0_5_node_56 | 0.4 | n |  | TRUE
84 | bus_LV_2771-18_0_5_node_54 | 0.4 | n |  | TRUE
85 | bus_LV_2771-18_0_5_node_55 | 0.4 | n |  | TRUE
86 | bus_LV_2771-18_0_5_node_65 | 0.4 | n |  | TRUE
87 | bus_LV_2771-18_0_5_node_67 | 0.4 | n |  | TRUE
88 | bus_LV_2771-18_0_5_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_2771-18_0_5_node_69 | 0.4 | n |  | TRUE
90 | bus_LV_2771-18_0_5_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_2771-18_0_5_node_103 | 0.4 | n |  | TRUE
92 | bus_LV_2771-18_0_5_node_104 | 0.4 | n |  | TRUE
93 | bus_LV_2771-18_0_5_node_105 | 0.4 | n |  | TRUE
94 | bus_LV_2771-18_0_5_node_71 | 0.4 | n |  | TRUE
95 | bus_LV_2771-18_0_5_node_72 | 0.4 | n |  | TRUE
96 | bus_LV_2771-18_0_5_node_73 | 0.4 | n |  | TRUE
97 | bus_LV_2771-18_0_5_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_2771-18_0_5_node_74 | 0.4 | n |  | TRUE
99 | bus_LV_2771-18_0_5_node_101 | 0.4 | n |  | TRUE
100 | bus_LV_2771-18_0_5_node_95 | 0.4 | n |  | TRUE
101 | bus_LV_2771-18_0_5_node_78 | 0.4 | n |  | TRUE
102 | bus_LV_2771-18_0_5_node_102 | 0.4 | n |  | TRUE
103 | bus_LV_2771-18_0_5_node_83 | 0.4 | n |  | TRUE
104 | bus_LV_2771-18_0_5_node_80 | 0.4 | n |  | TRUE
105 | bus_LV_2771-18_0_5_node_82 | 0.4 | n |  | TRUE
106 | bus_LV_2771-18_0_5_node_86 | 0.4 | n |  | TRUE
107 | bus_LV_2771-18_0_5_node_94 | 0.4 | n |  | TRUE
108 | bus_LV_2771-18_0_5_node_85 | 0.4 | n |  | TRUE
109 | bus_LV_2771-18_0_5_node_115 | 0.4 | n |  | TRUE
110 | bus_LV_2771-18_0_5_node_106 | 0.4 | n |  | TRUE
111 | bus_MV_569_0_node_153 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2771-18_0_5_load_0 | 0 | 0.0069836 | 0.0017503 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2771-18_0_5_load_2 | 2 | 0.0029445 | 0.00073795 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2771-18_0_5_load_4 | 4 | 0.0035076 | 0.0008791 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2771-18_0_5_load_45 | 6 | 0.0028279 | 0.00070875 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2771-18_0_5_load_5 | 7 | 0.0077427 | 0.0019405 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2771-18_0_5_load_26 | 10 | 0.0018629 | 0.0004669 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2771-18_0_5_load_98 | 12 | 0.0020657 | 0.00051772 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2771-18_0_5_load_96 | 15 | 0.0016686 | 0.00041819 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2771-18_0_5_load_14 | 17 | 0.006501 | 0.0016293 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2771-18_0_5_load_12 | 18 | 0.005031 | 0.0012609 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2771-18_0_5_load_6 | 19 | 0.0033764 | 0.00084621 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2771-18_0_5_load_35 | 20 | 0.0078928 | 0.0019781 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2771-18_0_5_load_7 | 21 | 0.0061131 | 0.0015321 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2771-18_0_5_load_8 | 22 | 0.0014161 | 0.0003549 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2771-18_0_5_load_9 | 23 | 0.0059815 | 0.0014991 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2771-18_0_5_load_11 | 24 | 0.0030487 | 0.00076408 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2771-18_0_5_load_36 | 27 | 0.0060171 | 0.001508 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2771-18_0_5_load_114 | 28 | 0.0054264 | 0.00136 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2771-18_0_5_load_61 | 29 | 0.0093247 | 0.002337 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2771-18_0_5_load_57 | 30 | 0.014094 | 0.0035323 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2771-18_0_5_load_90 | 32 | 0.0061356 | 0.0015377 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2771-18_0_5_load_107 | 33 | 0.006347 | 0.0015907 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2771-18_0_5_load_99 | 35 | 0.0071452 | 0.0017907 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2771-18_0_5_load_17 | 37 | 0.0036519 | 0.00091526 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2771-18_0_5_load_20 | 40 | 0.0047538 | 0.0011914 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2771-18_0_5_load_108 | 44 | 0.0041581 | 0.0010421 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2771-18_0_5_load_28 | 48 | 0.0028928 | 0.00072501 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2771-18_0_5_load_44 | 49 | 0.00082605 | 0.00020703 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2771-18_0_5_load_79 | 50 | 0.0024417 | 0.00061194 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2771-18_0_5_load_76 | 51 | 0.0039829 | 0.00099821 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2771-18_0_5_load_111 | 53 | 0.002657 | 0.00066591 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2771-18_0_5_load_109 | 54 | 0.0035696 | 0.00089463 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2771-18_0_5_load_42 | 55 | 0.010009 | 0.0025086 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2771-18_0_5_load_24 | 56 | 0.0048266 | 0.0012097 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2771-18_0_5_load_25 | 57 | 0.0043806 | 0.0010979 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2771-18_0_5_load_112 | 58 | 0.0072222 | 0.0018101 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2771-18_0_5_load_113 | 60 | 0.019707 | 0.0049391 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2771-18_0_5_load_31 | 61 | 0.0048897 | 0.0012255 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2771-18_0_5_load_32 | 62 | 0.0027696 | 0.00069413 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2771-18_0_5_load_33 | 63 | 0.0034351 | 0.00086092 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2771-18_0_5_load_89 | 64 | 0.008161 | 0.0020453 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2771-18_0_5_load_87 | 66 | 0.0041756 | 0.0010465 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2771-18_0_5_load_43 | 67 | 0.047211 | 0.011832 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2771-18_0_5_load_46 | 68 | 0.0023738 | 0.00059492 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2771-18_0_5_load_92 | 69 | 0.00094271 | 0.00023627 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2771-18_0_5_load_93 | 70 | 0.0016531 | 0.0004143 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2771-18_0_5_load_39 | 71 | 0.025578 | 0.0064105 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2771-18_0_5_load_41 | 73 | 0.0066063 | 0.0016557 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2771-18_0_5_load_48 | 74 | 0.010457 | 0.0026207 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2771-18_0_5_load_50 | 75 | 0.0014768 | 0.00037012 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2771-18_0_5_load_62 | 78 | 0.01411 | 0.0035363 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2771-18_0_5_load_58 | 81 | 0.018511 | 0.0046394 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2771-18_0_5_load_64 | 82 | 0.0045471 | 0.0011396 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2771-18_0_5_load_54 | 84 | 0.0012568 | 0.00031498 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2771-18_0_5_load_69 | 89 | 0.0042307 | 0.0010603 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2771-18_0_5_load_68 | 90 | 0.0045368 | 0.001137 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2771-18_0_5_load_103 | 91 | 0.00671 | 0.0016817 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2771-18_0_5_load_105 | 93 | 0.0029621 | 0.00074237 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2771-18_0_5_load_71 | 94 | 0.0047116 | 0.0011808 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2771-18_0_5_load_73 | 96 | 0.0045848 | 0.0011491 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2771-18_0_5_load_101 | 99 | 0.0023711 | 0.00059426 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2771-18_0_5_load_78 | 101 | 0.0042878 | 0.0010746 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2771-18_0_5_load_102 | 102 | 0.0024859 | 0.00062302 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2771-18_0_5_load_80 | 104 | 0.0017065 | 0.00042769 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2771-18_0_5_load_94 | 107 | 0.0008842 | 0.0002216 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2771-18_0_5_load_115 | 109 | 0.0043033 | 0.0010785 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2771-18_0_5_load_106 | 110 | 0.0044915 | 0.0011257 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2771-18_0_5_line_0 |  | 0 | 1 | 0.022005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2771-18_0_5_line_1 |  | 1 | 2 | 0.014054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2771-18_0_5_line_2 |  | 1 | 3 | 0.003493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2771-18_0_5_line_3 |  | 2 | 4 | 0.017018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2771-18_0_5_line_4 |  | 3 | 5 | 0.063083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2771-18_0_5_line_5 |  | 3 | 6 | 0.013572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2771-18_0_5_line_6 |  | 4 | 7 | 0.024511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2771-18_0_5_line_7 |  | 5 | 11 | 0.004628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2771-18_0_5_line_8 |  | 5 | 12 | 0.013112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2771-18_0_5_line_9 |  | 5 | 13 | 0.08343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_2771-18_0_5_line_10 |  | 7 | 19 | 0.010673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2771-18_0_5_line_11 |  | 8 | 9 | 0.049399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2771-18_0_5_line_12 |  | 8 | 10 | 0.017081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2771-18_0_5_line_13 |  | 9 | 25 | 0.057629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2771-18_0_5_line_14 |  | 9 | 26 | 0.061897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2771-18_0_5_line_15 |  | 9 | 22 | 0.032299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2771-18_0_5_line_16 |  | 10 | 56 | 0.017504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2771-18_0_5_line_17 |  | 11 | 35 | 0.00617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2771-18_0_5_line_18 |  | 11 | 36 | 0.027104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_2771-18_0_5_line_19 |  | 13 | 14 | 0.01948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2771-18_0_5_line_20 |  | 13 | 15 | 0.017249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2771-18_0_5_line_21 |  | 13 | 16 | 0.048027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2771-18_0_5_line_22 |  | 14 | 33 | 0.029408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2771-18_0_5_line_23 |  | 14 | 34 | 0.006792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2771-18_0_5_line_24 |  | 16 | 17 | 0.031882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2771-18_0_5_line_25 |  | 16 | 18 | 0.023699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2771-18_0_5_line_26 |  | 17 | 32 | 0.012182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2771-18_0_5_line_27 |  | 19 | 20 | 0.0083713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2771-18_0_5_line_28 |  | 21 | 22 | 0.0069783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2771-18_0_5_line_29 |  | 21 | 23 | 0.03938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2771-18_0_5_line_30 |  | 23 | 24 | 0.022058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2771-18_0_5_line_31 |  | 24 | 27 | 0.013692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2771-18_0_5_line_32 |  | 25 | 28 | 0.009848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2771-18_0_5_line_33 |  | 26 | 29 | 0.0031226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2771-18_0_5_line_34 |  | 26 | 30 | 0.039525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2771-18_0_5_line_35 |  | 27 | 31 | 0.020674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2771-18_0_5_line_36 |  | 29 | 83 | 0.046045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2771-18_0_5_line_37 |  | 30 | 81 | 0.044381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_2771-18_0_5_line_38 |  | 31 | 69 | 0.15156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2771-18_0_5_line_39 |  | 34 | 65 | 0.035086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_2771-18_0_5_line_40 |  | 34 | 62 | 0.031145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2771-18_0_5_line_41 |  | 36 | 110 | 0.009865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2771-18_0_5_line_42 |  | 36 | 92 | 0.006928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_2771-18_0_5_line_43 |  | 37 | 38 | 0.0037364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2771-18_0_5_line_44 |  | 37 | 39 | 0.027039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2771-18_0_5_line_45 |  | 38 | 40 | 0.008165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2771-18_0_5_line_46 |  | 38 | 41 | 0.013648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2771-18_0_5_line_47 |  | 39 | 42 | 0.019751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2771-18_0_5_line_48 |  | 39 | 43 | 0.00638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2771-18_0_5_line_49 |  | 41 | 44 | 0.028964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2771-18_0_5_line_50 |  | 41 | 45 | 0.006384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2771-18_0_5_line_51 |  | 42 | 46 | 0.016842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2771-18_0_5_line_52 |  | 42 | 47 | 0.011323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2771-18_0_5_line_53 |  | 42 | 48 | 0.019373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2771-18_0_5_line_54 |  | 43 | 49 | 0.0084053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2771-18_0_5_line_55 |  | 45 | 50 | 0.008482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2771-18_0_5_line_56 |  | 45 | 51 | 0.0067891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2771-18_0_5_line_57 |  | 46 | 52 | 0.013471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2771-18_0_5_line_58 |  | 46 | 53 | 0.031793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2771-18_0_5_line_59 |  | 47 | 54 | 0.009692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2771-18_0_5_line_60 |  | 49 | 55 | 0.047717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2771-18_0_5_line_61 |  | 51 | 97 | 0.018021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2771-18_0_5_line_62 |  | 52 | 58 | 0.007135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2771-18_0_5_line_63 |  | 52 | 59 | 0.035915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2771-18_0_5_line_64 |  | 55 | 72 | 0.022061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2771-18_0_5_line_65 |  | 56 | 57 | 0.0013857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2771-18_0_5_line_66 |  | 59 | 60 | 0.005502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2771-18_0_5_line_67 |  | 61 | 62 | 0.0079361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2771-18_0_5_line_68 |  | 61 | 63 | 0.026708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2771-18_0_5_line_69 |  | 63 | 64 | 0.033924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2771-18_0_5_line_70 |  | 64 | 66 | 0.019951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2771-18_0_5_line_71 |  | 65 | 67 | 0.023133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_2771-18_0_5_line_72 |  | 65 | 68 | 0.029533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2771-18_0_5_line_73 |  | 67 | 72 | 0.022761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2771-18_0_5_line_74 |  | 68 | 74 | 0.02579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2771-18_0_5_line_75 |  | 69 | 70 | 0.00018069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2771-18_0_5_line_76 |  | 71 | 72 | 0.050332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2771-18_0_5_line_77 |  | 71 | 73 | 0.015335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2771-18_0_5_line_78 |  | 75 | 76 | 0.03223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2771-18_0_5_line_79 |  | 76 | 77 | 0.010292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2771-18_0_5_line_80 |  | 77 | 78 | 0.030078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2771-18_0_5_line_81 |  | 78 | 83 | 0.0096076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2771-18_0_5_line_82 |  | 79 | 80 | 0.016194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_2771-18_0_5_line_83 |  | 79 | 81 | 0.040661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_2771-18_0_5_line_84 |  | 80 | 82 | 0.048436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_2771-18_0_5_line_85 |  | 82 | 86 | 0.022352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_2771-18_0_5_line_86 |  | 83 | 85 | 0.010314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2771-18_0_5_line_87 |  | 84 | 85 | 0.051882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2771-18_0_5_line_88 |  | 86 | 87 | 0.034763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_2771-18_0_5_line_89 |  | 87 | 88 | 0.016086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_2771-18_0_5_line_90 |  | 87 | 89 | 0.021701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2771-18_0_5_line_91 |  | 88 | 91 | 0.008407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2771-18_0_5_line_92 |  | 88 | 92 | 0.018203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
93 | LV_2771-18_0_5_line_93 |  | 89 | 90 | 0.02855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2771-18_0_5_line_94 |  | 92 | 93 | 0.009209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2771-18_0_5_line_95 |  | 94 | 95 | 0.012202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2771-18_0_5_line_96 |  | 94 | 96 | 0.013961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2771-18_0_5_line_97 |  | 95 | 97 | 0.050775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2771-18_0_5_line_98 |  | 97 | 101 | 0.005841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2771-18_0_5_line_99 |  | 97 | 98 | 0.032442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2771-18_0_5_line_100 |  | 98 | 99 | 0.007861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2771-18_0_5_line_101 |  | 98 | 100 | 0.031158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2771-18_0_5_line_102 |  | 100 | 102 | 0.009488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2771-18_0_5_line_103 |  | 100 | 103 | 0.0084047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2771-18_0_5_line_104 |  | 103 | 107 | 0.01573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2771-18_0_5_line_105 |  | 104 | 105 | 0.0072051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2771-18_0_5_line_106 |  | 105 | 106 | 0.0239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2771-18_0_5_line_107 |  | 106 | 109 | 0.011245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2771-18_0_5_line_108 |  | 106 | 108 | 0.010256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2771-18_0_5_line_109 |  | 107 | 108 | 0.021432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2771-18_0_5_trafo_49 | 0.63 MVA 20/0.4 kV | 111 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2609327.9454 | 1262108.6858 | 2609327.7179 | 1262130.6896
1 | 2609327.9454 | 1262108.6858 | 2609341.9992 | 1262108.7582
2 | 2609327.9454 | 1262108.6858 | 2609324.4424 | 1262108.6692
3 | 2609341.9992 | 1262108.7582 | 2609358.9602 | 1262108.8456 | 2609359.0024 | 1262108.8834
4 | 2609261.7427 | 1262113.0188 | 2609269.3828 | 1262112.219 | 2609289.6836 | 1262108.4814 | 2609324.4424 | 1262108.6692
5 | 2609324.4424 | 1262108.6692 | 2609324.5529 | 1262095.0974
6 | 2609365.221 | 1262130.3798 | 2609365.7232 | 1262114.8937 | 2609359.0024 | 1262108.8834
7 | 2609257.1389 | 1262113.612 | 2609261.7427 | 1262113.0188
8 | 2609264.5327 | 1262125.8318 | 2609261.7427 | 1262113.0188
9 | 2609261.7427 | 1262113.0188 | 2609269.3828 | 1262112.219 | 2609289.6836 | 1262108.4814 | 2609290.3942 | 1262150.3667 | 2609288.5356 | 1262163.4505
10 | 2609365.221 | 1262130.3798 | 2609365.1056 | 1262133.9391 | 2609372.2091 | 1262134.2874
11 | 2609260.9302 | 1262005.7999 | 2609268.2999 | 1262028.7381 | 2609276.5646 | 1262052.6562
12 | 2609276.5646 | 1262052.6562 | 2609293.6204 | 1262053.5772
13 | 2609260.9302 | 1262005.7999 | 2609268.2999 | 1262028.7381 | 2609284.4136 | 1262029.0301 | 2609301.8306 | 1262029.3463
14 | 2609215.2562 | 1261990.0627 | 2609226.9361 | 1261988.1573 | 2609253.5061 | 1261983.8734 | 2609260.9302 | 1262005.7999
15 | 2609260.9302 | 1262005.7999 | 2609283.1257 | 1261999.8303 | 2609280.6894 | 1261990.8396
16 | 2609293.6204 | 1262053.5772 | 2609311.0987 | 1262054.521
17 | 2609257.1389 | 1262113.612 | 2609255.9279 | 1262107.5616
18 | 2609230.3514 | 1262117.6955 | 2609238.4896 | 1262116.296 | 2609245.8065 | 1262115.0398 | 2609257.1389 | 1262113.612
19 | 2609288.5356 | 1262163.4505 | 2609285.8011 | 1262182.7372
20 | 2609272.0878 | 1262165.1149 | 2609276.9513 | 1262162.2427 | 2609288.5356 | 1262163.4505
21 | 2609288.5356 | 1262163.4505 | 2609290.3942 | 1262150.3667 | 2609325.206 | 1262150.1987
22 | 2609264.7887 | 1262203.3741 | 2609285.8011 | 1262182.7372
23 | 2609285.8011 | 1262182.7372 | 2609284.8489 | 1262189.4625
24 | 2609325.206 | 1262150.1987 | 2609357.0875 | 1262150.0396
25 | 2609325.206 | 1262150.1987 | 2609318.4584 | 1262172.8258 | 2609318.4603 | 1262172.9135
26 | 2609369.2689 | 1262149.9788 | 2609357.0875 | 1262150.0396
27 | 2609380.5704 | 1262134.6973 | 2609372.2091 | 1262134.2874
28 | 2609278.8641 | 1261984.1042 | 2609280.6894 | 1261990.8396
29 | 2609268.5642 | 1261946.095 | 2609278.8641 | 1261984.1042
30 | 2609268.5642 | 1261946.095 | 2609262.7947 | 1261924.8046
31 | 2609259.2134 | 1261911.5887 | 2609262.7947 | 1261924.8046
32 | 2609301.8306 | 1262029.3463 | 2609304.2035 | 1262019.788
33 | 2609215.2562 | 1261990.0627 | 2609212.1818 | 1261990.6097
34 | 2609215.2562 | 1261990.0627 | 2609219.2598 | 1262012.2507 | 2609222.2771 | 1262028.9592
35 | 2609250.7238 | 1261893.2628 | 2609255.8826 | 1261899.2971 | 2609259.2134 | 1261911.5887
36 | 2609166.9296 | 1261999.1166 | 2609199.16 | 1261992.951 | 2609209.6798 | 1261991.0548 | 2609212.1818 | 1261990.6097
37 | 2609222.2771 | 1262028.9592 | 2609222.6883 | 1262031.2357 | 2609224.5332 | 1262041.4677 | 2609211.7227 | 1262043.7606 | 2609197.1037 | 1262046.3842 | 2609193.3596 | 1262047.0549
38 | 2609250.7238 | 1261893.2628 | 2609354.6983 | 1261782.9891
39 | 2609279.9208 | 1262224.2008 | 2609280.85 | 1262217.631 | 2609284.8489 | 1262189.4625
40 | 2609284.8489 | 1262189.4625 | 2609315.967 | 1262190.7573
41 | 2609230.3514 | 1262117.6955 | 2609228.483 | 1262108.0082
42 | 2609230.3514 | 1262117.6955 | 2609223.5017 | 1262118.8634
43 | 2609256.281 | 1262340.7102 | 2609259.9571 | 1262340.0415
44 | 2609276.8785 | 1262349.1481 | 2609274.765 | 1262337.3478 | 2609259.9571 | 1262340.0415
45 | 2609257.9334 | 1262348.7072 | 2609256.281 | 1262340.7102
46 | 2609242.8156 | 1262343.1688 | 2609256.281 | 1262340.7102
47 | 2609276.8785 | 1262349.1481 | 2609281.195 | 1262368.4235
48 | 2609276.8785 | 1262349.1481 | 2609283.1405 | 1262347.8347
49 | 2609242.8156 | 1262343.1688 | 2609238.0613 | 1262314.5975
50 | 2609242.8156 | 1262343.1688 | 2609236.5161 | 1262344.3154
51 | 2609285.9382 | 1262384.5864 | 2609281.195 | 1262368.4235
52 | 2609281.195 | 1262368.4235 | 2609288.1205 | 1262366.7331 | 2609289.214 | 1262370.7821
53 | 2609281.195 | 1262368.4235 | 2609269.2656 | 1262371.3403 | 2609267.852 | 1262364.3907
54 | 2609283.1405 | 1262347.8347 | 2609282.0106 | 1262339.5056
55 | 2609236.5161 | 1262344.3154 | 2609234.9772 | 1262335.9739
56 | 2609236.5161 | 1262344.3154 | 2609229.8373 | 1262345.5342
57 | 2609285.9382 | 1262384.5864 | 2609292.5394 | 1262383.1513 | 2609294.2845 | 1262389.6362
58 | 2609254.7861 | 1262391.3759 | 2609285.9382 | 1262384.5864
59 | 2609289.214 | 1262370.7821 | 2609298.9321 | 1262370.5415
60 | 2609277.9367 | 1262291.9999 | 2609279.5061 | 1262321.0441 | 2609282.0106 | 1262339.5056
61 | 2609212.1095 | 1262348.7695 | 2609229.8373 | 1262345.5342
62 | 2609294.2845 | 1262389.6362 | 2609301.3895 | 1262388.78
63 | 2609294.2845 | 1262389.6362 | 2609303.6315 | 1262424.3189
64 | 2609277.371 | 1262269.9614 | 2609277.1777 | 1262277.9554 | 2609277.9367 | 1262291.9999
65 | 2609312.4823 | 1262054.5957 | 2609311.0987 | 1262054.521
66 | 2609303.6315 | 1262424.3189 | 2609308.9521 | 1262422.8596
67 | 2609323.7391 | 1262192.2029 | 2609318.1665 | 1262190.8488 | 2609315.967 | 1262190.7573
68 | 2609338.9194 | 1262210.9283 | 2609333.6776 | 1262210.0751 | 2609331.4894 | 1262207.5477 | 2609329.1406 | 1262196.9257 | 2609323.7391 | 1262192.2029
69 | 2609338.9194 | 1262210.9283 | 2609371.3419 | 1262220.9083
70 | 2609371.3419 | 1262220.9083 | 2609375.05 | 1262201.3049
71 | 2609279.9208 | 1262224.2008 | 2609278.1842 | 1262236.3953 | 2609277.9222 | 1262247.2075
72 | 2609279.9208 | 1262224.2008 | 2609309.1663 | 1262228.3123
73 | 2609277.371 | 1262269.9614 | 2609277.9222 | 1262247.2075
74 | 2609334.7055 | 1262231.9027 | 2609309.1663 | 1262228.3123
75 | 2609354.6983 | 1261782.9891 | 2609354.8722 | 1261782.9402
76 | 2609277.371 | 1262269.9614 | 2609298.2737 | 1262271.1726 | 2609305.2007 | 1262268.6483 | 2609308.7577 | 1262262.9278 | 2609310.0174 | 1262247.6942
77 | 2609314.3739 | 1262236.3295 | 2609310.9998 | 1262235.8127 | 2609310.0174 | 1262247.6942
78 | 2609131.81 | 1262002.843 | 2609128.6114 | 1261986.1044 | 2609125.7638 | 1261971.1855
79 | 2609131.81 | 1262002.843 | 2609133.7382 | 1262012.9528
80 | 2609133.7382 | 1262012.9528 | 2609163.3082 | 1262007.45
81 | 2609166.9296 | 1261999.1166 | 2609167.3478 | 1262001.4744 | 2609163.3082 | 1262007.45
82 | 2609142.8932 | 1262060.8662 | 2609142.0113 | 1262056.2617 | 2609153.3372 | 1262054.2333
83 | 2609153.3372 | 1262054.2333 | 2609158.1449 | 1262053.3734 | 2609172.9221 | 1262050.7166 | 2609189.3496 | 1262047.7732 | 2609193.3596 | 1262047.0549
84 | 2609142.8932 | 1262060.8662 | 2609151.4798 | 1262108.5354
85 | 2609155.4422 | 1262130.5331 | 2609151.4798 | 1262108.5354
86 | 2609164.9412 | 1261988.9955 | 2609166.9296 | 1261999.1166
87 | 2609164.9412 | 1261988.9955 | 2609176.1062 | 1261969.2881 | 2609184.1172 | 1261957.7148 | 2609197.7256 | 1261951.0424
88 | 2609155.4422 | 1262130.5331 | 2609188.5828 | 1262124.8469 | 2609189.7055 | 1262124.6596
89 | 2609189.7055 | 1262124.6596 | 2609195.7791 | 1262123.6127 | 2609205.56 | 1262121.9378
90 | 2609189.7055 | 1262124.6596 | 2609193.7473 | 1262145.9812
91 | 2609205.56 | 1262121.9378 | 2609203.9531 | 1262113.6852
92 | 2609205.56 | 1262121.9378 | 2609213.0501 | 1262120.6596 | 2609222.0248 | 1262119.1169 | 2609223.5017 | 1262118.8634
93 | 2609181.1211 | 1262161.9749 | 2609196.1991 | 1262158.9152 | 2609193.7473 | 1262145.9812
94 | 2609224.6176 | 1262128.0047 | 2609223.5017 | 1262118.8634
95 | 2609190.5538 | 1262316.9367 | 2609202.5621 | 1262314.7721
96 | 2609216.3017 | 1262312.2955 | 2609202.5621 | 1262314.7721
97 | 2609190.5538 | 1262316.9367 | 2609195.67 | 1262345.4196 | 2609196.7754 | 1262351.5699 | 2609212.1095 | 1262348.7695
98 | 2609212.1095 | 1262348.7695 | 2609211.3727 | 1262342.9755
99 | 2609199.9664 | 1262368.1195 | 2609197.1042 | 1262353.2605 | 2609196.7754 | 1262351.5699 | 2609212.1095 | 1262348.7695
100 | 2609199.9664 | 1262368.1195 | 2609207.7351 | 1262366.775
101 | 2609199.9664 | 1262368.1195 | 2609205.063 | 1262394.601 | 2609205.8552 | 1262398.7162
102 | 2609205.8552 | 1262398.7162 | 2609215.0418 | 1262396.2398
103 | 2609205.8552 | 1262398.7162 | 2609206.6697 | 1262402.9537 | 2609207.4469 | 1262406.9687
104 | 2609207.4469 | 1262406.9687 | 2609213.2807 | 1262404.8763 | 2609222.3296 | 1262401.8784
105 | 2609270.2991 | 1262404.2421 | 2609271.6568 | 1262411.3181
106 | 2609247.1714 | 1262409.999 | 2609254.7317 | 1262406.9865 | 2609261.868 | 1262405.3186 | 2609270.2991 | 1262404.2421
107 | 2609247.1714 | 1262409.999 | 2609249.0449 | 1262421.0873
108 | 2609243.6157 | 1262400.3758 | 2609247.1714 | 1262409.999
109 | 2609243.6157 | 1262400.3758 | 2609234.4933 | 1262400.2616 | 2609224.1037 | 1262401.2906 | 2609222.3296 | 1262401.8784

## bus_geodata
| x | y | coords
0 | 2609327.7179 | 1262130.6896
1 | 2609327.9454 | 1262108.6858
2 | 2609341.9992 | 1262108.7582
3 | 2609324.4424 | 1262108.6692
4 | 2609359.0024 | 1262108.8834
5 | 2609261.7427 | 1262113.0188
6 | 2609324.5529 | 1262095.0974
7 | 2609365.221 | 1262130.3798
8 | 2609276.5646 | 1262052.6562
9 | 2609260.9302 | 1262005.7999
10 | 2609293.6204 | 1262053.5772
11 | 2609257.1389 | 1262113.612
12 | 2609264.5327 | 1262125.8318
13 | 2609288.5356 | 1262163.4505
14 | 2609285.8011 | 1262182.7372
15 | 2609272.0878 | 1262165.1149
16 | 2609325.206 | 1262150.1987
17 | 2609357.0875 | 1262150.0396
18 | 2609318.4603 | 1262172.9135
19 | 2609372.2091 | 1262134.2874
20 | 2609380.5704 | 1262134.6973
21 | 2609278.8641 | 1261984.1042
22 | 2609280.6894 | 1261990.8396
23 | 2609268.5642 | 1261946.095
24 | 2609262.7947 | 1261924.8046
25 | 2609301.8306 | 1262029.3463
26 | 2609215.2562 | 1261990.0627
27 | 2609259.2134 | 1261911.5887
28 | 2609304.2035 | 1262019.788
29 | 2609212.1818 | 1261990.6097
30 | 2609222.2771 | 1262028.9592
31 | 2609250.7238 | 1261893.2628
32 | 2609369.2689 | 1262149.9788
33 | 2609264.7887 | 1262203.3741
34 | 2609284.8489 | 1262189.4625
35 | 2609255.9279 | 1262107.5616
36 | 2609230.3514 | 1262117.6955
37 | 2609259.9571 | 1262340.0415
38 | 2609256.281 | 1262340.7102
39 | 2609276.8785 | 1262349.1481
40 | 2609257.9334 | 1262348.7072
41 | 2609242.8156 | 1262343.1688
42 | 2609281.195 | 1262368.4235
43 | 2609283.1405 | 1262347.8347
44 | 2609238.0613 | 1262314.5975
45 | 2609236.5161 | 1262344.3154
46 | 2609285.9382 | 1262384.5864
47 | 2609289.214 | 1262370.7821
48 | 2609267.852 | 1262364.3907
49 | 2609282.0106 | 1262339.5056
50 | 2609234.9772 | 1262335.9739
51 | 2609229.8373 | 1262345.5342
52 | 2609294.2845 | 1262389.6362
53 | 2609254.7861 | 1262391.3759
54 | 2609298.9321 | 1262370.5415
55 | 2609277.9367 | 1262291.9999
56 | 2609311.0987 | 1262054.521
57 | 2609312.4823 | 1262054.5957
58 | 2609301.3895 | 1262388.78
59 | 2609303.6315 | 1262424.3189
60 | 2609308.9521 | 1262422.8596
61 | 2609323.7391 | 1262192.2029
62 | 2609315.967 | 1262190.7573
63 | 2609338.9194 | 1262210.9283
64 | 2609371.3419 | 1262220.9083
65 | 2609279.9208 | 1262224.2008
66 | 2609375.05 | 1262201.3049
67 | 2609277.9222 | 1262247.2075
68 | 2609309.1663 | 1262228.3123
69 | 2609354.6983 | 1261782.9891
70 | 2609354.8722 | 1261782.9402
71 | 2609310.0174 | 1262247.6942
72 | 2609277.371 | 1262269.9614
73 | 2609314.3739 | 1262236.3295
74 | 2609334.7055 | 1262231.9027
75 | 2609125.7638 | 1261971.1855
76 | 2609131.81 | 1262002.843
77 | 2609133.7382 | 1262012.9528
78 | 2609163.3082 | 1262007.45
79 | 2609153.3372 | 1262054.2333
80 | 2609142.8932 | 1262060.8662
81 | 2609193.3596 | 1262047.0549
82 | 2609151.4798 | 1262108.5354
83 | 2609166.9296 | 1261999.1166
84 | 2609197.7256 | 1261951.0424
85 | 2609164.9412 | 1261988.9955
86 | 2609155.4422 | 1262130.5331
87 | 2609189.7055 | 1262124.6596
88 | 2609205.56 | 1262121.9378
89 | 2609193.7473 | 1262145.9812
90 | 2609181.1211 | 1262161.9749
91 | 2609203.9531 | 1262113.6852
92 | 2609223.5017 | 1262118.8634
93 | 2609224.6176 | 1262128.0047
94 | 2609202.5621 | 1262314.7721
95 | 2609190.5538 | 1262316.9367
96 | 2609216.3017 | 1262312.2955
97 | 2609212.1095 | 1262348.7695
98 | 2609199.9664 | 1262368.1195
99 | 2609207.7351 | 1262366.775
100 | 2609205.8552 | 1262398.7162
101 | 2609211.3727 | 1262342.9755
102 | 2609215.0418 | 1262396.2398
103 | 2609207.4469 | 1262406.9687
104 | 2609271.6568 | 1262411.3181
105 | 2609270.2991 | 1262404.2421
106 | 2609247.1714 | 1262409.999
107 | 2609222.3296 | 1262401.8784
108 | 2609243.6157 | 1262400.3758
109 | 2609249.0449 | 1262421.0873
110 | 2609228.483 | 1262108.0082
111 | 2609284.8489 | 1262189.4625

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1