## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2773-15_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2773-15_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2773-15_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2773-15_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2773-15_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2773-15_0_4_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_2773-15_0_4_node_54 | 0.4 | n |  | TRUE
7 | bus_LV_2773-15_0_4_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_2773-15_0_4_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_2773-15_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2773-15_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2773-15_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2773-15_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2773-15_0_4_node_66 | 0.4 | n |  | TRUE
14 | bus_LV_2773-15_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_2773-15_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2773-15_0_4_node_61 | 0.4 | n |  | TRUE
17 | bus_LV_2773-15_0_4_node_90 | 0.4 | n |  | TRUE
18 | bus_LV_2773-15_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2773-15_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2773-15_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_2773-15_0_4_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_2773-15_0_4_node_101 | 0.4 | n |  | TRUE
23 | bus_LV_2773-15_0_4_node_99 | 0.4 | n |  | TRUE
24 | bus_LV_2773-15_0_4_node_55 | 0.4 | n |  | TRUE
25 | bus_LV_2773-15_0_4_node_56 | 0.4 | n |  | TRUE
26 | bus_LV_2773-15_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2773-15_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2773-15_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_2773-15_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2773-15_0_4_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_2773-15_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_2773-15_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_2773-15_0_4_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_2773-15_0_4_node_105 | 0.4 | n |  | TRUE
35 | bus_LV_2773-15_0_4_node_107 | 0.4 | n |  | TRUE
36 | bus_LV_2773-15_0_4_node_103 | 0.4 | n |  | TRUE
37 | bus_LV_2773-15_0_4_node_80 | 0.4 | n |  | TRUE
38 | bus_LV_2773-15_0_4_node_62 | 0.4 | n |  | TRUE
39 | bus_LV_2773-15_0_4_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_2773-15_0_4_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_2773-15_0_4_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_2773-15_0_4_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_2773-15_0_4_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_2773-15_0_4_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_2773-15_0_4_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_2773-15_0_4_node_52 | 0.4 | n |  | TRUE
47 | bus_LV_2773-15_0_4_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_2773-15_0_4_node_53 | 0.4 | n |  | TRUE
49 | bus_LV_2773-15_0_4_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_2773-15_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_2773-15_0_4_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_2773-15_0_4_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_2773-15_0_4_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_2773-15_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_2773-15_0_4_node_63 | 0.4 | n |  | TRUE
56 | bus_LV_2773-15_0_4_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_2773-15_0_4_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_2773-15_0_4_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_2773-15_0_4_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_2773-15_0_4_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_2773-15_0_4_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_2773-15_0_4_node_46 | 0.4 | n |  | TRUE
63 | bus_LV_2773-15_0_4_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_2773-15_0_4_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_2773-15_0_4_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_2773-15_0_4_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_2773-15_0_4_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_2773-15_0_4_node_72 | 0.4 | n |  | TRUE
69 | bus_LV_2773-15_0_4_node_73 | 0.4 | n |  | TRUE
70 | bus_LV_2773-15_0_4_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_2773-15_0_4_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_2773-15_0_4_node_76 | 0.4 | n |  | TRUE
73 | bus_LV_2773-15_0_4_node_77 | 0.4 | n |  | TRUE
74 | bus_LV_2773-15_0_4_node_75 | 0.4 | n |  | TRUE
75 | bus_LV_2773-15_0_4_node_92 | 0.4 | n |  | TRUE
76 | bus_LV_2773-15_0_4_node_88 | 0.4 | n |  | TRUE
77 | bus_LV_2773-15_0_4_node_67 | 0.4 | n |  | TRUE
78 | bus_LV_2773-15_0_4_node_68 | 0.4 | n |  | TRUE
79 | bus_LV_2773-15_0_4_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_2773-15_0_4_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_2773-15_0_4_node_71 | 0.4 | n |  | TRUE
82 | bus_LV_2773-15_0_4_node_79 | 0.4 | n |  | TRUE
83 | bus_LV_2773-15_0_4_node_87 | 0.4 | n |  | TRUE
84 | bus_LV_2773-15_0_4_node_78 | 0.4 | n |  | TRUE
85 | bus_LV_2773-15_0_4_node_85 | 0.4 | n |  | TRUE
86 | bus_LV_2773-15_0_4_node_74 | 0.4 | n |  | TRUE
87 | bus_LV_2773-15_0_4_node_81 | 0.4 | n |  | TRUE
88 | bus_LV_2773-15_0_4_node_82 | 0.4 | n |  | TRUE
89 | bus_LV_2773-15_0_4_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_2773-15_0_4_node_84 | 0.4 | n |  | TRUE
91 | bus_LV_2773-15_0_4_node_86 | 0.4 | n |  | TRUE
92 | bus_LV_2773-15_0_4_node_97 | 0.4 | n |  | TRUE
93 | bus_LV_2773-15_0_4_node_110 | 0.4 | n |  | TRUE
94 | bus_LV_2773-15_0_4_node_89 | 0.4 | n |  | TRUE
95 | bus_LV_2773-15_0_4_node_91 | 0.4 | n |  | TRUE
96 | bus_LV_2773-15_0_4_node_96 | 0.4 | n |  | TRUE
97 | bus_LV_2773-15_0_4_node_95 | 0.4 | n |  | TRUE
98 | bus_LV_2773-15_0_4_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_2773-15_0_4_node_94 | 0.4 | n |  | TRUE
100 | bus_LV_2773-15_0_4_node_98 | 0.4 | n |  | TRUE
101 | bus_LV_2773-15_0_4_node_102 | 0.4 | n |  | TRUE
102 | bus_LV_2773-15_0_4_node_109 | 0.4 | n |  | TRUE
103 | bus_LV_2773-15_0_4_node_108 | 0.4 | n |  | TRUE
104 | bus_LV_2773-15_0_4_node_104 | 0.4 | n |  | TRUE
105 | bus_LV_2773-15_0_4_node_106 | 0.4 | n |  | TRUE
106 | bus_MV_573_0_node_15 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2773-15_0_4_load_0 | 0 | 0.0096507 | 0.0024187 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2773-15_0_4_load_1 | 1 | 0.0073982 | 0.0018542 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2773-15_0_4_load_4 | 3 | 0.012222 | 0.0030632 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2773-15_0_4_load_15 | 5 | 0.0060213 | 0.0015091 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2773-15_0_4_load_54 | 6 | 0.0089707 | 0.0022483 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2773-15_0_4_load_33 | 8 | 0.020155 | 0.0050514 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2773-15_0_4_load_6 | 9 | 0.0061377 | 0.0015383 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2773-15_0_4_load_7 | 10 | 0.002814 | 0.00070526 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2773-15_0_4_load_8 | 11 | 0.0015415 | 0.00038634 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2773-15_0_4_load_66 | 13 | 0.002257 | 0.00056567 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2773-15_0_4_load_61 | 16 | 0.0023499 | 0.00058895 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2773-15_0_4_load_14 | 18 | 0.0021988 | 0.00055107 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2773-15_0_4_load_11 | 19 | 0.0093901 | 0.0023534 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2773-15_0_4_load_17 | 20 | 0.0053206 | 0.0013335 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2773-15_0_4_load_59 | 21 | 0.002245 | 0.00056266 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2773-15_0_4_load_101 | 22 | 0.0020825 | 0.00052194 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2773-15_0_4_load_99 | 23 | 0.0022557 | 0.00056534 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2773-15_0_4_load_55 | 24 | 0.001795 | 0.00044986 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2773-15_0_4_load_56 | 25 | 0.001796 | 0.00045012 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2773-15_0_4_load_18 | 26 | 0.0043363 | 0.0010868 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2773-15_0_4_load_19 | 27 | 0.0029871 | 0.00074865 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2773-15_0_4_load_39 | 30 | 0.0016549 | 0.00041477 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2773-15_0_4_load_22 | 31 | 0.0041041 | 0.0010286 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2773-15_0_4_load_105 | 34 | 0.0020113 | 0.00050408 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2773-15_0_4_load_107 | 35 | 0.0018481 | 0.00046318 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2773-15_0_4_load_103 | 36 | 0.0018855 | 0.00047255 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2773-15_0_4_load_80 | 37 | 0.0020021 | 0.00050176 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2773-15_0_4_load_62 | 38 | 0.0020505 | 0.00051389 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2773-15_0_4_load_37 | 39 | 0.0081385 | 0.0020397 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2773-15_0_4_load_35 | 40 | 0.013138 | 0.0032927 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2773-15_0_4_load_26 | 41 | 0.0069816 | 0.0017497 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2773-15_0_4_load_30 | 43 | 0.014944 | 0.0037452 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2773-15_0_4_load_29 | 44 | 0.0081181 | 0.0020346 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2773-15_0_4_load_31 | 45 | 0.016105 | 0.0040362 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2773-15_0_4_load_32 | 47 | 0.014948 | 0.0037464 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2773-15_0_4_load_53 | 48 | 0.010608 | 0.0026587 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2773-15_0_4_load_34 | 49 | 0.013138 | 0.0032926 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2773-15_0_4_load_36 | 50 | 0.0027392 | 0.00068651 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2773-15_0_4_load_40 | 52 | 0.0027392 | 0.00068651 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2773-15_0_4_load_41 | 53 | 0.014944 | 0.0037452 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2773-15_0_4_load_42 | 54 | 0.0027392 | 0.00068651 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2773-15_0_4_load_63 | 55 | 0.0032909 | 0.00082477 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2773-15_0_4_load_43 | 56 | 0.0027392 | 0.00068651 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2773-15_0_4_load_44 | 57 | 0.0084195 | 0.0021101 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2773-15_0_4_load_51 | 59 | 0.012223 | 0.0030633 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2773-15_0_4_load_49 | 60 | 0.003302 | 0.00082756 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2773-15_0_4_load_47 | 61 | 0.0062534 | 0.0015672 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2773-15_0_4_load_46 | 62 | 0.01005 | 0.0025187 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2773-15_0_4_load_48 | 63 | 0.0053021 | 0.0013288 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2773-15_0_4_load_50 | 64 | 0.0044976 | 0.0011272 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2773-15_0_4_load_57 | 65 | 0.0013341 | 0.00033435 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2773-15_0_4_load_58 | 66 | 0.0027432 | 0.00068751 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2773-15_0_4_load_60 | 67 | 0.0029675 | 0.00074372 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2773-15_0_4_load_72 | 68 | 0.00088852 | 0.00022268 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2773-15_0_4_load_73 | 69 | 0.0017025 | 0.00042668 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2773-15_0_4_load_64 | 70 | 0.002672 | 0.00066968 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2773-15_0_4_load_65 | 71 | 0.0020905 | 0.00052394 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2773-15_0_4_load_77 | 73 | 0.0013462 | 0.0003374 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2773-15_0_4_load_75 | 74 | 0.0044177 | 0.0011072 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2773-15_0_4_load_92 | 75 | 0.0016305 | 0.00040864 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2773-15_0_4_load_88 | 76 | 0.0020941 | 0.00052482 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2773-15_0_4_load_67 | 77 | 0.0015556 | 0.00038987 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2773-15_0_4_load_68 | 78 | 0.001445 | 0.00036214 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2773-15_0_4_load_69 | 79 | 0.0015686 | 0.00039312 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2773-15_0_4_load_70 | 80 | 0.0020252 | 0.00050756 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2773-15_0_4_load_71 | 81 | 0.0012759 | 0.00031977 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2773-15_0_4_load_87 | 83 | 0.00086143 | 0.00021589 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2773-15_0_4_load_78 | 84 | 0.0011431 | 0.00028649 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2773-15_0_4_load_85 | 85 | 0.0014683 | 0.000368 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2773-15_0_4_load_74 | 86 | 0.0038126 | 0.00095552 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2773-15_0_4_load_81 | 87 | 0.0020683 | 0.00051836 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2773-15_0_4_load_82 | 88 | 0.0019753 | 0.00049506 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2773-15_0_4_load_84 | 90 | 0.0020518 | 0.00051422 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2773-15_0_4_load_86 | 91 | 0.0017336 | 0.00043448 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2773-15_0_4_load_97 | 92 | 0.0019574 | 0.00049057 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2773-15_0_4_load_110 | 93 | 0.0015341 | 0.00038448 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2773-15_0_4_load_89 | 94 | 0.0021383 | 0.0005359 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2773-15_0_4_load_91 | 95 | 0.002253 | 0.00056465 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2773-15_0_4_load_96 | 96 | 0.0021623 | 0.00054193 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2773-15_0_4_load_95 | 97 | 0.0021128 | 0.00052951 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2773-15_0_4_load_93 | 98 | 0.0021291 | 0.00053361 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2773-15_0_4_load_94 | 99 | 0.0021844 | 0.00054746 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2773-15_0_4_load_98 | 100 | 0.0022189 | 0.0005561 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2773-15_0_4_load_102 | 101 | 0.002025 | 0.00050751 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2773-15_0_4_load_108 | 103 | 0.0019004 | 0.00047629 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2773-15_0_4_load_104 | 104 | 0.0022523 | 0.00056448 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2773-15_0_4_load_106 | 105 | 0.0022968 | 0.00057563 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2773-15_0_4_line_0 |  | 0 | 1 | 0.027203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2773-15_0_4_line_1 |  | 0 | 2 | 0.041047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2773-15_0_4_line_2 |  | 2 | 3 | 0.020895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2773-15_0_4_line_3 |  | 2 | 4 | 0.010825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2773-15_0_4_line_4 |  | 3 | 5 | 0.0212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2773-15_0_4_line_5 |  | 4 | 6 | 0.045153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2773-15_0_4_line_6 |  | 5 | 7 | 0.025474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2773-15_0_4_line_7 |  | 6 | 8 | 0.014359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2773-15_0_4_line_8 |  | 7 | 20 | 0.016753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2773-15_0_4_line_9 |  | 7 | 15 | 0.012468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_2773-15_0_4_line_10 |  | 8 | 47 | 0.021655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2773-15_0_4_line_11 |  | 9 | 10 | 0.0055208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2773-15_0_4_line_12 |  | 9 | 11 | 0.006157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2773-15_0_4_line_13 |  | 10 | 12 | 0.014454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2773-15_0_4_line_14 |  | 12 | 13 | 0.014426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2773-15_0_4_line_15 |  | 12 | 14 | 0.027195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2773-15_0_4_line_16 |  | 13 | 17 | 0.015559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2773-15_0_4_line_17 |  | 14 | 18 | 0.018383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2773-15_0_4_line_18 |  | 14 | 19 | 0.018942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2773-15_0_4_line_19 |  | 15 | 16 | 0.018079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2773-15_0_4_line_20 |  | 16 | 21 | 0.00038699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2773-15_0_4_line_21 |  | 17 | 75 | 0.0067429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2773-15_0_4_line_22 |  | 17 | 76 | 0.014834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2773-15_0_4_line_23 |  | 18 | 22 | 0.003111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2773-15_0_4_line_24 |  | 20 | 24 | 0.004629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2773-15_0_4_line_25 |  | 21 | 65 | 0.022487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2773-15_0_4_line_26 |  | 22 | 23 | 0.0074615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2773-15_0_4_line_27 |  | 23 | 100 | 0.0075543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2773-15_0_4_line_28 |  | 24 | 25 | 0.0094634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_2773-15_0_4_line_29 |  | 25 | 59 | 0.015067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_2773-15_0_4_line_30 |  | 26 | 27 | 0.093035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2773-15_0_4_line_31 |  | 27 | 28 | 0.10032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2773-15_0_4_line_32 |  | 28 | 29 | 0.041797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2773-15_0_4_line_33 |  | 29 | 30 | 0.033935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2773-15_0_4_line_34 |  | 30 | 38 | 0.0065656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2773-15_0_4_line_35 |  | 31 | 32 | 0.10119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2773-15_0_4_line_36 |  | 32 | 33 | 0.073845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2773-15_0_4_line_37 |  | 33 | 34 | 0.019832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2773-15_0_4_line_38 |  | 33 | 35 | 0.024923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2773-15_0_4_line_39 |  | 34 | 36 | 0.00097843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2773-15_0_4_line_40 |  | 35 | 37 | 0.0075583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2773-15_0_4_line_41 |  | 36 | 104 | 0.0049791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2773-15_0_4_line_42 |  | 37 | 82 | 0.020634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2773-15_0_4_line_43 |  | 38 | 55 | 0.019394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2773-15_0_4_line_44 |  | 39 | 40 | 0.0331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2773-15_0_4_line_45 |  | 40 | 49 | 0.032887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2773-15_0_4_line_46 |  | 41 | 42 | 0.031926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2773-15_0_4_line_47 |  | 42 | 43 | 0.029457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2773-15_0_4_line_48 |  | 43 | 46 | 0.051244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2773-15_0_4_line_49 |  | 44 | 45 | 0.011584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2773-15_0_4_line_50 |  | 45 | 47 | 0.01748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2773-15_0_4_line_51 |  | 46 | 48 | 0.019341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2773-15_0_4_line_52 |  | 48 | 53 | 0.032174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2773-15_0_4_line_53 |  | 49 | 50 | 0.032908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2773-15_0_4_line_54 |  | 50 | 51 | 0.016176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2773-15_0_4_line_55 |  | 51 | 52 | 0.017289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2773-15_0_4_line_56 |  | 51 | 53 | 0.0033466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2773-15_0_4_line_57 |  | 52 | 54 | 0.0064418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2773-15_0_4_line_58 |  | 54 | 56 | 0.0064418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2773-15_0_4_line_59 |  | 55 | 70 | 0.018844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2773-15_0_4_line_60 |  | 56 | 57 | 0.0022307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2773-15_0_4_line_61 |  | 57 | 58 | 0.026554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2773-15_0_4_line_62 |  | 58 | 59 | 0.0055255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2773-15_0_4_line_63 |  | 58 | 60 | 0.023809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2773-15_0_4_line_64 |  | 60 | 61 | 0.021122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2773-15_0_4_line_65 |  | 61 | 62 | 0.01369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2773-15_0_4_line_66 |  | 62 | 63 | 0.019265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2773-15_0_4_line_67 |  | 63 | 64 | 0.0027971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2773-15_0_4_line_68 |  | 65 | 66 | 0.018729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2773-15_0_4_line_69 |  | 66 | 67 | 0.011393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2773-15_0_4_line_70 |  | 67 | 68 | 0.00074066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2773-15_0_4_line_71 |  | 68 | 69 | 0.01206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2773-15_0_4_line_72 |  | 69 | 86 | 0.01662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2773-15_0_4_line_73 |  | 70 | 71 | 0.020931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2773-15_0_4_line_74 |  | 71 | 72 | 0.035219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2773-15_0_4_line_75 |  | 72 | 73 | 0.030697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2773-15_0_4_line_76 |  | 72 | 74 | 0.016528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2773-15_0_4_line_77 |  | 73 | 84 | 0.0018924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2773-15_0_4_line_78 |  | 74 | 86 | 0.0071341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2773-15_0_4_line_79 |  | 75 | 93 | 0.0077359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2773-15_0_4_line_80 |  | 76 | 94 | 0.0018327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2773-15_0_4_line_81 |  | 77 | 78 | 0.0057293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2773-15_0_4_line_82 |  | 77 | 79 | 0.015081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2773-15_0_4_line_83 |  | 78 | 80 | 0.0068657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2773-15_0_4_line_84 |  | 79 | 81 | 0.007589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2773-15_0_4_line_85 |  | 80 | 82 | 0.017508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2773-15_0_4_line_86 |  | 81 | 83 | 0.0067901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2773-15_0_4_line_87 |  | 82 | 84 | 0.028771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2773-15_0_4_line_88 |  | 83 | 85 | 0.0061691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2773-15_0_4_line_89 |  | 85 | 89 | 0.0034215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2773-15_0_4_line_90 |  | 87 | 88 | 0.0080848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2773-15_0_4_line_91 |  | 87 | 89 | 0.016552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2773-15_0_4_line_92 |  | 88 | 90 | 0.0075695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2773-15_0_4_line_93 |  | 89 | 91 | 0.0051111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2773-15_0_4_line_94 |  | 90 | 92 | 0.0074994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2773-15_0_4_line_95 |  | 91 | 93 | 0.013075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2773-15_0_4_line_96 |  | 94 | 95 | 0.0077753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2773-15_0_4_line_97 |  | 95 | 96 | 0.007693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2773-15_0_4_line_98 |  | 96 | 97 | 0.0074051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2773-15_0_4_line_99 |  | 97 | 99 | 0.0075865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2773-15_0_4_line_100 |  | 98 | 99 | 0.0078334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2773-15_0_4_line_101 |  | 101 | 102 | 0.00017566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2773-15_0_4_line_102 |  | 102 | 103 | 0.0072744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2773-15_0_4_line_103 |  | 103 | 105 | 0.0079752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2773-15_0_4_line_104 |  | 104 | 105 | 0.017788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2773-15_0_4_trafo_55 | 0.63 MVA 20/0.4 kV | 106 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2612066.5443 | 1260994.2606 | 2612071.5191 | 1261021.0049
1 | 2612059.038 | 1260953.9062 | 2612066.5443 | 1260994.2606
2 | 2612059.038 | 1260953.9062 | 2612079.6819 | 1260950.6784
3 | 2612059.038 | 1260953.9062 | 2612048.3124 | 1260955.5856
4 | 2612079.6819 | 1260950.6784 | 2612100.6277 | 1260947.4034
5 | 2612048.3124 | 1260955.5856 | 2612042.673 | 1260910.7861
6 | 2612125.7957 | 1260943.4682 | 2612100.6277 | 1260947.4034
7 | 2612040.8796 | 1260896.5397 | 2612042.673 | 1260910.7861
8 | 2612125.7957 | 1260943.4682 | 2612127.4195 | 1260937.9233 | 2612126.02 | 1260927.038
9 | 2612130.2477 | 1260955.1185 | 2612125.7957 | 1260943.4682
10 | 2612040.8796 | 1260896.5397 | 2612038.1749 | 1260875.0539
11 | 2612135.2728 | 1260995.7072 | 2612135.9511 | 1261001.1861
12 | 2612135.2728 | 1260995.7072 | 2612134.5163 | 1260989.5968
13 | 2612137.727 | 1261015.5304 | 2612135.9511 | 1261001.1861
14 | 2612137.727 | 1261015.5304 | 2612152.064 | 1261013.9282
15 | 2612135.9762 | 1261042.6675 | 2612137.727 | 1261015.5304
16 | 2612167.5264 | 1261012.2002 | 2612152.064 | 1261013.9282
17 | 2612135.9762 | 1261042.6675 | 2612150.5109 | 1261053.9235
18 | 2612135.9762 | 1261042.6675 | 2612121.5204 | 1261054.9079
19 | 2612130.2477 | 1260955.1185 | 2612148.2118 | 1260953.0797
20 | 2612148.5963 | 1260953.0361 | 2612148.2118 | 1260953.0797
21 | 2612167.5264 | 1261012.2002 | 2612174.2224 | 1261011.406
22 | 2612167.5264 | 1261012.2002 | 2612174.2055 | 1261025.4452
23 | 2612152.7693 | 1261056.0269 | 2612152.1278 | 1261055.1757 | 2612150.5109 | 1261053.9235
24 | 2612126.02 | 1260927.038 | 2612125.4297 | 1260922.4469
25 | 2612170.9401 | 1260950.5003 | 2612148.5963 | 1260953.0361
26 | 2612152.7693 | 1261056.0269 | 2612157.2601 | 1261061.9856
27 | 2612161.8067 | 1261068.0185 | 2612157.2601 | 1261061.9856
28 | 2612125.4297 | 1260922.4469 | 2612124.2229 | 1260913.0607
29 | 2612122.3016 | 1260898.1165 | 2612124.2229 | 1260913.0607
30 | 2612402.1973 | 1260994.4838 | 2612399.288 | 1260987.6955 | 2612365.5132 | 1260908.9862
31 | 2612330.4656 | 1260816.625 | 2612329.2655 | 1260828.4973 | 2612334.3954 | 1260836.4689 | 2612365.5132 | 1260908.9862
32 | 2612330.4656 | 1260816.625 | 2612322.1806 | 1260811.2597 | 2612316.3089 | 1260808.5569 | 2612309.871 | 1260806.3309 | 2612303.6217 | 1260804.0275 | 2612296.8949 | 1260813.9537
33 | 2612296.8949 | 1260813.9537 | 2612282.5238 | 1260840.3308 | 2612281.4539 | 1260844.0779
34 | 2612281.4539 | 1260844.0779 | 2612279.6514 | 1260850.3912
35 | 2612295.6206 | 1261120.2927 | 2612396.7834 | 1261122.8156
36 | 2612295.6206 | 1261120.2927 | 2612294.784 | 1261058.4712 | 2612292.4802 | 1261046.6806
37 | 2612292.4802 | 1261046.6806 | 2612276.1442 | 1261057.9257
38 | 2612292.4802 | 1261046.6806 | 2612281.2374 | 1261024.4378
39 | 2612276.1442 | 1261057.9257 | 2612275.3382 | 1261058.4805
40 | 2612277.8278 | 1261017.6922 | 2612281.2374 | 1261024.4378
41 | 2612275.3382 | 1261058.4805 | 2612271.2369 | 1261061.3037
42 | 2612268.5196 | 1260999.2766 | 2612277.8278 | 1261017.6922
43 | 2612279.6514 | 1260850.3912 | 2612274.327 | 1260869.0398
44 | 2612195.4616 | 1260824.3177 | 2612228.3226 | 1260820.3437
45 | 2612162.8123 | 1260828.266 | 2612195.4616 | 1260824.3177
46 | 2612027.682 | 1260791.6991 | 2611996.1794 | 1260796.8828
47 | 2612027.682 | 1260791.6991 | 2612056.7489 | 1260786.9195
48 | 2612107.4729 | 1260779.6973 | 2612077.777 | 1260783.4617 | 2612056.7489 | 1260786.9195
49 | 2612034.5449 | 1260846.2176 | 2612035.9918 | 1260857.7112
50 | 2612038.1749 | 1260875.0539 | 2612035.9918 | 1260857.7112
51 | 2612107.4729 | 1260779.6973 | 2612109.8034 | 1260798.8973
52 | 2612113.68 | 1260830.8367 | 2612109.8034 | 1260798.8973
53 | 2612162.8123 | 1260828.266 | 2612130.1421 | 1260832.2169
54 | 2612114.0833 | 1260834.1589 | 2612130.1421 | 1260832.2169
55 | 2612114.0833 | 1260834.1589 | 2612116.2867 | 1260851.3074
56 | 2612114.0833 | 1260834.1589 | 2612113.68 | 1260830.8367
57 | 2612116.2867 | 1260851.3074 | 2612117.1076 | 1260857.6967
58 | 2612117.1076 | 1260857.6967 | 2612117.9286 | 1260864.086
59 | 2612274.327 | 1260869.0398 | 2612269.1535 | 1260887.1599
60 | 2612117.9286 | 1260864.086 | 2612118.2129 | 1260866.2986
61 | 2612121.597 | 1260892.6362 | 2612118.2129 | 1260866.2986
62 | 2612121.597 | 1260892.6362 | 2612122.3016 | 1260898.1165
63 | 2612121.597 | 1260892.6362 | 2612145.2252 | 1260889.7119
64 | 2612145.2252 | 1260889.7119 | 2612166.1874 | 1260887.1177
65 | 2612179.7736 | 1260885.4362 | 2612166.1874 | 1260887.1177
66 | 2612179.7736 | 1260885.4362 | 2612198.8928 | 1260883.0701
67 | 2612201.6688 | 1260882.7265 | 2612198.8928 | 1260883.0701
68 | 2612170.9401 | 1260950.5003 | 2612189.5501 | 1260948.3882
69 | 2612200.8707 | 1260947.1035 | 2612189.5501 | 1260948.3882
70 | 2612201.6066 | 1260947.0199 | 2612200.8707 | 1260947.1035
71 | 2612201.6066 | 1260947.0199 | 2612213.5894 | 1260945.66
72 | 2612230.1034 | 1260943.7858 | 2612213.5894 | 1260945.66
73 | 2612263.3767 | 1260907.2783 | 2612266.5622 | 1260896.2359 | 2612269.1535 | 1260887.1599
74 | 2612253.615 | 1260941.1175 | 2612263.3767 | 1260907.2783
75 | 2612253.615 | 1260941.1175 | 2612254.9382 | 1260971.7855
76 | 2612253.615 | 1260941.1175 | 2612237.1921 | 1260942.9813
77 | 2612255.7764 | 1260973.4822 | 2612254.9382 | 1260971.7855 | 2612254.9382 | 1260971.7855
78 | 2612230.1034 | 1260943.7858 | 2612237.1921 | 1260942.9813
79 | 2612181.9045 | 1261010.4948 | 2612174.2224 | 1261011.406
80 | 2612174.2055 | 1261025.4452 | 2612175.0307 | 1261027.0816
81 | 2612238.6768 | 1261003.2276 | 2612244.3566 | 1261002.4756
82 | 2612238.6768 | 1261003.2276 | 2612223.7265 | 1261005.2069
83 | 2612244.3566 | 1261002.4756 | 2612251.1629 | 1261001.5745
84 | 2612216.2031 | 1261006.203 | 2612223.7265 | 1261005.2069
85 | 2612268.5196 | 1260999.2766 | 2612251.1629 | 1261001.5745
86 | 2612209.4718 | 1261007.0941 | 2612216.2031 | 1261006.203
87 | 2612268.5196 | 1260999.2766 | 2612255.7764 | 1260973.4822
88 | 2612203.3561 | 1261007.9038 | 2612209.4718 | 1261007.0941
89 | 2612199.9641 | 1261008.3529 | 2612203.3561 | 1261007.9038
90 | 2612207.6384 | 1261023.0182 | 2612211.3869 | 1261030.1814
91 | 2612199.9641 | 1261008.3529 | 2612207.6384 | 1261023.0182
92 | 2612211.3869 | 1261030.1814 | 2612214.8965 | 1261036.8881
93 | 2612199.9641 | 1261008.3529 | 2612194.8887 | 1261008.9549
94 | 2612218.3736 | 1261043.5327 | 2612214.8965 | 1261036.8881
95 | 2612194.8887 | 1261008.9549 | 2612181.9045 | 1261010.4948
96 | 2612175.0307 | 1261027.0816 | 2612178.5317 | 1261034.0242
97 | 2612178.5317 | 1261034.0242 | 2612181.9955 | 1261040.8932
98 | 2612185.3297 | 1261047.5051 | 2612181.9955 | 1261040.8932
99 | 2612185.3297 | 1261047.5051 | 2612188.7456 | 1261054.2791
100 | 2612192.2727 | 1261061.2735 | 2612188.7456 | 1261054.2791
101 | 2612244.0232 | 1261080.0366 | 2612243.8785 | 1261080.1362
102 | 2612244.0232 | 1261080.0366 | 2612250.0152 | 1261075.912
103 | 2612256.5844 | 1261071.39 | 2612250.0152 | 1261075.912
104 | 2612271.2369 | 1261061.3037 | 2612256.5844 | 1261071.39

## bus_geodata
| x | y | coords
0 | 2612066.5443 | 1260994.2606
1 | 2612071.5191 | 1261021.0049
2 | 2612059.038 | 1260953.9062
3 | 2612079.6819 | 1260950.6784
4 | 2612048.3124 | 1260955.5856
5 | 2612100.6277 | 1260947.4034
6 | 2612042.673 | 1260910.7861
7 | 2612125.7957 | 1260943.4682
8 | 2612040.8796 | 1260896.5397
9 | 2612135.2728 | 1260995.7072
10 | 2612135.9511 | 1261001.1861
11 | 2612134.5163 | 1260989.5968
12 | 2612137.727 | 1261015.5304
13 | 2612152.064 | 1261013.9282
14 | 2612135.9762 | 1261042.6675
15 | 2612130.2477 | 1260955.1185
16 | 2612148.2118 | 1260953.0797
17 | 2612167.5264 | 1261012.2002
18 | 2612150.5109 | 1261053.9235
19 | 2612121.5204 | 1261054.9079
20 | 2612126.02 | 1260927.038
21 | 2612148.5963 | 1260953.0361
22 | 2612152.7693 | 1261056.0269
23 | 2612157.2601 | 1261061.9856
24 | 2612125.4297 | 1260922.4469
25 | 2612124.2229 | 1260913.0607
26 | 2612402.1973 | 1260994.4838
27 | 2612365.5132 | 1260908.9862
28 | 2612330.4656 | 1260816.625
29 | 2612296.8949 | 1260813.9537
30 | 2612281.4539 | 1260844.0779
31 | 2612396.7834 | 1261122.8156
32 | 2612295.6206 | 1261120.2927
33 | 2612292.4802 | 1261046.6806
34 | 2612276.1442 | 1261057.9257
35 | 2612281.2374 | 1261024.4378
36 | 2612275.3382 | 1261058.4805
37 | 2612277.8278 | 1261017.6922
38 | 2612279.6514 | 1260850.3912
39 | 2612228.3226 | 1260820.3437
40 | 2612195.4616 | 1260824.3177
41 | 2611996.1794 | 1260796.8828
42 | 2612027.682 | 1260791.6991
43 | 2612056.7489 | 1260786.9195
44 | 2612034.5449 | 1260846.2176
45 | 2612035.9918 | 1260857.7112
46 | 2612107.4729 | 1260779.6973
47 | 2612038.1749 | 1260875.0539
48 | 2612109.8034 | 1260798.8973
49 | 2612162.8123 | 1260828.266
50 | 2612130.1421 | 1260832.2169
51 | 2612114.0833 | 1260834.1589
52 | 2612116.2867 | 1260851.3074
53 | 2612113.68 | 1260830.8367
54 | 2612117.1076 | 1260857.6967
55 | 2612274.327 | 1260869.0398
56 | 2612117.9286 | 1260864.086
57 | 2612118.2129 | 1260866.2986
58 | 2612121.597 | 1260892.6362
59 | 2612122.3016 | 1260898.1165
60 | 2612145.2252 | 1260889.7119
61 | 2612166.1874 | 1260887.1177
62 | 2612179.7736 | 1260885.4362
63 | 2612198.8928 | 1260883.0701
64 | 2612201.6688 | 1260882.7265
65 | 2612170.9401 | 1260950.5003
66 | 2612189.5501 | 1260948.3882
67 | 2612200.8707 | 1260947.1035
68 | 2612201.6066 | 1260947.0199
69 | 2612213.5894 | 1260945.66
70 | 2612269.1535 | 1260887.1599
71 | 2612263.3767 | 1260907.2783
72 | 2612253.615 | 1260941.1175
73 | 2612254.9382 | 1260971.7855
74 | 2612237.1921 | 1260942.9813
75 | 2612174.2224 | 1261011.406
76 | 2612174.2055 | 1261025.4452
77 | 2612238.6768 | 1261003.2276
78 | 2612244.3566 | 1261002.4756
79 | 2612223.7265 | 1261005.2069
80 | 2612251.1629 | 1261001.5745
81 | 2612216.2031 | 1261006.203
82 | 2612268.5196 | 1260999.2766
83 | 2612209.4718 | 1261007.0941
84 | 2612255.7764 | 1260973.4822
85 | 2612203.3561 | 1261007.9038
86 | 2612230.1034 | 1260943.7858
87 | 2612207.6384 | 1261023.0182
88 | 2612211.3869 | 1261030.1814
89 | 2612199.9641 | 1261008.3529
90 | 2612214.8965 | 1261036.8881
91 | 2612194.8887 | 1261008.9549
92 | 2612218.3736 | 1261043.5327
93 | 2612181.9045 | 1261010.4948
94 | 2612175.0307 | 1261027.0816
95 | 2612178.5317 | 1261034.0242
96 | 2612181.9955 | 1261040.8932
97 | 2612185.3297 | 1261047.5051
98 | 2612192.2727 | 1261061.2735
99 | 2612188.7456 | 1261054.2791
100 | 2612161.8067 | 1261068.0185
101 | 2612243.8785 | 1261080.1362
102 | 2612244.0232 | 1261080.0366
103 | 2612250.0152 | 1261075.912
104 | 2612271.2369 | 1261061.3037
105 | 2612256.5844 | 1261071.39
106 | 2612125.7957 | 1260943.4682

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1